03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_013 | Single Phase Fault with Stuck Breaker on S HAYS 3 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 (530553) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. ANGUS 3 (530714) 115.0 kV to GORHAM 3 (530552) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.5. ANGUS 3 (530714) 115.0 kV to Load #1 b.6. PFEIFER 3 (530725) 115.0 kV to Load #1 b.7. ANGUS 3 (530714) 115.0 kV to remove bus # b.8. PFEIFER 3 (530725) 115.0 kV to remove bus # b.9. GORHAM 3 (530552) 115.0 kV to Load #1 b.10. RUSLPMP3 (530684) 115.0 kV to Load #1 b.11. GORHAM 3 (530552) 115.0 kV to remove bus # b.12. RUSLPMP3 (530684) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_014 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_015 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_016 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_017 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_018 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_019 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_020 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_021 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_022 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_023 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_024 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_025 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_026 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. SMOKYHL6 (530592) 230.0 kV to SMKYP2 6 (530599) 230.0 kV Transmission Circuit #1 b.4. SHG2 34 1 (530715) 34.5 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus #1 b.6. SMKYP2 6 (530599) 230.0 kV to remove bus # b.7. SHP234 1 (530604) 34.5 kV to remove bus # b.8. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_027 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to remove bus #1 b.4. SMKYP1G1 (530594) 0.7 kV to remove bus #1 b.5. SMKYP2G1 (530600) 0.6 kV to remove bus #1 b.6. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_028 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.3. SMKYT2 1 (530634) 13.9 kV to Generator #1 b.4. SMKYT2 1 (530634) 13.9 kV to remove bus # b.5. SMKYP1G1 (530594) 0.7 kV to remove bus #1 b.6. SMKYP1 6 (530593) 230.0 kV to remove bus # b.7. SHP134 1 (530595) 34.5 kV to remove bus # b.8. SMKYT1 1 (530633) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_029 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to remove bus #1 b.4. SMKYP1G1 (530594) 0.7 kV to remove bus #1 b.5. SMKYP2G1 (530600) 0.6 kV to remove bus #1 b.6. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_030 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_031 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_032 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_033 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_034 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.2. LACROS 3 (530603) 115.0 kV to remove bus #1 b.3. NEKOMA 3 (530608) 115.0 kV to remove bus #1 b.4. ALXNDR 3 (530606) 115.0 kV to remove bus #1 b.5. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.6. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.7. HZRNGPL3 (530609) 115.0 kV to remove bus # b.8. ALEXNDR1 (539702) 34.5 kV to Load #1 b.9. LAXTAP 3 (530602) 115.0 kV to remove bus # b.10. NKMA2 1 (530630) 12.5 kV to remove bus # b.11. ALEXNDR1 (539702) 34.5 kV to remove bus # b.12. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_035 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_036 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LACROS 3 (530603) 115.0 kV to remove bus #1 b.4. NEKOMA 3 (530608) 115.0 kV to remove bus #1 b.5. ALXNDR 3 (530606) 115.0 kV to remove bus #1 b.7. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.8. ALEXNDR1 (539702) 34.5 kV to Load #1 b.9. LAXTAP 3 (530602) 115.0 kV to remove bus # b.10. NKMA2 1 (530630) 12.5 kV to remove bus # b.11. ALEXNDR1 (539702) 34.5 kV to remove bus # b.12. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_037 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to HEIZER 3 (530601) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_038 | Single Phase Fault with Stuck Breaker on RICE 3 (530623) 115 kV Bus a. Apply Fault at the RICE 3 (530623) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. BUSHTON3 (530681) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_039 | Single Phase Fault with Stuck Breaker on RICE 3 (530623) 115 kV Bus a. Apply Fault at the RICE 3 (530623) 115 kV Bus b. Clear Fault after 19 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 3 (530623) 115.0 kV to Load #1 b.3. RICE 3 (530623) 115.0 kV to Load #K1 b.4. RICE 3 (530623) 115.0 kV to Load #K2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_040 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 6 (530686) 230.0 kV to remove bus #1 b.3. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. PRWINDG1 (530690) 0.7 kV to Generator #1 b.6. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.7. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.8. PRWINDG1 (530690) 0.7 kV to remove bus # b.9. BUFCRKT11 (530691) 12.5 kV to remove bus # b.10. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_041 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_042 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_001 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_002 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_003 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_004 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #1 b.4. EMPEC121 (532740) 13.8 kV to Generator #2 b.5. EMPEC121 (532740) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_005 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.2. EMPEC121 (532740) 13.8 kV to Generator #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #2 b.4. EMPEC121 (532740) 13.8 kV to remove bus # b.5. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_006 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_007 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.2. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.3. EMPEC7 1 (532744) 18.0 kV to remove bus # b.4. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_008 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_009 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_010 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_011 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_012 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_013 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_014 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_015 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_016 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_017 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. IAT G1 1 (542957) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_018 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_019 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_020 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_021 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_022 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_023 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_024 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_025 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_026 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_027 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_028 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_029 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_030 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_031 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_032 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_033 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IAT G1 1 (542957) 24.0 kV to remove bus # b.2. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_034 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_035 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 35.25 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. HAWTHN5 (543665) 161.0 kV to LEVEE 5 (542976) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to remove bus # b.4. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_036 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 35.25 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. HAWTHN5 (543665) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.3. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.4. HAWTHN5 (543665) 161.0 kV to LEVEE 5 (542976) 161.0 kV Transmission Circuit #1 b.5. HAW G5 1 (542951) 22.0 kV to remove bus # b.6. RANDLPH5 (543027) 161.0 kV to Load #1 b.7. RANDLPH5 (543027) 161.0 kV to Load #4 b.8. RANDLPH5 (543027) 161.0 kV to remove bus # b.9. HAWTHN5 (543665) 161.0 kV to LEVEE 5 (542976) 161.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_001 | 3 Phase fault on CAR395 5 161.00 (547485) 161 kV Bus a. Apply fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.3. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_002 | 3 Phase fault on HOL387 5 161.00 (547482) 161 kV Bus a. Apply fault at the HOL387 5 161.00 (547482) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZD312 5 (547474) 161.0 kV to HOL387 5 (547482) 161.0 kV Transmission Circuit #1 b.2. HOL387 5 (547482) 161.0 kV to HOL478_5 (547626) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_003 | 3 Phase fault on RDS295 5 161.00 (547473) 161 kV Bus a. Apply fault at the RDS295 5 161.00 (547473) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_004 | 3 Phase fault on BRN331 5 161.00 (547475) 161 kV Bus a. Apply fault at the BRN331 5 161.00 (547475) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZD312 5 (547474) 161.0 kV to BRN331 5 (547475) 161.0 kV Transmission Circuit #1 b.2. BRN331 5 (547475) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_005 | 3 Phase fault on GRT433 5 161.00 (547495) 161 kV Bus a. Apply fault at the GRT433 5 161.00 (547495) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRN412 5 (547488) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 b.2. BRN413 5 (547489) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_006 | 3 Phase fault on BOL431 5 161.00 (547493) 161 kV Bus a. Apply fault at the BOL431 5 161.00 (547493) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_007 | 3 Phase fault on JOP391 5 161.00 (547593) 161 kV Bus a. Apply fault at the JOP391 5 161.00 (547593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.2. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_008 | 3 Phase fault on RVS438 5 161.00 (547497) 161 kV Bus a. Apply fault at the RVS438 5 161.00 (547497) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVS438 5 (547497) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_009 | 3 Phase fault on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_010 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_011 | 3 Phase fault on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.4. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.5. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 b.6. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-T (539943) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_012 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_013 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_014 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_015 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_016 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_017 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_018 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_019 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_020 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_021 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_022 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_023 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_024 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_025 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_028 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_029 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_030 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_031 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_032 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_033 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_034 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_035 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_036 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_037 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_038 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_039 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G17-068-GEN1 (589063). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_040 | 3 Phase fault on GILL 4 138.00 (533047) 138 kV Bus a. Apply fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_041 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_042 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_043 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_044 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_045 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_046 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_047 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_048 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_049 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_050 | 3 Phase fault on EMCPHER3 115.00 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 115.00 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to MANVILE3 (533426) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_051 | 3 Phase fault on EMCPHER3 115.00 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 115.00 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_052 | 3 Phase fault on MANVILE3 115.00 (533426) 115 kV Bus a. Apply fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_053 | 3 Phase fault on REFINRY3 115.00 (533427) 115 kV Bus a. Apply fault at the REFINRY3 115.00 (533427) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REFINRY3 (533427) 115.0 kV to MCPHER 3 (533428) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_054 | 3 Phase fault on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_055 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_056 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_057 | 3 Phase fault on HEC 2 69.000 (533513) 69 kV Bus a. Apply fault at the HEC 2 69.000 (533513) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 2 (533513) 69.0 kV to 17HALST2 (533521) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_058 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_059 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHROP (344923) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_060 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_061 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_062 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_063 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKS (300041) 345.0 kV to 7BLAND (344154) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_064 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKS (300041) 345.0 kV to 7LOOSECRK (344327) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_065 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_066 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_067 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_068 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_069 | 3 Phase fault on 5COMPTN 161.00 (300719) 161 kV Bus a. Apply fault at the 5COMPTN 161.00 (300719) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_070 | 3 Phase fault on 5GRANDVIEW% 161.00 (338099) 161 kV Bus a. Apply fault at the 5GRANDVIEW% 161.00 (338099) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to 5OSAGE CRK#! (338682) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_071 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.3. BUFORD 5 (504440) 161.0 kV to NORFORK5 (505448) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_072 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.2. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_073 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_074 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_075 | 3 Phase fault on OZD312 5 161.00 (547474) 161 kV Bus a. Apply fault at the OZD312 5 161.00 (547474) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZD312 5 (547474) 161.0 kV to OZD312 2 (547562) 69.0 kV to OZD312T1 (547710) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_076 | 3 Phase fault on BRN413 5 161.00 (547489) 161 kV Bus a. Apply fault at the BRN413 5 161.00 (547489) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRN413 5 (547489) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_077 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_078 | 3 Phase fault on 5GRANDVIEW% 161.00 (338099) 161 kV Bus a. Apply fault at the 5GRANDVIEW% 161.00 (338099) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_079 | 3 Phase fault on 5OMAHA+ 161.00 (338105) 161 kV Bus a. Apply fault at the 5OMAHA+ 161.00 (338105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HARRISON.E! (338104) 161.0 kV to 5OMAHA+ (338105) 161.0 kV Transmission Circuit #1 b.2. 5OMAHA+ (338105) 161.0 kV to 5OMAHA (338106) 161.0 kV Transmission Circuit #1 b.3. 5OMAHA+ (338105) 161.0 kV to OZD312 5 (547474) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_080 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_081 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_082 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_083 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_084 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_085 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_086 | 3 Phase fault on OAKGRV 5 161.00 (541227) 161 kV Bus a. Apply fault at the OAKGRV 5 161.00 (541227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAINVL5 (541226) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 b.2. OAKGRV 5 (541227) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_087 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_088 | 3 Phase fault on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_089 | 3 Phase fault on WINJT N5 161.00 (543009) 161 kV Bus a. Apply fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_090 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_091 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_092 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_093 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_094 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_095 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_096 | 3 Phase fault on CONWAY 138.00 (539009) 138 kV Bus a. Apply fault at the CONWAY 138.00 (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_097 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_098 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_099 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_100 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_101 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_102 | 3 Phase fault on CORONAD3 115.00 (533394) 115 kV Bus a. Apply fault at the CORONAD3 115.00 (533394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_103 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_104 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_105 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_106 | 3 Phase fault on 43LORAN 115.00 (533440) 115 kV Bus a. Apply fault at the 43LORAN 115.00 (533440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.2. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.3. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_107 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_108 | 3 Phase fault on BYRONTP4 138.00 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 138.00 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.2. CHRKCTY4 (520431) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.3. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.4. BYRONTP4 (520432) 138.0 kV to UNIONVL4 (520453) 138.0 kV Transmission Circuit #1 b.5. BYRONTP4 (520432) 138.0 kV to BYRON 4 (520477) 138.0 kV Transmission Circuit #1 b.6. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.7. SANDYCR4 (520433) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 b.8. SANDYCR4 (520433) 138.0 kV to UNIONVL4 (520453) 138.0 kV Transmission Circuit #1 b.9. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_109 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_110 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_111 | 3 Phase fault on LAKCTY 2 69.000 (543092) 69 kV Bus a. Apply fault at the LAKCTY 2 69.000 (543092) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 b.2. BLUSPRG2 (543088) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 b.3. BLUSPRG2 (543088) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_112 | 3 Phase fault on BYPASJT2 69.000 (543084) 69 kV Bus a. Apply fault at the BYPASJT2 69.000 (543084) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYJT2 (543079) 69.0 kV to BYPASJT2 (543084) 69.0 kV Transmission Circuit #1 b.2. BYPASJT2 (543084) 69.0 kV to IND WTR2 (543086) 69.0 kV Transmission Circuit #1 b.3. BYPASJT2 (543084) 69.0 kV to LIBRTYS2 (543095) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_113 | 3 Phase fault on MILCKJT2 69.000 (543110) 69 kV Bus a. Apply fault at the MILCKJT2 69.000 (543110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.3. IND WTR2 (543086) 69.0 kV to CEMCITY2 (543090) 69.0 kV Transmission Circuit #1 b.4. IND WTR2 (543086) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.5. TMP LAF2 (543103) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.6. LAFJCT 2 (543104) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.7. MILCKJT2 (543110) 69.0 kV to LAFARGE2 (543111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_114 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_115 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_116 | 3 Phase fault on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_117 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_118 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_119 | 3 Phase fault on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_120 | 3 Phase fault on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_121 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_122 | 3 Phase fault on ANTHONY4 138.00 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 138.00 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_123 | 3 Phase fault on SALTCRK3 115.00 (533434) 115 kV Bus a. Apply fault at the SALTCRK3 115.00 (533434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to SALTCRK3 (533434) 115.0 kV Transmission Circuit #1 b.2. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_124 | 3 Phase fault on HUNTSVL3 115.00 (530618) 115 kV Bus a. Apply fault at the HUNTSVL3 115.00 (530618) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_125 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_126 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_127 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_128 | 3 Phase fault on 5BUTLER 161.00 (301342) 161 kV Bus a. Apply fault at the 5BUTLER 161.00 (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_129 | 3 Phase fault on STALEY 2 69.000 (541261) 69 kV Bus a. Apply fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_130 | 3 Phase fault on FROSTRD_CAP5161.00 (541139) 161 kV Bus a. Apply fault at the FROSTRD_CAP5161.00 (541139) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD_CAP5 (541139) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_131 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_132 | 3 Phase fault on WBURGE_CAP5 161.00 (541148) 161 kV Bus a. Apply fault at the WBURGE_CAP5 161.00 (541148) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE_CAP5 (541148) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_133 | 3 Phase fault on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_134 | 3 Phase fault on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_135 | 3 Phase fault on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.4. NICHOL XF1 1 (549940) 13.2 kV to NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_136 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.3. MILL XF1 1 (549946) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_137 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 b.3. MILL XF2 1 (549948) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_138 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_139 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_140 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_141 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_142 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_143 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_144 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_145 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_146 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_147 | 3 Phase fault on SUB B 69.000 (548810) 69 kV Bus a. Apply fault at the SUB B 69.000 (548810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_148 | 3 Phase fault on SUB J 69.000 (548811) 69 kV Bus a. Apply fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_149 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_150 | 3 Phase fault on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_151 | 3 Phase fault on KCPL JCT 69.000 (548832) 69 kV Bus a. Apply fault at the KCPL JCT 69.000 (548832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB F (548803) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 b.2. SUB E (548804) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_152 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_153 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_154 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_155 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_156 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_157 | 3 Phase fault on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_158 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_159 | 3 Phase fault on NORTON 5 161.00 (543064) 161 kV Bus a. Apply fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (543064) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_160 | 3 Phase fault on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_N2 (543089) 69.0 kV to SUGRCRK_S2 (543163) 69.0 kV Transmission Circuit #z1 b.2. SUGRCRK_N2 (543089) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 b.3. SUGRCK_TP_W2 (543164) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 b.4. SUGRCK_TP_W2 (543164) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 b.5. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_161 | 3 Phase fault on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_162 | 3 Phase fault on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_163 | 3 Phase fault on 3 VANBU3 115.00 (533435) 115 kV Bus a. Apply fault at the 3 VANBU3 115.00 (533435) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3 VANBU3 (533435) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_164 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_165 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_166 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_167 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_168 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_169 | 3 Phase fault on CRAWFRD3 115.00 (533364) 115 kV Bus a. Apply fault at the CRAWFRD3 115.00 (533364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFRD3 (533364) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.2. CRAWFRD3 (533364) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 b.3. MENTOR 3 (533374) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_170 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_171 | 3 Phase fault on SO GATE3 115.00 (533379) 115 kV Bus a. Apply fault at the SO GATE3 115.00 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.2. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_172 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_173 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_174 | 3 Phase fault on WPRTTS 2 69.000 (530596) 69 kV Bus a. Apply fault at the WPRTTS 2 69.000 (530596) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.2. GB STH 2 (530569) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.3. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.4. WPRTTS 2 (530596) 69.0 kV to WPRT2 2 (530597) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_175 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_176 | 3 Phase fault on COLLEG 2 69.000 (530574) 69 kV Bus a. Apply fault at the COLLEG 2 69.000 (530574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 b.2. COLLEG 2 (530574) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_177 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_178 | 3 Phase fault on NEKOMA 2 69.000 (530564) 69 kV Bus a. Apply fault at the NEKOMA 2 69.000 (530564) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_179 | 3 Phase fault on BKHLTAP2 69.000 (530589) 69 kV Bus a. Apply fault at the BKHLTAP2 69.000 (530589) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.2. SUSANK 2 (530571) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.3. BNK HL 2 (530572) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.4. HITHMN 2 (530573) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_180 | 3 Phase fault on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_181 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_182 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_183 | 3 Phase fault on RICE 3 115.00 (530623) 115 kV Bus a. Apply fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_184 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_185 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_186 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_187 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_188 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_189 | 3 Phase fault on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_190 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_191 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_192 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_193 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_194 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_195 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_196 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_197 | 3 Phase fault on BUSHTON3 115.00 (530681) 115 kV Bus a. Apply fault at the BUSHTON3 115.00 (530681) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHTON3 (530681) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_198 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_199 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_200 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_201 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_202 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_203 | 3 Phase fault on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_204 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_205 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_206 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_207 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_208 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_209 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_210 | 3 Phase fault on RAGO 4 138.00 (539000) 138 kV Bus a. Apply fault at the RAGO 4 138.00 (539000) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_211 | 3 Phase fault on OTISSUB3 115.00 (539684) 115 kV Bus a. Apply fault at the OTISSUB3 115.00 (539684) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.2. OTISSUB3 (539684) 115.0 kV to OTISSUB1 (539723) 34.5 kV to OTIS1-T (539925) 2.4 kV Three Winding #1 b.3. OTISSUB3 (539684) 115.0 kV to OTISSUB1 (539723) 34.5 kV to OTIS2-T (539926) 2.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_212 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.3. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_213 | 3 Phase fault on EUREKA 5 161.00 (506932) 161 kV Bus a. Apply fault at the EUREKA 5 161.00 (506932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to EUREKA 5 (506932) 161.0 kV Transmission Circuit #1 b.2. 5OSAGE CRK#! (338682) 161.0 kV to EUREKA 5 (506932) 161.0 kV Transmission Circuit #1 b.3. BEAVER 5 (505480) 161.0 kV to EUREKA 5 (506932) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_214 | 3 Phase fault on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_215 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_216 | 3 Phase fault on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_217 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_218 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_219 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_220 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_221 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_222 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_223 | 3 Phase fault on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_224 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_225 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_226 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_227 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_228 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_229 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_230 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_231 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_232 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_233 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_234 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_235 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_236 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_237 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_238 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_239 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_240 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_241 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to BARBER 4 (539674) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_242 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_243 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_244 | 3 Phase fault on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.3. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_245 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_246 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_247 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_248 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_249 | 3 Phase fault on WILLIAM3 115.00 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 115.00 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_250 | 3 Phase fault on KSAVWTP3 115.00 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 115.00 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_251 | 3 Phase fault on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_252 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_253 | 3 Phase fault on SUNCITY3 115.00 (539697) 115 kV Bus a. Apply fault at the SUNCITY3 115.00 (539697) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.3. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.4. GRNBURG3 (539664) 115.0 kV to GRNBURG1 (539710) 34.5 kV to GRNBUG-T (539910) 13.8 kV Three Winding #1 b.5. SUNCITY3 (539697) 115.0 kV to SUNCITY1 (539733) 34.5 kV to SUNCT-T (539937) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_254 | 3 Phase fault on FORD 3 115.00 (539758) 115 kV Bus a. Apply fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.3. FORD 3 (539758) 115.0 kV to FORD 1 (539765) 34.5 kV to FORD T (539968) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_255 | 3 Phase fault on ST JOHN3 115.00 (530624) 115 kV Bus a. Apply fault at the ST JOHN3 115.00 (530624) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_256 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_257 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_258 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_259 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_260 | 3 Phase fault on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_261 | 3 Phase fault on DCBEEF3 115.00 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 115.00 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_262 | 3 Phase fault on SPEARVL3 115.00 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 115.00 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_263 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_264 | 3 Phase fault on N-DODGE3 115.00 (539680) 115 kV Bus a. Apply fault at the N-DODGE3 115.00 (539680) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DODG3 (539641) 115.0 kV to N-DODGE3 (539680) 115.0 kV Transmission Circuit #1 b.2. N-DODGE3 (539680) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. N-DODGE3 (539680) 115.0 kV to N-DODGE1 (539720) 34.5 kV to N-DODG-T (539922) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_265 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_266 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_267 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_268 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_269 | 3 Phase fault on BARBER 4 138.00 (539674) 138 kV Bus a. Apply fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 3 (539760) 115.0 kV to BARBER 4 (539674) 138.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_270 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G18-114-GEN2 (763335). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_271 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_272 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_273 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_274 | 3 Phase fault on HARPER 4 138.00 (539668) 138 kV Bus a. Apply fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_275 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G11-008-GEN7 (539858). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_276 | 3 Phase fault on ELLSWTH3 115.00 (539662) 115 kV Bus a. Apply fault at the ELLSWTH3 115.00 (539662) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTH3 (539662) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_277 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_278 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_279 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_280 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKS (300041) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_281 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKS (300041) 345.0 kV to 7SALEMTP (300472) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_282 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_283 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_284 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_285 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_286 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_287 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_288 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_289 | 3 Phase fault on 7FRANKSRCTP 345.00 (300051) 345 kV Bus a. Apply fault at the 7FRANKSRCTP 345.00 (300051) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKSRCTP (300051) 345.0 kV to 7FRANKSRCT (301554) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_290 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5HYDERHL (300793) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_291 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_292 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_293 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_294 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_295 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_296 | 3 Phase fault on 5COFFMN 161.00 (300072) 161 kV Bus a. Apply fault at the 5COFFMN 161.00 (300072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COFFMN (300072) 161.0 kV to 5HUBEN (300088) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_297 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_298 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_299 | 3 Phase fault on 5HUBEN 161.00 (300088) 161 kV Bus a. Apply fault at the 5HUBEN 161.00 (300088) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 5MRSHFL (300102) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_300 | 3 Phase fault on 5HUBEN 161.00 (300088) 161 kV Bus a. Apply fault at the 5HUBEN 161.00 (300088) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 5PHLIPS (300109) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_301 | 3 Phase fault on 5HUBEN 161.00 (300088) 161 kV Bus a. Apply fault at the 5HUBEN 161.00 (300088) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 5WHISPR (301077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_302 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5BTLFD (300348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_303 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_304 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5RIVRDL (300726) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_305 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_306 | 3 Phase fault on 5MANSFDMN 161.00 (300095) 161 kV Bus a. Apply fault at the 5MANSFDMN 161.00 (300095) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MANSFDMN (300095) 161.0 kV to 5LOGAN (301161) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_307 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_308 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_309 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_310 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to 5MORGANXF2 (301622) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_311 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_312 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_313 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_314 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_315 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_316 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOL (301040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_317 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_318 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_319 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_320 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_321 | 3 Phase fault on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STKAEC (300118) 161.0 kV to 5HYDERHL (300793) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_322 | 3 Phase fault on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STKAEC (300118) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_323 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_324 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_325 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_326 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2MOCITY (300304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_327 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_328 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_329 | 3 Phase fault on 5BTLFD 161.00 (300348) 161 kV Bus a. Apply fault at the 5BTLFD 161.00 (300348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_330 | 3 Phase fault on 2BEAMAN 69.000 (300527) 69 kV Bus a. Apply fault at the 2BEAMAN 69.000 (300527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEAMAN (300527) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_331 | 3 Phase fault on 2DRESDN 69.000 (300528) 69 kV Bus a. Apply fault at the 2DRESDN 69.000 (300528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DRESDN (300528) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_332 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_333 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_334 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_335 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_336 | 3 Phase fault on 2HUGHSV 69.000 (300533) 69 kV Bus a. Apply fault at the 2HUGHSV 69.000 (300533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HUGHSV (300533) 69.0 kV to 2SWSPJC (300543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_337 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_338 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_339 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_340 | 3 Phase fault on 2MALTAB 69.000 (300535) 69 kV Bus a. Apply fault at the 2MALTAB 69.000 (300535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAB (300535) 69.0 kV to 2MALTAJ (300536) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_341 | 3 Phase fault on 2MALTAJ 69.000 (300536) 69 kV Bus a. Apply fault at the 2MALTAJ 69.000 (300536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAJ (300536) 69.0 kV to 2MARSHL (300537) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_342 | 3 Phase fault on 2MALTAJ 69.000 (300536) 69 kV Bus a. Apply fault at the 2MALTAJ 69.000 (300536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAJ (300536) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_343 | 3 Phase fault on 2MARSHL 69.000 (300537) 69 kV Bus a. Apply fault at the 2MARSHL 69.000 (300537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MARSHL (300537) 69.0 kV to 2SWSPJC (300543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_344 | 3 Phase fault on 2NAPTON 69.000 (300538) 69 kV Bus a. Apply fault at the 2NAPTON 69.000 (300538) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NAPTON (300538) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_345 | 3 Phase fault on 2NAPTON 69.000 (300538) 69 kV Bus a. Apply fault at the 2NAPTON 69.000 (300538) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NAPTON (300538) 69.0 kV to 2PILOTG (300560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_346 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_347 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_348 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2FLORNC (300553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_349 | 3 Phase fault on 2SWSPJC 69.000 (300543) 69 kV Bus a. Apply fault at the 2SWSPJC 69.000 (300543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SWSPJC (300543) 69.0 kV to 2SWSPNG (300544) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_350 | 3 Phase fault on 2FLORNC 69.000 (300553) 69 kV Bus a. Apply fault at the 2FLORNC 69.000 (300553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FLORNC (300553) 69.0 kV to 2SYRACS (300564) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_351 | 3 Phase fault on 2IVYBND 69.000 (300557) 69 kV Bus a. Apply fault at the 2IVYBND 69.000 (300557) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IVYBND (300557) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_352 | 3 Phase fault on 2MTHULD 69.000 (300558) 69 kV Bus a. Apply fault at the 2MTHULD 69.000 (300558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MTHULD (300558) 69.0 kV to 2STOVER (300562) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_353 | 3 Phase fault on 2KENOMA 69.000 (300650) 69 kV Bus a. Apply fault at the 2KENOMA 69.000 (300650) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KENOMA (300650) 69.0 kV to 2LOCKWD (300676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_354 | 3 Phase fault on 2MILO 69.000 (300654) 69 kV Bus a. Apply fault at the 2MILO 69.000 (300654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MILO (300654) 69.0 kV to 2CLARK (300802) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_355 | 3 Phase fault on 2ASHGRV 69.000 (300657) 69 kV Bus a. Apply fault at the 2ASHGRV 69.000 (300657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHGRV (300657) 69.0 kV to 2CAVESP (300664) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_356 | 3 Phase fault on 2ASHGRV 69.000 (300657) 69 kV Bus a. Apply fault at the 2ASHGRV 69.000 (300657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_357 | 3 Phase fault on 2ASHGRV 69.000 (300657) 69 kV Bus a. Apply fault at the 2ASHGRV 69.000 (300657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHGRV (300657) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_358 | 3 Phase fault on 2BILLNG 69.000 (300658) 69 kV Bus a. Apply fault at the 2BILLNG 69.000 (300658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BILLNG (300658) 69.0 kV to BIL221 2 (547546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_359 | 3 Phase fault on 2BILLNG 69.000 (300658) 69 kV Bus a. Apply fault at the 2BILLNG 69.000 (300658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BILLNG (300658) 69.0 kV to CPK446 2 (547618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_360 | 3 Phase fault on 2BOWRML 69.000 (300659) 69 kV Bus a. Apply fault at the 2BOWRML 69.000 (300659) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOWRML (300659) 69.0 kV to 2ROUNDGRVETP (301395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_361 | 3 Phase fault on 2BOWRML 69.000 (300659) 69 kV Bus a. Apply fault at the 2BOWRML 69.000 (300659) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOWRML (300659) 69.0 kV to ALB262 2 (547553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_362 | 3 Phase fault on 2CAPEFR 69.000 (300662) 69 kV Bus a. Apply fault at the 2CAPEFR 69.000 (300662) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CAPEFR (300662) 69.0 kV to 2FLTCRK (300671) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_363 | 3 Phase fault on 2CAPEFR 69.000 (300662) 69 kV Bus a. Apply fault at the 2CAPEFR 69.000 (300662) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CAPEFR (300662) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_364 | 3 Phase fault on 2CLEVER 69.000 (300665) 69 kV Bus a. Apply fault at the 2CLEVER 69.000 (300665) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVER (300665) 69.0 kV to BIL221 2 (547546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_365 | 3 Phase fault on 2CRANE 69.000 (300667) 69 kV Bus a. Apply fault at the 2CRANE 69.000 (300667) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CRANE (300667) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_366 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2GRNFLD (300672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_367 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_368 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2BONA (300800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_369 | 3 Phase fault on 2ELWOOD 69.000 (300669) 69 kV Bus a. Apply fault at the 2ELWOOD 69.000 (300669) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_370 | 3 Phase fault on 2GRNFLD 69.000 (300672) 69 kV Bus a. Apply fault at the 2GRNFLD 69.000 (300672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GRNFLD (300672) 69.0 kV to 2LOCKWD (300676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_371 | 3 Phase fault on 2GRNFLD 69.000 (300672) 69 kV Bus a. Apply fault at the 2GRNFLD 69.000 (300672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GRNFLD (300672) 69.0 kV to 2ARCOLA (300797) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_372 | 3 Phase fault on 2GRNFLD 69.000 (300672) 69 kV Bus a. Apply fault at the 2GRNFLD 69.000 (300672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GRNFLD (300672) 69.0 kV to 2ROUNDGRVETP (301395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_373 | 3 Phase fault on 2MTVRN 69.000 (300677) 69 kV Bus a. Apply fault at the 2MTVRN 69.000 (300677) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MTVRN (300677) 69.0 kV to 2MIDWYTP (300684) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_374 | 3 Phase fault on 2MTVRN 69.000 (300677) 69 kV Bus a. Apply fault at the 2MTVRN 69.000 (300677) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MTVRN (300677) 69.0 kV to CPK446 2 (547618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_375 | 3 Phase fault on 5NIXA-1 161.00 (300678) 161 kV Bus a. Apply fault at the 5NIXA-1 161.00 (300678) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_376 | 3 Phase fault on 2PRDYTP 69.000 (300679) 69 kV Bus a. Apply fault at the 2PRDYTP 69.000 (300679) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PRDYTP (300679) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_377 | 3 Phase fault on 2VERONA 69.000 (300680) 69 kV Bus a. Apply fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_378 | 3 Phase fault on 2MIDWY 69.000 (300683) 69 kV Bus a. Apply fault at the 2MIDWY 69.000 (300683) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MIDWY (300683) 69.0 kV to 2MIDWYTP (300684) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_379 | 3 Phase fault on 2MIDWYTP 69.000 (300684) 69 kV Bus a. Apply fault at the 2MIDWYTP 69.000 (300684) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MIDWYTP (300684) 69.0 kV to ALB262 2 (547553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_380 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_381 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_382 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_383 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_384 | 3 Phase fault on 2BEARCK 69.000 (300713) 69 kV Bus a. Apply fault at the 2BEARCK 69.000 (300713) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEARCK (300713) 69.0 kV to 2GRTNA (300720) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_385 | 3 Phase fault on 2BEARCK 69.000 (300713) 69 kV Bus a. Apply fault at the 2BEARCK 69.000 (300713) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEARCK (300713) 69.0 kV to 2ROCKWY (300728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_386 | 3 Phase fault on 2BLUWTP 69.000 (300714) 69 kV Bus a. Apply fault at the 2BLUWTP 69.000 (300714) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLUWTP (300714) 69.0 kV to 2BLUWTR (300715) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_387 | 3 Phase fault on 2BLUWTP 69.000 (300714) 69 kV Bus a. Apply fault at the 2BLUWTP 69.000 (300714) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLUWTP (300714) 69.0 kV to 2KMBRLNTP (300721) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_388 | 3 Phase fault on 2BLUWTP 69.000 (300714) 69 kV Bus a. Apply fault at the 2BLUWTP 69.000 (300714) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLUWTP (300714) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_389 | 3 Phase fault on 2BRANSN 69.000 (300716) 69 kV Bus a. Apply fault at the 2BRANSN 69.000 (300716) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRANSN (300716) 69.0 kV to 2ROCKWY (300728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_390 | 3 Phase fault on 5COMPTN 161.00 (300719) 161 kV Bus a. Apply fault at the 5COMPTN 161.00 (300719) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COMPTN (300719) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_391 | 3 Phase fault on 2GRTNA 69.000 (300720) 69 kV Bus a. Apply fault at the 2GRTNA 69.000 (300720) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GRTNA (300720) 69.0 kV to 2REEDSP (300725) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_392 | 3 Phase fault on 2KMBRLNTP 69.000 (300721) 69 kV Bus a. Apply fault at the 2KMBRLNTP 69.000 (300721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KMBRLNTP (300721) 69.0 kV to 2STONBR (300733) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_393 | 3 Phase fault on 2KMBRLNTP 69.000 (300721) 69 kV Bus a. Apply fault at the 2KMBRLNTP 69.000 (300721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KMBRLNTP (300721) 69.0 kV to 2KMBRLN (301625) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_394 | 3 Phase fault on 2LAKE-K 69.000 (300722) 69 kV Bus a. Apply fault at the 2LAKE-K 69.000 (300722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAKE-K (300722) 69.0 kV to 2REEDSP (300725) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_395 | 3 Phase fault on 2LAKE-K 69.000 (300722) 69 kV Bus a. Apply fault at the 2LAKE-K 69.000 (300722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAKE-K (300722) 69.0 kV to 2SILDOL (300730) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_396 | 3 Phase fault on 2LAKE-K 69.000 (300722) 69 kV Bus a. Apply fault at the 2LAKE-K 69.000 (300722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAKE-K (300722) 69.0 kV to 2STONBR (300733) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_397 | 3 Phase fault on 2LAKE-K 69.000 (300722) 69 kV Bus a. Apply fault at the 2LAKE-K 69.000 (300722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAKE-K (300722) 69.0 kV to 2STULTS (300734) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_398 | 3 Phase fault on 2PARDIS 69.000 (300723) 69 kV Bus a. Apply fault at the 2PARDIS 69.000 (300723) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PARDIS (300723) 69.0 kV to TABLE R2 (505474) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_399 | 3 Phase fault on 2ROCKWY 69.000 (300728) 69 kV Bus a. Apply fault at the 2ROCKWY 69.000 (300728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ROCKWY (300728) 69.0 kV to 2TANYVL (300736) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_400 | 3 Phase fault on 2SILDOL 69.000 (300730) 69 kV Bus a. Apply fault at the 2SILDOL 69.000 (300730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SILDOL (300730) 69.0 kV to 2T.ROCKSW (301360) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_401 | 3 Phase fault on 2SPOKAN 69.000 (300732) 69 kV Bus a. Apply fault at the 2SPOKAN 69.000 (300732) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SPOKAN (300732) 69.0 kV to 2RENOHLW (300738) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_402 | 3 Phase fault on 2STULTS 69.000 (300734) 69 kV Bus a. Apply fault at the 2STULTS 69.000 (300734) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STULTS (300734) 69.0 kV to 2RENOHLW (300738) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_403 | 3 Phase fault on 2T.ROCK 69.000 (300735) 69 kV Bus a. Apply fault at the 2T.ROCK 69.000 (300735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2T.ROCK (300735) 69.0 kV to TABLE R2 (505474) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_404 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_405 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_406 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_407 | 3 Phase fault on 2BUFFLO 69.000 (300770) 69 kV Bus a. Apply fault at the 2BUFFLO 69.000 (300770) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUFFLO (300770) 69.0 kV to 2MARCH (300781) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_408 | 3 Phase fault on 2BUFFLO 69.000 (300770) 69 kV Bus a. Apply fault at the 2BUFFLO 69.000 (300770) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUFFLO (300770) 69.0 kV to 2POLK (300786) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_409 | 3 Phase fault on 2BUFFLO 69.000 (300770) 69 kV Bus a. Apply fault at the 2BUFFLO 69.000 (300770) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUFFLO (300770) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_410 | 3 Phase fault on 2BUFFLO 69.000 (300770) 69 kV Bus a. Apply fault at the 2BUFFLO 69.000 (300770) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUFFLO (300770) 69.0 kV to 2WOODHL (300791) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_411 | 3 Phase fault on 2BUFFLO 69.000 (300770) 69 kV Bus a. Apply fault at the 2BUFFLO 69.000 (300770) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BUFFLO (300770) 69.0 kV to 2LONGLN (301068) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_412 | 3 Phase fault on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2EUDORA (300774) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_413 | 3 Phase fault on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2EUDORA (300774) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_414 | 3 Phase fault on 2FAIRGR 69.000 (300775) 69 kV Bus a. Apply fault at the 2FAIRGR 69.000 (300775) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FAIRGR (300775) 69.0 kV to 2PLEAST (300785) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_415 | 3 Phase fault on 2PLEAST 69.000 (300785) 69 kV Bus a. Apply fault at the 2PLEAST 69.000 (300785) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PLEAST (300785) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_416 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_417 | 3 Phase fault on 2ARCOLA 69.000 (300797) 69 kV Bus a. Apply fault at the 2ARCOLA 69.000 (300797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ARCOLA (300797) 69.0 kV to 2HYDERHL (300798) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_418 | 3 Phase fault on 2HYDERHL 69.000 (300798) 69 kV Bus a. Apply fault at the 2HYDERHL 69.000 (300798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HYDERHL (300798) 69.0 kV to 2ARNICA (300799) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_419 | 3 Phase fault on 2HYDERHL 69.000 (300798) 69 kV Bus a. Apply fault at the 2HYDERHL 69.000 (300798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HYDERHL (300798) 69.0 kV to 2CEDRSP (300801) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_420 | 3 Phase fault on 2CLARK 69.000 (300802) 69 kV Bus a. Apply fault at the 2CLARK 69.000 (300802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLARK (300802) 69.0 kV to 2WALKER (300814) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_421 | 3 Phase fault on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_422 | 3 Phase fault on 5LOGAN 161.00 (301161) 161 kV Bus a. Apply fault at the 5LOGAN 161.00 (301161) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_423 | 3 Phase fault on 2T.ROCKSW 69.000 (301360) 69 kV Bus a. Apply fault at the 2T.ROCKSW 69.000 (301360) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2T.ROCKSW (301360) 69.0 kV to TABLE R2 (505474) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_424 | 3 Phase fault on 2ROUNDGROVE 69.000 (301393) 69 kV Bus a. Apply fault at the 2ROUNDGROVE 69.000 (301393) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ROUNDGROVE (301393) 69.0 kV to 2ROUNDGRVETP (301395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_425 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_426 | 3 Phase fault on 5MCBAINB2 161.00 (301489) 161 kV Bus a. Apply fault at the 5MCBAINB2 161.00 (301489) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_427 | 3 Phase fault on 5REEDSP 161.00 (301521) 161 kV Bus a. Apply fault at the 5REEDSP 161.00 (301521) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REEDSP (301521) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_428 | 3 Phase fault on 5LOYMART 2 161.00 (344041) 161 kV Bus a. Apply fault at the 5LOYMART 2 161.00 (344041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_429 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_430 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_431 | 3 Phase fault on 5MCBAIN T 161.00 (345071) 161 kV Bus a. Apply fault at the 5MCBAIN T 161.00 (345071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_432 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_433 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2MACON_AM (346096) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_434 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2DUPONT (346169) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_435 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2ROTH TAP (346170) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_436 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2SPRK TAP (346171) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_437 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_438 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_439 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_440 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_441 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_442 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_443 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_444 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_445 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_446 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_447 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_448 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_449 | 3 Phase fault on NIXA 2 69.000 (505501) 69 kV Bus a. Apply fault at the NIXA 2 69.000 (505501) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_450 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_451 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_452 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_453 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_454 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_455 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_456 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_457 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_458 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_459 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_460 | 3 Phase fault on HAYS 3 115.00 (530562) 115 kV Bus a. Apply fault at the HAYS 3 115.00 (530562) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYS 3 (530562) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_461 | 3 Phase fault on HAYS 3 115.00 (530562) 115 kV Bus a. Apply fault at the HAYS 3 115.00 (530562) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYS 3 (530562) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_462 | 3 Phase fault on N HAYS3 115.00 (530581) 115 kV Bus a. Apply fault at the N HAYS3 115.00 (530581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_463 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_464 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_465 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_466 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_467 | 3 Phase fault on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_468 | 3 Phase fault on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_469 | 3 Phase fault on RICE 3 115.00 (530623) 115 kV Bus a. Apply fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTONW 3 (530718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_470 | 3 Phase fault on VINETAP3 115.00 (530693) 115 kV Bus a. Apply fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_471 | 3 Phase fault on VINE2 3 115.00 (530694) 115 kV Bus a. Apply fault at the VINE2 3 115.00 (530694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINE2 3 (530694) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_472 | 3 Phase fault on VINE2 3 115.00 (530694) 115 kV Bus a. Apply fault at the VINE2 3 115.00 (530694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINE2 3 (530694) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_473 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_474 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_475 | 3 Phase fault on CLARKCOUNTY7 345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G19-030-TAP (763677) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G11-008-GEN7 (539858). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_476 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_477 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_478 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_479 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_480 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_481 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_482 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_483 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_484 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_485 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_486 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G17-068-GEN1 (589063). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_487 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G17-068-GEN1 (589063). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_488 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_489 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_490 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_491 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_492 | 3 Phase fault on BERG 3 115.00 (533367) 115 kV Bus a. Apply fault at the BERG 3 115.00 (533367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG 3 (533367) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_493 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_494 | 3 Phase fault on ARKVAL 3 115.00 (533411) 115 kV Bus a. Apply fault at the ARKVAL 3 115.00 (533411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_495 | 3 Phase fault on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRG3 (533429) 115.0 kV to MNDRGCT3 (533430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_496 | 3 Phase fault on CESSNAJ2 69.000 (533503) 69 kV Bus a. Apply fault at the CESSNAJ2 69.000 (533503) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CESSNAJ2 (533503) 69.0 kV to 11HALST2 (533509) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_497 | 3 Phase fault on 11HALST2 69.000 (533509) 69 kV Bus a. Apply fault at the 11HALST2 69.000 (533509) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 11HALST2 (533509) 69.0 kV to 17HALST2 (533521) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_498 | 3 Phase fault on 14LORAN2 69.000 (533511) 69 kV Bus a. Apply fault at the 14LORAN2 69.000 (533511) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 14LORAN2 (533511) 69.0 kV to 17HUXMN2 (533522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_499 | 3 Phase fault on 17HALST2 69.000 (533521) 69 kV Bus a. Apply fault at the 17HALST2 69.000 (533521) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17HALST2 (533521) 69.0 kV to 17HUXMN2 (533522) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_500 | 3 Phase fault on 17HUXMN2 69.000 (533522) 69 kV Bus a. Apply fault at the 17HUXMN2 69.000 (533522) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17HUXMN2 (533522) 69.0 kV to 17 PLUM2 (533523) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_501 | 3 Phase fault on NW-DGTP3 115.00 (539628) 115 kV Bus a. Apply fault at the NW-DGTP3 115.00 (539628) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DGTP3 (539628) 115.0 kV to W-DODGE3 (539699) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_502 | 3 Phase fault on NW-DGTP3 115.00 (539628) 115 kV Bus a. Apply fault at the NW-DGTP3 115.00 (539628) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DGTP3 (539628) 115.0 kV to LOCHS (539944) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_503 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G18-114-GEN2 (763335). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_504 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G18-114-GEN2 (763335). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_505 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_506 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G11-008-GEN7 (539858). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_507 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G11-008-GEN7 (539858). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_508 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G11-008-GEN7 (539858). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_509 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G11-008-GEN7 (539858). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_510 | 3 Phase fault on FROSTRD_CAP5161.00 (541139) 161 kV Bus a. Apply fault at the FROSTRD_CAP5161.00 (541139) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD_CAP5 (541139) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_511 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_512 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_513 | 3 Phase fault on WBURGE_CAP5 161.00 (541148) 161 kV Bus a. Apply fault at the WBURGE_CAP5 161.00 (541148) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE_CAP5 (541148) 161.0 kV to WBURGE 5 (541228) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_514 | 3 Phase fault on WSTELEC_CAP5161.00 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5161.00 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_515 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_516 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_517 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_518 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_519 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_520 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_521 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_522 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_523 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_524 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_525 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to SMTHVL 5 (541204) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_526 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_527 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_528 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_529 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_530 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_531 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_532 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_533 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_534 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_535 | 3 Phase fault on RAYTOWN5 161.00 (541219) 161 kV Bus a. Apply fault at the RAYTOWN5 161.00 (541219) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_536 | 3 Phase fault on FROSTRD5 161.00 (541220) 161 kV Bus a. Apply fault at the FROSTRD5 161.00 (541220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD5 (541220) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_537 | 3 Phase fault on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_538 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_539 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_540 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_541 | 3 Phase fault on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 5 (541229) 161.0 kV to LEX161 5 (541232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_542 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_543 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_544 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_545 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_546 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_547 | 3 Phase fault on 13&40 2 69.000 (541266) 69 kV Bus a. Apply fault at the 13&40 2 69.000 (541266) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to ODESSA 2 (541267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_548 | 3 Phase fault on ODESSA 2 69.000 (541267) 69 kV Bus a. Apply fault at the ODESSA 2 69.000 (541267) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 2 (541267) 69.0 kV to ODESSACTY2 (541526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_549 | 3 Phase fault on WBURGP 2 69.000 (541268) 69 kV Bus a. Apply fault at the WBURGP 2 69.000 (541268) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to WBURGE 2 (541269) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_550 | 3 Phase fault on WBURGE 2 69.000 (541269) 69 kV Bus a. Apply fault at the WBURGE 2 69.000 (541269) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 2 (541269) 69.0 kV to MONSERTP (541524) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_551 | 3 Phase fault on KNOSTER2 69.000 (541270) 69 kV Bus a. Apply fault at the KNOSTER2 69.000 (541270) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOSTER2 (541270) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_552 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_553 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_554 | 3 Phase fault on SEDS 2 69.000 (541272) 69 kV Bus a. Apply fault at the SEDS 2 69.000 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_555 | 3 Phase fault on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_556 | 3 Phase fault on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_557 | 3 Phase fault on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_558 | 3 Phase fault on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_559 | 3 Phase fault on COLECMP2 69.000 (541276) 69 kV Bus a. Apply fault at the COLECMP2 69.000 (541276) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLECMP2 (541276) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_560 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_561 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_562 | 3 Phase fault on NRAYMORE 161.00 (541317) 161 kV Bus a. Apply fault at the NRAYMORE 161.00 (541317) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORE (541317) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_563 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBW5 (541336) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_564 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_565 | 3 Phase fault on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161.0 kV to WAFBE5 (541338) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_566 | 3 Phase fault on MONSERTP 69.000 (541524) 69 kV Bus a. Apply fault at the MONSERTP 69.000 (541524) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONSERTP (541524) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_567 | 3 Phase fault on KNOSTERTP 69.000 (541534) 69 kV Bus a. Apply fault at the KNOSTERTP 69.000 (541534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOSTERTP (541534) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_568 | 3 Phase fault on LAMONTETP 69.000 (541535) 69 kV Bus a. Apply fault at the LAMONTETP 69.000 (541535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMONTETP (541535) 69.0 kV to LAMONTE (541536) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_569 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_570 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_571 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_572 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_573 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_574 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_575 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_576 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_577 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_578 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_579 | 3 Phase fault on LVISTA 5 161.00 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 161.00 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_580 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_581 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_582 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_583 | 3 Phase fault on MALTABN5 161.00 (543059) 161 kV Bus a. Apply fault at the MALTABN5 161.00 (543059) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_584 | 3 Phase fault on MALTABN5 161.00 (543059) 161 kV Bus a. Apply fault at the MALTABN5 161.00 (543059) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_585 | 3 Phase fault on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_586 | 3 Phase fault on S EAST 5 161.00 (543071) 161 kV Bus a. Apply fault at the S EAST 5 161.00 (543071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S EAST 5 (543071) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_587 | 3 Phase fault on MRSHLJT5 161.00 (543072) 161 kV Bus a. Apply fault at the MRSHLJT5 161.00 (543072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRSHLJT5 (543072) 161.0 kV to MIAMI_ 5 (543073) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_588 | 3 Phase fault on DUNCNRD2 69.000 (543091) 69 kV Bus a. Apply fault at the DUNCNRD2 69.000 (543091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_589 | 3 Phase fault on SUGRCRK_S2 69.000 (543163) 69 kV Bus a. Apply fault at the SUGRCRK_S2 69.000 (543163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_S2 (543163) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_590 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON416J2 (547402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_591 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_592 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON352 2 (547406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_593 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_594 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_595 | 3 Phase fault on RES364 2 69.000 (547424) 69 kV Bus a. Apply fault at the RES364 2 69.000 (547424) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RES364 2 (547424) 69.0 kV to ALB262 2 (547553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_596 | 3 Phase fault on HER209 2 69.000 (547425) 69 kV Bus a. Apply fault at the HER209 2 69.000 (547425) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HER209 2 (547425) 69.0 kV to BOL 73 2 (547528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_597 | 3 Phase fault on BUF243J2 69.000 (547432) 69 kV Bus a. Apply fault at the BUF243J2 69.000 (547432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUF243J2 (547432) 69.0 kV to BUF342 2 (547575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_598 | 3 Phase fault on BUF409 2 69.000 (547434) 69 kV Bus a. Apply fault at the BUF409 2 69.000 (547434) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUF409 2 (547434) 69.0 kV to BUF342 2 (547575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_599 | 3 Phase fault on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUPTAP 2 (547436) 69.0 kV to CUPSUB 2 (547437) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_600 | 3 Phase fault on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUPTAP 2 (547436) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_601 | 3 Phase fault on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUPTAP 2 (547436) 69.0 kV to GRN614 2 (547613) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_602 | 3 Phase fault on EXP450T2 69.000 (547440) 69 kV Bus a. Apply fault at the EXP450T2 69.000 (547440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP450T2 (547440) 69.0 kV to EXP4502 (547441) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_603 | 3 Phase fault on EXP450T2 69.000 (547440) 69 kV Bus a. Apply fault at the EXP450T2 69.000 (547440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP450T2 (547440) 69.0 kV to BOL 73 2 (547528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_604 | 3 Phase fault on EXP450T2 69.000 (547440) 69 kV Bus a. Apply fault at the EXP450T2 69.000 (547440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP450T2 (547440) 69.0 kV to BRT323 2 (547567) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_605 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_606 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_607 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_608 | 3 Phase fault on KOD471 2 69.000 (547463) 69 kV Bus a. Apply fault at the KOD471 2 69.000 (547463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOD471 2 (547463) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_609 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_610 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_611 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_612 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_613 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_614 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_615 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_616 | 3 Phase fault on LAR382 5 161.00 (547479) 161 kV Bus a. Apply fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_617 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_618 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_619 | 3 Phase fault on RVS438 5 161.00 (547497) 161 kV Bus a. Apply fault at the RVS438 5 161.00 (547497) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVS438 5 (547497) 161.0 kV to HOL478_5 (547626) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_620 | 3 Phase fault on BOL 73 2 69.000 (547528) 69 kV Bus a. Apply fault at the BOL 73 2 69.000 (547528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 2 (547528) 69.0 kV to BUF342 2 (547575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_621 | 3 Phase fault on BOL 73 2 69.000 (547528) 69 kV Bus a. Apply fault at the BOL 73 2 69.000 (547528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 2 (547528) 69.0 kV to BOL367 2 (547584) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_622 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_623 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to LAW260 2 (547552) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_624 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_625 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_626 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MON152 2 (547540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_627 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_628 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_629 | 3 Phase fault on MON152 2 69.000 (547540) 69 kV Bus a. Apply fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_630 | 3 Phase fault on FRP217 2 69.000 (547545) 69 kV Bus a. Apply fault at the FRP217 2 69.000 (547545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRP217 2 (547545) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_631 | 3 Phase fault on FRP217 2 69.000 (547545) 69 kV Bus a. Apply fault at the FRP217 2 69.000 (547545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRP217 2 (547545) 69.0 kV to BOL602 2 (547612) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_632 | 3 Phase fault on BIL221 2 69.000 (547546) 69 kV Bus a. Apply fault at the BIL221 2 69.000 (547546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIL221 2 (547546) 69.0 kV to REP359 2 (547580) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_633 | 3 Phase fault on BIL221 2 69.000 (547546) 69 kV Bus a. Apply fault at the BIL221 2 69.000 (547546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIL221 2 (547546) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_634 | 3 Phase fault on ARC250 2 69.000 (547549) 69 kV Bus a. Apply fault at the ARC250 2 69.000 (547549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARC250 2 (547549) 69.0 kV to GRN614 2 (547613) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_635 | 3 Phase fault on LAW260 2 69.000 (547552) 69 kV Bus a. Apply fault at the LAW260 2 69.000 (547552) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAW260 2 (547552) 69.0 kV to HTC338 2 (547573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_636 | 3 Phase fault on ALB262 2 69.000 (547553) 69 kV Bus a. Apply fault at the ALB262 2 69.000 (547553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALB262 2 (547553) 69.0 kV to HTC338 2 (547573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_637 | 3 Phase fault on ALB262 2 69.000 (547553) 69 kV Bus a. Apply fault at the ALB262 2 69.000 (547553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALB262 2 (547553) 69.0 kV to MTV463 2 (547619) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_638 | 3 Phase fault on TIP292 2 69.000 (547559) 69 kV Bus a. Apply fault at the TIP292 2 69.000 (547559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 2 (547559) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_639 | 3 Phase fault on OZD312 2 69.000 (547562) 69 kV Bus a. Apply fault at the OZD312 2 69.000 (547562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZD312 2 (547562) 69.0 kV to FOR410 2 (547603) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_640 | 3 Phase fault on MTV351 2 69.000 (547577) 69 kV Bus a. Apply fault at the MTV351 2 69.000 (547577) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTV351 2 (547577) 69.0 kV to MTV420 2 (547606) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_641 | 3 Phase fault on MTV351 2 69.000 (547577) 69 kV Bus a. Apply fault at the MTV351 2 69.000 (547577) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTV351 2 (547577) 69.0 kV to MTV463 2 (547619) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_642 | 3 Phase fault on MTV351 2 69.000 (547577) 69 kV Bus a. Apply fault at the MTV351 2 69.000 (547577) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTV351 2 (547577) 69.0 kV to MTV348 2 (547620) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_643 | 3 Phase fault on AUR355 2 69.000 (547578) 69 kV Bus a. Apply fault at the AUR355 2 69.000 (547578) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR355 2 (547578) 69.0 kV to MTV420 2 (547606) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_644 | 3 Phase fault on BOL367 2 69.000 (547584) 69 kV Bus a. Apply fault at the BOL367 2 69.000 (547584) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL367 2 (547584) 69.0 kV to BOL602 2 (547612) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_645 | 3 Phase fault on RNM393 2 69.000 (547595) 69 kV Bus a. Apply fault at the RNM393 2 69.000 (547595) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 2 (547595) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_646 | 3 Phase fault on LKW400 2 69.000 (547598) 69 kV Bus a. Apply fault at the LKW400 2 69.000 (547598) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKW400 2 (547598) 69.0 kV to GRN614 2 (547613) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_647 | 3 Phase fault on STK418 2 69.000 (547605) 69 kV Bus a. Apply fault at the STK418 2 69.000 (547605) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STK418 2 (547605) 69.0 kV to STK324J2 (547616) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_648 | 3 Phase fault on WIL369 2 69.000 (547691) 69 kV Bus a. Apply fault at the WIL369 2 69.000 (547691) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WIL369 2 (547691) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_649 | 3 Phase fault on WIL482 69.000 (547726) 69 kV Bus a. Apply fault at the WIL482 69.000 (547726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WIL482 (547726) 69.0 kV to WIL479 (547727) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_650 | 3 Phase fault on COX 269.000 (549910) 69 kV Bus a. Apply fault at the COX 269.000 (549910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_651 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to LAUREL 2 (549924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_652 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_653 | 3 Phase fault on DAYTON 269.000 (549913) 69 kV Bus a. Apply fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_654 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_655 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_656 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_657 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_658 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_659 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_660 | 3 Phase fault on MENTOR 5161.00 (549963) 161 kV Bus a. Apply fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_661 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_662 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_663 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_664 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5FRANKS (300078) 161.0 kV to 7FRANKS (300041) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_665 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5FRANKS (300078) 161.0 kV to 7FRANKS (300041) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_666 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 7HUBEN (300042) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_667 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_668 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLARK (300802) 69.0 kV to 5CLARK (300070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_669 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_670 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_671 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_672 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_673 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_674 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHRP (300302) 69.0 kV to 5LATHRP (300091) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_675 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MORGAN (300782) 69.0 kV to 5MORGAN (300101) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_676 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NORTON (300540) 69.0 kV to 5NORTON (300105) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_677 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_678 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_679 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_680 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_681 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_682 | 3 Phase fault on 5REEDSP 161.00 (301521) 161 kV Bus a. Apply fault at the 5REEDSP 161.00 (301521) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2REEDSP (300725) 69.0 kV to 5REEDSP (301521) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_683 | 3 Phase fault on 5RENOHLW 161.00 (301129) 161 kV Bus a. Apply fault at the 5RENOHLW 161.00 (301129) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2RENOHLW (300738) 69.0 kV to 5RENOHLW (301129) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_684 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_685 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_686 | 3 Phase fault on 5HYDERHL 161.00 (300793) 161 kV Bus a. Apply fault at the 5HYDERHL 161.00 (300793) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HYDERHL (300798) 69.0 kV to 5HYDERHL (300793) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_687 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_688 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_689 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_690 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_691 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_692 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_693 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_694 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_695 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_696 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_697 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_698 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_699 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_700 | 3 Phase fault on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138.0 kV to WAKITA 2 (521085) 69.0 kV to WAKITA_13.8 (520435) 13.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_701 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_702 | 3 Phase fault on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_703 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_704 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_705 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_706 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_707 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_708 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_709 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_710 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_711 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_712 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_713 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_714 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_715 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_716 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_717 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_718 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_719 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_720 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_721 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_722 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_723 | 3 Phase fault on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_724 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV to MOUN 2X1 (533097) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_725 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_726 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_727 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_728 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_729 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_730 | 3 Phase fault on HEC 3 115.00 (533419) 115 kV Bus a. Apply fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_731 | 3 Phase fault on 3 VANBU3 115.00 (533435) 115 kV Bus a. Apply fault at the 3 VANBU3 115.00 (533435) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3 VANBU3 (533435) 115.0 kV to 3 VANBU2 (533527) 69.0 kV to 3VANBUR1 (533446) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_732 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_733 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_734 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_735 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_736 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_737 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to None Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_738 | 3 Phase fault on NEVADA 5 161.00 (541208) 161 kV Bus a. Apply fault at the NEVADA 5 161.00 (541208) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 2 (541308) 69.0 kV to NEVADA 5 (541208) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_739 | 3 Phase fault on NEVADA 5 161.00 (541208) 161 kV Bus a. Apply fault at the NEVADA 5 161.00 (541208) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEVADA 2 (541308) 69.0 kV to NEVADA 5 (541208) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_740 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_741 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_742 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_743 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 2 (541269) 69.0 kV to WBURGE 5 (541228) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_744 | 3 Phase fault on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 2 (541267) 69.0 kV to ODESSA 5 (541229) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_745 | 3 Phase fault on LEX161 5 161.00 (541232) 161 kV Bus a. Apply fault at the LEX161 5 161.00 (541232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX69 2 (541264) 69.0 kV to LEX161 5 (541232) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_746 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_747 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to LBRTYST5 (541248) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_748 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_749 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_750 | 3 Phase fault on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_751 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_752 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_753 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_754 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH 12 (400) 13.8 kV Three Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_755 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to None Three Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_756 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_757 | 3 Phase fault on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_758 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_759 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_760 | 3 Phase fault on MON383 5 161.00 (547480) 161 kV Bus a. Apply fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_761 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_762 | 3 Phase fault on CPK446 5 161.00 (547499) 161 kV Bus a. Apply fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_763 | 3 Phase fault on RNM393 5 161.00 (547500) 161 kV Bus a. Apply fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_764 | 3 Phase fault on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STK418 2 (547605) 69.0 kV to 5STKAEC (300118) 161.0 kV to STK418 1 (547719) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_765 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_766 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_767 | 3 Phase fault on SUB M-161 161.00 (548814) 161 kV Bus a. Apply fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_768 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_769 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_770 | 3 Phase fault on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_771 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_772 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_773 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_774 | 3 Phase fault on 2BEARCK 69.000 (300713) 69 kV Bus a. Apply fault at the 2BEARCK 69.000 (300713) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEARCK (300713) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_775 | 3 Phase fault on 2REEDSP 69.000 (300725) 69 kV Bus a. Apply fault at the 2REEDSP 69.000 (300725) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2REEDSP (300725) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_776 | 3 Phase fault on 7FRANKSRCT 345.00 (301554) 345 kV Bus a. Apply fault at the 7FRANKSRCT 345.00 (301554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKSRCT (301554) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_777 | 3 Phase fault on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL3 (539701) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_778 | 3 Phase fault on MON383 2 69.000 (547591) 69 kV Bus a. Apply fault at the MON383 2 69.000 (547591) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 2 (547591) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_779 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_780 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_781 | 3 Phase fault on SUB M 69.000 (548815) 69 kV Bus a. Apply fault at the SUB M 69.000 (548815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_782 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_783 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_784 | 3 Phase fault on BOL431 5 161.00 (547493) 161 kV Bus a. Apply fault at the BOL431 5 161.00 (547493) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_785 | 3 Phase fault on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_786 | 3 Phase fault on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_787 | 3 Phase fault on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.4. NICHOL XF1 1 (549940) 13.2 kV to NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_788 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.3. MILL XF1 1 (549946) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_789 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 b.3. MILL XF2 1 (549948) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_790 | 3 Phase fault on 2BILLNG 69.000 (300658) 69 kV Bus a. Apply fault at the 2BILLNG 69.000 (300658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BILLNG (300658) 69.0 kV to BIL221 2 (547546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_791 | 3 Phase fault on 2BILLNG 69.000 (300658) 69 kV Bus a. Apply fault at the 2BILLNG 69.000 (300658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BILLNG (300658) 69.0 kV to CPK446 2 (547618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_792 | 3 Phase fault on 2BRNSPG 69.000 (300660) 69 kV Bus a. Apply fault at the 2BRNSPG 69.000 (300660) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BRNSPG (300660) 69.0 kV to 2CLEVER (300665) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_793 | 3 Phase fault on 2CASSIDY 69.000 (300663) 69 kV Bus a. Apply fault at the 2CASSIDY 69.000 (300663) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CASSIDY (300663) 69.0 kV to 2JAMESV (300673) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_794 | 3 Phase fault on 2CLEVER 69.000 (300665) 69 kV Bus a. Apply fault at the 2CLEVER 69.000 (300665) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEVER (300665) 69.0 kV to BIL221 2 (547546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_795 | 3 Phase fault on 2JAMESV 69.000 (300673) 69 kV Bus a. Apply fault at the 2JAMESV 69.000 (300673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to BHJ415 2 (547604) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_796 | 3 Phase fault on 2MTVRN 69.000 (300677) 69 kV Bus a. Apply fault at the 2MTVRN 69.000 (300677) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MTVRN (300677) 69.0 kV to CPK446 2 (547618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_797 | 3 Phase fault on 5STRAFFORD 161.00 (301368) 161 kV Bus a. Apply fault at the 5STRAFFORD 161.00 (301368) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STRAFFORD (301368) 161.0 kV to 5MCCARTNEY (301568) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_798 | 3 Phase fault on 5MCCARTNEY 161.00 (301568) 161 kV Bus a. Apply fault at the 5MCCARTNEY 161.00 (301568) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCCARTNEY (301568) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_799 | 3 Phase fault on HER209 2 69.000 (547425) 69 kV Bus a. Apply fault at the HER209 2 69.000 (547425) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HER209 2 (547425) 69.0 kV to BOL 73 2 (547528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_800 | 3 Phase fault on BUF243J2 69.000 (547432) 69 kV Bus a. Apply fault at the BUF243J2 69.000 (547432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUF243J2 (547432) 69.0 kV to BUF243 2 (547547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_801 | 3 Phase fault on BUF243J2 69.000 (547432) 69 kV Bus a. Apply fault at the BUF243J2 69.000 (547432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUF243J2 (547432) 69.0 kV to BUF342 2 (547575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_802 | 3 Phase fault on BUF243J2 69.000 (547432) 69 kV Bus a. Apply fault at the BUF243J2 69.000 (547432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUF243J2 (547432) 69.0 kV to FRG397 2 (547596) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_803 | 3 Phase fault on STRKAMO2 69.000 (547433) 69 kV Bus a. Apply fault at the STRKAMO2 69.000 (547433) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRKAMO2 (547433) 69.0 kV to STR370 2 (547587) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_804 | 3 Phase fault on STRKAMO2 69.000 (547433) 69 kV Bus a. Apply fault at the STRKAMO2 69.000 (547433) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRKAMO2 (547433) 69.0 kV to BHJ415 2 (547604) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_805 | 3 Phase fault on BUF409 2 69.000 (547434) 69 kV Bus a. Apply fault at the BUF409 2 69.000 (547434) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUF409 2 (547434) 69.0 kV to BUF342 2 (547575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_806 | 3 Phase fault on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUPTAP 2 (547436) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_807 | 3 Phase fault on EXP450T2 69.000 (547440) 69 kV Bus a. Apply fault at the EXP450T2 69.000 (547440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP450T2 (547440) 69.0 kV to EXP4502 (547441) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_808 | 3 Phase fault on EXP450T2 69.000 (547440) 69 kV Bus a. Apply fault at the EXP450T2 69.000 (547440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP450T2 (547440) 69.0 kV to BOL 73 2 (547528) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_809 | 3 Phase fault on EXP450T2 69.000 (547440) 69 kV Bus a. Apply fault at the EXP450T2 69.000 (547440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP450T2 (547440) 69.0 kV to BRT323 2 (547567) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_810 | 3 Phase fault on OZK457 2 69.000 (547442) 69 kV Bus a. Apply fault at the OZK457 2 69.000 (547442) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZK457 2 (547442) 69.0 kV to OZK434 2 (547609) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_811 | 3 Phase fault on REP451 2 69.000 (547443) 69 kV Bus a. Apply fault at the REP451 2 69.000 (547443) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REP451 2 (547443) 69.0 kV to REP345 2 (547576) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_812 | 3 Phase fault on REP451 2 69.000 (547443) 69 kV Bus a. Apply fault at the REP451 2 69.000 (547443) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REP451 2 (547443) 69.0 kV to REP359 2 (547580) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_813 | 3 Phase fault on BOL 73 2 69.000 (547528) 69 kV Bus a. Apply fault at the BOL 73 2 69.000 (547528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 2 (547528) 69.0 kV to BUF342 2 (547575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_814 | 3 Phase fault on BOL 73 2 69.000 (547528) 69 kV Bus a. Apply fault at the BOL 73 2 69.000 (547528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 2 (547528) 69.0 kV to BOL367 2 (547584) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_815 | 3 Phase fault on SED 80 2 69.000 (547529) 69 kV Bus a. Apply fault at the SED 80 2 69.000 (547529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SED 80 2 (547529) 69.0 kV to BRT323 2 (547567) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_816 | 3 Phase fault on SED 80 2 69.000 (547529) 69 kV Bus a. Apply fault at the SED 80 2 69.000 (547529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SED 80 2 (547529) 69.0 kV to FRG397 2 (547596) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_817 | 3 Phase fault on SED 80 2 69.000 (547529) 69 kV Bus a. Apply fault at the SED 80 2 69.000 (547529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SED 80 2 (547529) 69.0 kV to WIL479 (547727) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_818 | 3 Phase fault on SED 80 2 69.000 (547529) 69 kV Bus a. Apply fault at the SED 80 2 69.000 (547529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SED 80 2 (547529) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_819 | 3 Phase fault on NIX114 2 69.000 (547535) 69 kV Bus a. Apply fault at the NIX114 2 69.000 (547535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIX114 2 (547535) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_820 | 3 Phase fault on NIX114 2 69.000 (547535) 69 kV Bus a. Apply fault at the NIX114 2 69.000 (547535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIX114 2 (547535) 69.0 kV to BHJ415 2 (547604) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_821 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to LAW260 2 (547552) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_822 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_823 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_824 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_825 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to REP345 2 (547576) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_826 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_827 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_828 | 3 Phase fault on FRP217 2 69.000 (547545) 69 kV Bus a. Apply fault at the FRP217 2 69.000 (547545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRP217 2 (547545) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_829 | 3 Phase fault on BIL221 2 69.000 (547546) 69 kV Bus a. Apply fault at the BIL221 2 69.000 (547546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIL221 2 (547546) 69.0 kV to REP359 2 (547580) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_830 | 3 Phase fault on BIL221 2 69.000 (547546) 69 kV Bus a. Apply fault at the BIL221 2 69.000 (547546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIL221 2 (547546) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_831 | 3 Phase fault on LAW260 2 69.000 (547552) 69 kV Bus a. Apply fault at the LAW260 2 69.000 (547552) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAW260 2 (547552) 69.0 kV to HTC338 2 (547573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_832 | 3 Phase fault on OZK330 2 69.000 (547570) 69 kV Bus a. Apply fault at the OZK330 2 69.000 (547570) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZK330 2 (547570) 69.0 kV to BHJ415 2 (547604) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_833 | 3 Phase fault on OZK330 2 69.000 (547570) 69 kV Bus a. Apply fault at the OZK330 2 69.000 (547570) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZK330 2 (547570) 69.0 kV to OZK434 2 (547609) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_834 | 3 Phase fault on BOL367 2 69.000 (547584) 69 kV Bus a. Apply fault at the BOL367 2 69.000 (547584) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL367 2 (547584) 69.0 kV to BOL602 2 (547612) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_835 | 3 Phase fault on STR370 2 69.000 (547587) 69 kV Bus a. Apply fault at the STR370 2 69.000 (547587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STR370 2 (547587) 69.0 kV to FRG397 2 (547596) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_836 | 3 Phase fault on WIL369 2 69.000 (547691) 69 kV Bus a. Apply fault at the WIL369 2 69.000 (547691) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WIL369 2 (547691) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_837 | 3 Phase fault on WIL482 69.000 (547726) 69 kV Bus a. Apply fault at the WIL482 69.000 (547726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WIL482 (547726) 69.0 kV to WIL479 (547727) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_838 | 3 Phase fault on HIGHWAY M 269.000 (549909) 69 kV Bus a. Apply fault at the HIGHWAY M 269.000 (549909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHWAY M 2 (549909) 69.0 kV to BLACKMAN 2 (549916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_839 | 3 Phase fault on COX 269.000 (549910) 69 kV Bus a. Apply fault at the COX 269.000 (549910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_840 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to LAUREL 2 (549924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_841 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_842 | 3 Phase fault on GALLOWAY 269.000 (549915) 69 kV Bus a. Apply fault at the GALLOWAY 269.000 (549915) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALLOWAY 2 (549915) 69.0 kV to BLACKMAN 2 (549916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_843 | 3 Phase fault on BLACKMAN 269.000 (549916) 69 kV Bus a. Apply fault at the BLACKMAN 269.000 (549916) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKMAN 2 (549916) 69.0 kV to INGRAM 2 (549917) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_844 | 3 Phase fault on BLACKMAN 269.000 (549916) 69 kV Bus a. Apply fault at the BLACKMAN 269.000 (549916) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLACKMAN 2 (549916) 69.0 kV to MILL 2 (549918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_845 | 3 Phase fault on INGRAM 269.000 (549917) 69 kV Bus a. Apply fault at the INGRAM 269.000 (549917) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INGRAM 2 (549917) 69.0 kV to MILL 2 (549918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_846 | 3 Phase fault on MILL 269.000 (549918) 69 kV Bus a. Apply fault at the MILL 269.000 (549918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 2 (549918) 69.0 kV to CHAD 2 (549919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_847 | 3 Phase fault on MILL 269.000 (549918) 69 kV Bus a. Apply fault at the MILL 269.000 (549918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 2 (549918) 69.0 kV to PACKER 2 (549932) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_848 | 3 Phase fault on CHAD 269.000 (549919) 69 kV Bus a. Apply fault at the CHAD 269.000 (549919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAD 2 (549919) 69.0 kV to HARGISS 2 (549920) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_849 | 3 Phase fault on HARGISS 269.000 (549920) 69 kV Bus a. Apply fault at the HARGISS 269.000 (549920) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARGISS 2 (549920) 69.0 kV to MAIN STREET2 (549921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_850 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to GRAND 2 (549922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_851 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_852 | 3 Phase fault on GRAND 269.000 (549922) 69 kV Bus a. Apply fault at the GRAND 269.000 (549922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 2 (549922) 69.0 kV to MONROE 2 (549923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_853 | 3 Phase fault on LAUREL 269.000 (549924) 69 kV Bus a. Apply fault at the LAUREL 269.000 (549924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAUREL 2 (549924) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_854 | 3 Phase fault on NICHOLS 269.000 (549925) 69 kV Bus a. Apply fault at the NICHOLS 269.000 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 2 (549925) 69.0 kV to FRISCO 2 (549926) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_855 | 3 Phase fault on FRISCO 269.000 (549926) 69 kV Bus a. Apply fault at the FRISCO 269.000 (549926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRISCO 2 (549926) 69.0 kV to N HWY13 2 (549927) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_856 | 3 Phase fault on N HWY13 269.000 (549927) 69 kV Bus a. Apply fault at the N HWY13 269.000 (549927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HWY13 2 (549927) 69.0 kV to NORTON 2 (549928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_857 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_858 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to NEERGARD 2 (549930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_859 | 3 Phase fault on NEERGARD 269.000 (549930) 69 kV Bus a. Apply fault at the NEERGARD 269.000 (549930) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEERGARD 2 (549930) 69.0 kV to LECOMPTE 2 (549931) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_860 | 3 Phase fault on LECOMPTE 269.000 (549931) 69 kV Bus a. Apply fault at the LECOMPTE 269.000 (549931) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LECOMPTE 2 (549931) 69.0 kV to PACKER 2 (549932) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_861 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_862 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_863 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_864 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_865 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_866 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_867 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_868 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_869 | 3 Phase fault on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_870 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_871 | 3 Phase fault on CPK446 5 161.00 (547499) 161 kV Bus a. Apply fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_872 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_873 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_874 | 3 Phase fault on NORTON 5161.00 (549967) 161 kV Bus a. Apply fault at the NORTON 5161.00 (549967) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (549967) 161.0 kV to NORTON 2 (549928) 69.0 kV to NORTON XF1 1 (549942) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_875 | 3 Phase fault on OZK434 2 69.000 (547609) 69 kV Bus a. Apply fault at the OZK434 2 69.000 (547609) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZK434 2 (547609) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_876 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_001 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_002 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_003 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_004 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_005 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_006 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_007 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_008 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_009 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_010 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_011 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-221GEN1 (760307) and G17-227GEN1 (760664). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_013 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_014 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_015 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_016 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_017 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_018 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_019 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_020 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_021 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_022 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_023 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. This is issue is also oberved in PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_024 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_025 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_026 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_027 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_028 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_029 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_030 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_031 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G11-008-GEN7 (539858). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_032 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequnecy protection trips G11-008-GEN7 (539858). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_033 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_036 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_037 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_038 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_039 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_040 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_041 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_042 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_043 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_044 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_045 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_046 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_048 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_049 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_051 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.4. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.5. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.6. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.7. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.8. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.9. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.10. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.11. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.12. BELOIT 3 (539650) 115.0 kV to BELOIT 1 (539750) 34.5 kV to BELOIT-T (539901) 7.2 kV Three Winding #1 b.13. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 b.14. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 b.15. SMITH-C3 (539693) 115.0 kV to SMITH-C1 (539731) 34.5 kV to SMITHC-T (539934) 7.2 kV Three Winding #1 b.16. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 b.17. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-T (539943) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on MAIZE 4 138.00 (533054) 138 kV Bus a. Apply Fault at the MAIZE 4 138.00 (533054) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply Fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 b.2. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.3. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.3. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 b.4. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on SLATECRK4 138.00 (533070) 138 kV Bus a. Apply Fault at the SLATECRK4 138.00 (533070) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. CRESWLN4 (532981) 138.0 kV to SLATECRK4 (533070) 138.0 kV Transmission Circuit #1 b.3. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.4. SLATEXFMR1 (533139) 34.5 kV to SLATEGSU1 (533140) 34.5 kV Transmission Circuit #1 b.5. SLATEGEN1 (533141) 0.7 kV to SLATEGSU1 (533140) 34.5 kV Two Winding #1 b.6. SLATECRK4 (533070) 138.0 kV to SLATEXFMR1 (533139) 34.5 kV to SLATETV1 (533142) 13.2 kV Three Winding #1 b.7. CRESW1 1 (533080) 13.2 kV to CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on MIDLTNT4 138.00 (514804) 138 kV Bus a. Apply Fault at the MIDLTNT4 138.00 (514804) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.4. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.7. MIDLTNT4 (514804) 138.0 kV to GEN-2016-071 (587480) 138.0 kV Transmission Circuit #1 b.8. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.9. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.4. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.6. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.7. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT1 (532723) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply Fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.5. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 b.6. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GILL W 4 138.00 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.6. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.3. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.4. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.5. SUMNER 4 (532984) 138.0 kV to GEN-2017-121 (761838) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on 3 VANBU3 115.00 (533435) 115 kV Bus a. Apply Fault at the 3 VANBU3 115.00 (533435) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.2. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 b.3. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.4. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.5. 3 VANBU3 (533435) 115.0 kV to 3 VANBU2 (533527) 69.0 kV to 3VANBUR1 (533446) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.4. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 b.5. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.6. CIRCLE 3 (533413) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.2. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 b.5. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on HEC GT 3 115.00 (533421) 115 kV Bus a. Apply Fault at the HEC GT 3 115.00 (533421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.5. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on MANVILE3 115.00 (533426) 115 kV Bus a. Apply Fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to MCPHGT4 (532705) 13.8 kV Two Winding #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply Fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to MCPHGT3 (532704) 13.8 kV Two Winding #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.4. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.2. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.3. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.3. LANG 3 (533304) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.4. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.5. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.2. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. RENO 1X1 (532807) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. RENO 2X1 (532810) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on RENO 3 115.00 (533416) 115 kV Bus a. Apply Fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit #1 b.3. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.2. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.7. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.8. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.2. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.3. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 b.5. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on 7CALAWY 1 345.00 (344224) 345 kV Bus a. Apply Fault at the 7CALAWY 1 345.00 (344224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7CALAWY 1 (344224) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.6. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.7. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 b.8. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 b.9. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on 5HARRISON.E!161.00 (338104) 161 kV Bus a. Apply Fault at the 5HARRISON.E!161.00 (338104) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HARRISON.E! (338104) 161.0 kV to 5OMAHA+ (338105) 161.0 kV Transmission Circuit #1 b.2. 5HARRISON.E! (338104) 161.0 kV to 5EVERTON RD (338107) 161.0 kV Transmission Circuit #1 b.3. 5HARRISON.E! (338104) 161.0 kV to 5SUMMIT (338121) 161.0 kV Transmission Circuit #1 b.4. 5HARRISON.E! (338104) 161.0 kV to 5HARRISON.S# (338681) 161.0 kV Transmission Circuit #1 b.5. 5OMAHA+ (338105) 161.0 kV to OZD312 5 (547474) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply Fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 b.2. 5PERCHE (343004) 161.0 kV to 2PERCHE (343005) 69.0 kV Two Winding #1 b.3. 5PERCHE (343004) 161.0 kV to 2PERCHE2 (343052) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load #1 b.4. SALSBRY5 (543062) 161.0 kV to Load #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply Fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.3. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.4. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.4. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on OZD312 5 161.00 (547474) 161 kV Bus a. Apply Fault at the OZD312 5 161.00 (547474) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OMAHA+ (338105) 161.0 kV to OZD312 5 (547474) 161.0 kV Transmission Circuit #1 b.2. OZD312 5 (547474) 161.0 kV to BRN331 5 (547475) 161.0 kV Transmission Circuit #1 b.3. OZD312 5 (547474) 161.0 kV to HOL387 5 (547482) 161.0 kV Transmission Circuit #1 b.4. OZD312 5 (547474) 161.0 kV to OZD312 1 (547648) 4.6 kV Two Winding #1 b.5. OZD312 5 (547474) 161.0 kV to OZD312 2 (547562) 69.0 kV to OZD312T1 (547710) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.4. DAD368 5 (547478) 161.0 kV to GEN-2019-016 (763560) 161.0 kV Transmission Circuit #1 b.5. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.4. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on CPK446 5 161.00 (547499) 161 kV Bus a. Apply Fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.3. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply Fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.4. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.5. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.6. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on OZD312 5 161.00 (547474) 161 kV Bus a. Apply Fault at the OZD312 5 161.00 (547474) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OMAHA+ (338105) 161.0 kV to OZD312 5 (547474) 161.0 kV Transmission Circuit #1 b.2. OZD312 5 (547474) 161.0 kV to BRN331 5 (547475) 161.0 kV Transmission Circuit #1 b.3. OZD312 5 (547474) 161.0 kV to HOL387 5 (547482) 161.0 kV Transmission Circuit #1 b.4. OZD312 5 (547474) 161.0 kV to OZD312 1 (547648) 4.6 kV Two Winding #1 b.5. BRN331 5 (547475) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 b.6. OZD312 5 (547474) 161.0 kV to OZD312 2 (547562) 69.0 kV to OZD312T1 (547710) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 b.2. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.4. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.5. DAD368 5 (547478) 161.0 kV to GEN-2019-016 (763560) 161.0 kV Transmission Circuit #1 b.6. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on BRN412 5 161.00 (547488) 161 kV Bus a. Apply Fault at the BRN412 5 161.00 (547488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 b.2. OZD312 5 (547474) 161.0 kV to BRN331 5 (547475) 161.0 kV Transmission Circuit #1 b.3. BRN331 5 (547475) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 b.4. BRN412 5 (547488) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on BRN412 5 161.00 (547488) 161 kV Bus a. Apply Fault at the BRN412 5 161.00 (547488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 b.2. BRN331 5 (547475) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 b.3. BRN412 5 (547488) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 b.4. BRN413 5 (547489) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on GRT433 5 161.00 (547495) 161 kV Bus a. Apply Fault at the GRT433 5 161.00 (547495) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRN412 5 (547488) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 b.2. BRN413 5 (547489) 161.0 kV to GRT433 5 (547495) 161.0 kV Transmission Circuit #1 b.3. BRN413 5 (547489) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on RDS295 5 161.00 (547473) 161 kV Bus a. Apply Fault at the RDS295 5 161.00 (547473) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on RVS438 5 161.00 (547497) 161 kV Bus a. Apply Fault at the RVS438 5 161.00 (547497) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.2. OZD312 5 (547474) 161.0 kV to HOL387 5 (547482) 161.0 kV Transmission Circuit #1 b.3. HOL387 5 (547482) 161.0 kV to HOL478_5 (547626) 161.0 kV Transmission Circuit #1 b.4. BRN413 5 (547489) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.5. RVS438 5 (547497) 161.0 kV to HOL478_5 (547626) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 b.4. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on OZD312 5 161.00 (547474) 161 kV Bus a. Apply Fault at the OZD312 5 161.00 (547474) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OMAHA+ (338105) 161.0 kV to OZD312 5 (547474) 161.0 kV Transmission Circuit #1 b.2. OZD312 5 (547474) 161.0 kV to BRN331 5 (547475) 161.0 kV Transmission Circuit #1 b.3. OZD312 5 (547474) 161.0 kV to HOL387 5 (547482) 161.0 kV Transmission Circuit #1 b.4. OZD312 5 (547474) 161.0 kV to OZD312 1 (547648) 4.6 kV Two Winding #1 b.5. HOL387 5 (547482) 161.0 kV to HOL478_5 (547626) 161.0 kV Transmission Circuit #1 b.6. OZD312 5 (547474) 161.0 kV to OZD312 2 (547562) 69.0 kV to OZD312T1 (547710) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply Fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.3. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.4. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 b.3. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply Fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 b.3. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 b.4. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 b.5. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on CORONAD3 115.00 (533394) 115 kV Bus a. Apply Fault at the CORONAD3 115.00 (533394) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 b.2. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEC 2 (533513) 69.0 kV to HEC GT 2 (533514) 69.0 kV Transmission Circuit #1 b.2. HEC 2 (533513) 69.0 kV to 17HALST2 (533521) 69.0 kV Transmission Circuit #1 b.3. HEC 2 (533513) 69.0 kV to HEC 3 (533419) 115.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 b.4. MOORLND4 (520999) 138.0 kV to MORLND1 (520996) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply Fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 b.2. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.3. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 b.4. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on BLUVLY 161.00 (548806) 69 kV Bus a. Apply Fault at the BLUVLY 161.00 (548806) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.3. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.4. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.5. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 b.6. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 b.7. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 b.8. BLU VAL 1 (548833) 14.4 kV to BLUVLY (548806) 69.0 kV Two Winding #1 b.9. BLU VAL 2 (548834) 14.4 kV to BLUVLY (548806) 69.0 kV Two Winding #1 b.10. BLU VAL 3 (548835) 13.8 kV to BLUVLY (548806) 69.0 kV Two Winding #1 b.11. BLUVLY (548806) 69.0 kV to Load #T1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. BLUMILS5 (543004) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on JTEC 5161.00 (549954) 161 kV Bus a. Apply Fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 b.2. JTEC GEN#1 1 (549890) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.3. JTEC CTS 1 (549891) 12.5 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.4. JTEC GEN#2 1 (549893) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.5. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.6. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.7. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 b.4. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.4. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply Fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JRPS GT1 1 (549900) 13.8 kV to JAMES RIVER5 (549961) 161.0 kV Two Winding #1 b.2. JRPS GT2 1 (549901) 13.8 kV to JAMES RIVER5 (549961) 161.0 kV Two Winding #1 b.3. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.4. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 b.5. JAMES RIVER5 (549961) 161.0 kV to JRPS 69B-2 2 (549903) 69.0 kV to JRPS XF2 1 (549945) 13.2 kV Three Winding #1 b.6. JAMES RIVER5 (549961) 161.0 kV to JAMES RIVER2 (549904) 69.0 kV to JRPS XF1 1 (549944) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on MILL 5161.00 (549962) 161 kV Bus a. Apply Fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.3. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.4. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on MENTOR 5161.00 (549963) 161 kV Bus a. Apply Fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 b.2. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.5. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.6. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on CLAY 5161.00 (549970) 161 kV Bus a. Apply Fault at the CLAY 5161.00 (549970) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.3. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.4. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on PIC WEST 5161.00 (549971) 161 kV Bus a. Apply Fault at the PIC WEST 5161.00 (549971) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. BLUMILS5 (543004) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on BLUVLY 69.00 (548806) 69 kV Bus a. Apply Fault at the BLUVLY 69.00 (548806) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY (548806) 69.0 kV to Load #T2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on TWR 33 3 115.00 (533455) 115 kV Bus a. Apply Fault at the TWR 33 3 115.00 (533455) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.2. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.4. SPF X3 1 (505495) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 b.4. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on STOCKTN5 161.00 (505498) 161 kV Bus a. Apply Fault at the STOCKTN5 161.00 (505498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5STKAEC (300118) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 b.2. STOCKTN5 (505498) 161.0 kV to STK #1 1 (505500) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on STOCKTN5 161.00 (505498) 161 kV Bus a. Apply Fault at the STOCKTN5 161.00 (505498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 b.2. STOCKTN5 (505498) 161.0 kV to STK #1 1 (505500) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on TABLE R5 161.00 (505472) 161 kV Bus a. Apply Fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5RENOHLWTP (300130) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 b.2. 5RENOHLWTP (300130) 161.0 kV to 5RIVERSIDE (300805) 161.0 kV Transmission Circuit #1 b.3. 5RENOHLWTP (300130) 161.0 kV to 5RENOHLW (301129) 161.0 kV Transmission Circuit #1 b.4. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.5. 5COMPTN (300719) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 b.6. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.7. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.8. TABLE R5 (505472) 161.0 kV to TBR1&2 1 (505476) 13.8 kV Two Winding #1 b.9. TABLE R5 (505472) 161.0 kV to TBR3&4 1 (505478) 13.8 kV Two Winding #1 b.10. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.11. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.12. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.13. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on TABLE R5 161.00 (505472) 161 kV Bus a. Apply Fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.3. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.4. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.5. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.6. TABLE R5 (505472) 161.0 kV to TBR1&2 1 (505476) 13.8 kV Two Winding #1 b.7. TABLE R5 (505472) 161.0 kV to TBR3&4 1 (505478) 13.8 kV Two Winding #1 b.8. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.9. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.10. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.11. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.2. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.3. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.5. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.6. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.7. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.8. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 b.2. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.5. SPF X1 1 (505491) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ASHGRV (300657) 69.0 kV to 2CAVESP (300664) 69.0 kV Transmission Circuit #1 b.2. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 b.3. 2ASHGRV (300657) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 b.4. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 b.5. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 b.6. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #2 b.7. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply Fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.4. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.5. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 b.7. TRUMAN 5 (505502) 161.0 kV to TRU123 1 (505504) 13.8 kV Two Winding #1 b.8. TRUMAN 5 (505502) 161.0 kV to TRU456 1 (505506) 13.8 kV Two Winding #1 b.9. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.5. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.6. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.7. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply Fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.4. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on NOELSW 4 138.00 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 138.00 (520430) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply Fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.2. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 b.3. WAKTASW4 (520434) 138.0 kV to WAKITA 2 (521085) 69.0 kV to WAKITA_13.8 (520435) 13.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply Fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 b.3. WAKTASW4 (520434) 138.0 kV to WAKITA 2 (521085) 69.0 kV to WAKITA_13.8 (520435) 13.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply Fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 b.3. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.4. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on DRIFTWD4 138.00 (521200) 138 kV Bus a. Apply Fault at the DRIFTWD4 138.00 (521200) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.2. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.3. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.4. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on DRIFTWD4 138.00 (521200) 138 kV Bus a. Apply Fault at the DRIFTWD4 138.00 (521200) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.2. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 b.3. DRFTWDTERT (521185) 13.8 kV to DRIFTWD4 (521200) 138.0 kV to DRIFTWD2 (521201) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.4. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.7. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.8. HARPER 4 (539668) 138.0 kV to HARPER 1 (539713) 34.5 kV to HARPER-T (539913) 8.7 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.3. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply Fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 b.2. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.3. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.4. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.8. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.2. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.3. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.4. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.6. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.9. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.2. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.3. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 b.4. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 b.5. HOLCOMB3 (531448) 115.0 kV to Load #S1 b.6. HOLCOMB3 (531448) 115.0 kV to Load #S2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply Fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. FTDODGP1 (539670) 15.0 kV to FTDODGE3 (539671) 115.0 kV Two Winding #1 b.4. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.5. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 b.6. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. FTDODGE3 (539671) 115.0 kV to FTDDGDV1 (539715) 34.5 kV to FTDODG-T (539915) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.3. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CIM-PLT3 (539654) 115.0 kV to CIM-PLT (539780) 13.8 kV Two Winding #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply Fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.2. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply Fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.6. NKMA2 1 (530630) 12.5 kV to NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.4. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.5. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.4. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.5. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply Fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on VINETAP3 115.00 (530693) 115 kV Bus a. Apply Fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.5. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.6. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.7. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on NESCTY 3 115.00 (530607) 115 kV Bus a. Apply Fault at the NESCTY 3 115.00 (530607) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NESCTY 3 (530607) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NESCTY 3 (530607) 115.0 kV to NESS-CT1 (539722) 34.5 kV to NES-CT-T (539924) 13.8 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.9. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.10. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on BUSHTON3 115.00 (530681) 115 kV Bus a. Apply Fault at the BUSHTON3 115.00 (530681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit #1 b.2. BUSHTON3 (530681) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on RICE 6 230.00 (530686) 230 kV Bus a. Apply Fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit #1 b.2. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit #1 b.2. RICE 3 (530623) 115.0 kV to Load #1 b.3. RICE 3 (530623) 115.0 kV to Load #K1 b.4. RICE 3 (530623) 115.0 kV to Load #K2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. RICE 3 (530623) 115.0 kV to Load #1 b.3. RICE 3 (530623) 115.0 kV to Load #K1 b.4. RICE 3 (530623) 115.0 kV to Load #K2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. RICE 3 (530623) 115.0 kV to BUSHTON3 (530681) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on PAWN-ED3 115.00 (530622) 115 kV Bus a. Apply Fault at the PAWN-ED3 115.00 (530622) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARDS3 (530617) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.2. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.3. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.4. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.5. KINSLEY3 (530619) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.6. PAWNEE 3 (530621) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.7. PAWNEE 3 (530621) 115.0 kV to LARNED3 (530685) 115.0 kV Transmission Circuit #1 b.8. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.9. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.10. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on VINETAP3 115.00 (530693) 115 kV Bus a. Apply Fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.4. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.5. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.5. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.7. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on SHAYS_230 230.00 (530610) 230 kV Bus a. Apply Fault at the SHAYS_230 230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on BUFLOCRK6 230.00 (530688) 230 kV Bus a. Apply Fault at the BUFLOCRK6 230.00 (530688) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.3. BUFLOCRK1 (530689) 34.5 kV to PRWNDCL1 (530701) 34.5 kV Transmission Circuit #1 b.4. PRWINDG1 (530690) 0.7 kV to PRWNDCL1 (530701) 34.5 kV Two Winding #1 b.5. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.8. BUFLOCRK6 (530688) 230.0 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on RICE 3 115.00 (530623) 115 kV Bus a. Apply Fault at the RICE 3 115.00 (530623) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.4. RICE 3 (530623) 115.0 kV to Load #1 b.5. RICE 3 (530623) 115.0 kV to Load #K1 b.6. RICE 3 (530623) 115.0 kV to Load #K2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to Load #1 b.2. LYONS 3 (530620) 115.0 kV to Load #E1 b.3. LYONS 3 (530620) 115.0 kV to Load #K1 b.4. LYONS 3 (530620) 115.0 kV to Load #K2 b.5. LYONS 3 (530620) 115.0 kV to Load #K3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on COYOTE 4 138.00 (515581) 138 kV Bus a. Apply Fault at the COYOTE 4 138.00 (515581) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. COYOTE 4 (515581) 138.0 kV to BLUFCRK4 (520447) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. GRANTCO4 (515546) 138.0 kV to GRANTCO2 (515547) 69.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 b.5. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on GRANTCO2 69.000 (515547) 69 kV Bus a. Apply Fault at the GRANTCO2 69.000 (515547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. GRANTCO4 (515546) 138.0 kV to GRANTCO2 (515547) 69.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 b.5. GRANTCO2 (515547) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. GRANTCO4 (515546) 138.0 kV to GRANTCO2 (515547) 69.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.4. GRANTCO4 (515546) 138.0 kV to GRANTCO2 (515547) 69.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALVAOGE2 (514792) 69.0 kV to KNOBHIL2 (514794) 69.0 kV Transmission Circuit #1 b.2. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.4. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.5. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 b.6. KNOBHIL2 (514794) 69.0 kV to KNOBHIL4 (514795) 138.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. MATHWSN7 (515497) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on REDNGTN7 345.00 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 345.00 (515875) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. REDNGTN7 (515875) 345.0 kV to REDDIRT7 (515877) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on RENFROW4 138.00 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on RENFROW4 138.00 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to RCKFALL4 (515427) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to RCKFALL4 (515427) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTER 4 (514708) 138.0 kV to WOODRNG4 (514714) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 b.5. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on WOODRNG4 138.00 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 138.00 (514714) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to MARSHL 4 (514733) 138.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 b.5. WOODRNG4 (514714) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 b.2. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWRDEHV4 (515376) 138.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to REDNGTN7 (515875) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to SKELTON7 (515990) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on 5CLARK 161.00 (300070) 161 kV Bus a. Apply Fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 b.2. 5CLARK (300070) 161.0 kV to 2CLARK (300802) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 b.2. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 b.2. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply Fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JAMESV (300089) 161.0 kV to 5RIVRDL (300726) 161.0 kV Transmission Circuit #1 b.2. 5JAMESV (300089) 161.0 kV to 5BTLFD (300348) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply Fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LATHRP (300091) 161.0 kV to 5MPLTAP (300036) 161.0 kV Transmission Circuit #1 b.2. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply Fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 b.2. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply Fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to 5MORGANXF2 (301622) 161.0 kV Transmission Circuit #1 b.2. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on 5NORTON 161.00 (300105) 161 kV Bus a. Apply Fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 b.2. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply Fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOL (301040) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to 2SEDALI (300541) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply Fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5STKAEC (300118) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 b.2. 5STKAEC (300118) 161.0 kV to 5HYDERHL (300793) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply Fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply Fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply Fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 b.2. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply Fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SMTHTN (300542) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 b.2. 2SMTHTN (300542) 69.0 kV to 2FLORNC (300553) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on 2BILLNG 69.000 (300658) 69 kV Bus a. Apply Fault at the 2BILLNG 69.000 (300658) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BILLNG (300658) 69.0 kV to CPK446 2 (547618) 69.0 kV Transmission Circuit #1 b.2. 2BILLNG (300658) 69.0 kV to BIL221 2 (547546) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on 2CAPEFR 69.000 (300662) 69 kV Bus a. Apply Fault at the 2CAPEFR 69.000 (300662) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CAPEFR (300662) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 b.2. 2CAPEFR (300662) 69.0 kV to 2FLTCRK (300671) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply Fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2DADEVL (300668) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 b.2. 2DADEVL (300668) 69.0 kV to 2GRNFLD (300672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on 2MTVRN 69.000 (300677) 69 kV Bus a. Apply Fault at the 2MTVRN 69.000 (300677) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MTVRN (300677) 69.0 kV to CPK446 2 (547618) 69.0 kV Transmission Circuit #1 b.2. 2MTVRN (300677) 69.0 kV to 2MIDWYTP (300684) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on 2VERONA 69.000 (300680) 69 kV Bus a. Apply Fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 b.2. 2VERONA (300680) 69.0 kV to 2PRDYTP (300679) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on 2BEARCK 69.000 (300713) 69 kV Bus a. Apply Fault at the 2BEARCK 69.000 (300713) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BEARCK (300713) 69.0 kV to 2GRTNA (300720) 69.0 kV Transmission Circuit #1 b.2. 2BEARCK (300713) 69.0 kV to 2ROCKWY (300728) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on 2BLUWTP 69.000 (300714) 69 kV Bus a. Apply Fault at the 2BLUWTP 69.000 (300714) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BLUWTP (300714) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 b.2. 2BLUWTP (300714) 69.0 kV to 2KMBRLNTP (300721) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on 2GRTNA 69.000 (300720) 69 kV Bus a. Apply Fault at the 2GRTNA 69.000 (300720) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GRTNA (300720) 69.0 kV to 2REEDSP (300725) 69.0 kV Transmission Circuit #1 b.2. 2GRTNA (300720) 69.0 kV to 2BEARCK (300713) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on 2KMBRLNTP 69.000 (300721) 69 kV Bus a. Apply Fault at the 2KMBRLNTP 69.000 (300721) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2KMBRLNTP (300721) 69.0 kV to 2BLUWTP (300714) 69.0 kV Transmission Circuit #1 b.2. 2KMBRLNTP (300721) 69.0 kV to 2STONBR (300733) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on 2LAKE-K 69.000 (300722) 69 kV Bus a. Apply Fault at the 2LAKE-K 69.000 (300722) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LAKE-K (300722) 69.0 kV to 2REEDSP (300725) 69.0 kV Transmission Circuit #1 b.2. 2LAKE-K (300722) 69.0 kV to 2SILDOL (300730) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on 2SILDOL 69.000 (300730) 69 kV Bus a. Apply Fault at the 2SILDOL 69.000 (300730) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SILDOL (300730) 69.0 kV to 2T.ROCKSW (301360) 69.0 kV Transmission Circuit #1 b.2. 2SILDOL (300730) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on 2STULTS 69.000 (300734) 69 kV Bus a. Apply Fault at the 2STULTS 69.000 (300734) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STULTS (300734) 69.0 kV to 2RENOHLW (300738) 69.0 kV Transmission Circuit #1 b.2. 2STULTS (300734) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply Fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2EUDORA (300774) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 b.2. 2EUDORA (300774) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply Fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5COLLINS (300816) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 b.2. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on 5MCBAINB2 161.00 (301489) 161 kV Bus a. Apply Fault at the 5MCBAINB2 161.00 (301489) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5MCBAINB2 (301489) 161.0 kV to 5MCBAINB1 (300501) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on 5LOYMART 2 161.00 (344041) 161 kV Bus a. Apply Fault at the 5LOYMART 2 161.00 (344041) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LOYMART 2 (344041) 161.0 kV to 5LOYMART 1 (344040) 161.0 kV Transmission Circuit #z b.2. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply Fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to WOODRNG4 (514714) 138.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply Fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MDFRDTP4 (515569) 138.0 kV to RENFROW4 (515544) 138.0 kV Transmission Circuit #1 b.2. MDFRDTP4 (515569) 138.0 kV to RDRUNNR4 (515426) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138.0 kV to KNOBHIL4 (514795) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on RICE 6 230.00 (530686) 230 kV Bus a. Apply Fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 3 (530623) 115.0 kV to LYONS 3 (530620) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_363 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply Fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 b.2. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER3 (533417) 115.0 kV to EMCPHER6 (532872) 230.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 b.2. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on REFINRY3 115.00 (533427) 115 kV Bus a. Apply Fault at the REFINRY3 115.00 (533427) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REFINRY3 (533427) 115.0 kV to EMCPHER3 (533417) 115.0 kV Transmission Circuit #1 b.2. REFINRY3 (533427) 115.0 kV to MCPHER 3 (533428) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on CLDWELL4 138.00 (539003) 138 kV Bus a. Apply Fault at the CLDWELL4 138.00 (539003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLDWELL4 (539003) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.2. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply Fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILAN_GOAB (539008) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.2. MILAN_GOAB (539008) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.2. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply Fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply Fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on GRNBURG3 115.00 (539664) 115 kV Bus a. Apply Fault at the GRNBURG3 115.00 (539664) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.2. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on FORD 3 115.00 (539758) 115 kV Bus a. Apply Fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_381 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.2. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_382 | Single Phase Fault with Stuck Breaker on NFTDODG3 115.00 (539771) 115 kV Bus a. Apply Fault at the NFTDODG3 115.00 (539771) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NFTDODG3 (539771) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #2 b.2. NFTDODG3 (539771) 115.0 kV to SPRVL 3 (539759) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_383 | Single Phase Fault with Stuck Breaker on CRKCK 3 115.00 (539783) 115 kV Bus a. Apply Fault at the CRKCK 3 115.00 (539783) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRKCK 3 (539783) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.2. CRKCK 3 (539783) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_384 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_385 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_386 | Single Phase Fault with Stuck Breaker on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply Fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. IRONWOOD7 (539803) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_387 | Single Phase Fault with Stuck Breaker on GEN-2011-008345.00 (539840) 345 kV Bus a. Apply Fault at the GEN-2011-008345.00 (539840) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2011-008 (539840) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. GEN-2011-008 (539840) 345.0 kV to G-2011-008-3 (539857) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_388 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_389 | Single Phase Fault with Stuck Breaker on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply Fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_390 | Single Phase Fault with Stuck Breaker on PRALEE 5 161.00 (541206) 161 kV Bus a. Apply Fault at the PRALEE 5 161.00 (541206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_391 | Single Phase Fault with Stuck Breaker on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply Fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 b.2. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_392 | Single Phase Fault with Stuck Breaker on RAYTOWN5 161.00 (541219) 161 kV Bus a. Apply Fault at the RAYTOWN5 161.00 (541219) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 b.2. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_393 | Single Phase Fault with Stuck Breaker on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply Fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to WSTELEC_CAP5 (541149) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_394 | Single Phase Fault with Stuck Breaker on GRAINVL5 161.00 (541226) 161 kV Bus a. Apply Fault at the GRAINVL5 161.00 (541226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAINVL5 (541226) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 b.2. GRAINVL5 (541226) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_395 | Single Phase Fault with Stuck Breaker on OAKGRV 5 161.00 (541227) 161 kV Bus a. Apply Fault at the OAKGRV 5 161.00 (541227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKGRV 5 (541227) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 b.2. OAKGRV 5 (541227) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_396 | Single Phase Fault with Stuck Breaker on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply Fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WBURGE 5 (541228) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WBURGE_CAP5 (541148) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_397 | Single Phase Fault with Stuck Breaker on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply Fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ODESSA 5 (541229) 161.0 kV to WBURGE 5 (541228) 161.0 kV Transmission Circuit #1 b.2. ODESSA 5 (541229) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_398 | Single Phase Fault with Stuck Breaker on RICHMND5 161.00 (541236) 161 kV Bus a. Apply Fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to LEX161 5 (541232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_399 | Single Phase Fault with Stuck Breaker on BLSPW 5 161.00 (541237) 161 kV Bus a. Apply Fault at the BLSPW 5 161.00 (541237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPW 5 (541237) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_400 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDEAST5 (541241) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. SEDEAST5 (541241) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_401 | Single Phase Fault with Stuck Breaker on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply Fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY2 (541262) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 b.2. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_402 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 b.2. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_403 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.2. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_404 | Single Phase Fault with Stuck Breaker on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply Fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELHYS 2 (541273) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 b.2. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_405 | Single Phase Fault with Stuck Breaker on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply Fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDS 2 (541272) 69.0 kV Transmission Circuit #1 b.2. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_406 | Single Phase Fault with Stuck Breaker on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply Fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDPLT 2 (541275) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 b.2. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_407 | Single Phase Fault with Stuck Breaker on COLECMP2 69.000 (541276) 69 kV Bus a. Apply Fault at the COLECMP2 69.000 (541276) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLECMP2 (541276) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 b.2. COLECMP2 (541276) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_408 | Single Phase Fault with Stuck Breaker on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply Fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 b.2. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_409 | Single Phase Fault with Stuck Breaker on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply Fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WAFBW_SW5 (541335) 161.0 kV to WBURGE 5 (541228) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_410 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAFBE_SW5 (541337) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. WAFBE_SW5 (541337) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_411 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_412 | Single Phase Fault with Stuck Breaker on MONSERTP 69.000 (541524) 69 kV Bus a. Apply Fault at the MONSERTP 69.000 (541524) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONSERTP (541524) 69.0 kV to WBURGE 2 (541269) 69.0 kV Transmission Circuit #1 b.2. MONSERTP (541524) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_413 | Single Phase Fault with Stuck Breaker on KNOSTERTP 69.000 (541534) 69 kV Bus a. Apply Fault at the KNOSTERTP 69.000 (541534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOSTERTP (541534) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 b.2. KNOSTERTP (541534) 69.0 kV to MONSERTP (541524) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_414 | Single Phase Fault with Stuck Breaker on LAMONTETP 69.000 (541535) 69 kV Bus a. Apply Fault at the LAMONTETP 69.000 (541535) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMONTETP (541535) 69.0 kV to SEDN 2 (541271) 69.0 kV Transmission Circuit #1 b.2. LAMONTETP (541535) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_415 | Single Phase Fault with Stuck Breaker on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply Fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. LAKCTYJ2 (543087) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_416 | Single Phase Fault with Stuck Breaker on BLUSPRG2 69.000 (543088) 69 kV Bus a. Apply Fault at the BLUSPRG2 69.000 (543088) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUSPRG2 (543088) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 b.2. BLUSPRG2 (543088) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_417 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCNRD2 (543091) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 b.2. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_418 | Single Phase Fault with Stuck Breaker on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply Fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CUPTAP 2 (547436) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 b.2. CUPTAP 2 (547436) 69.0 kV to GRN614 2 (547613) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_419 | Single Phase Fault with Stuck Breaker on PRC460 2 69.000 (547449) 69 kV Bus a. Apply Fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 b.2. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_420 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_421 | Single Phase Fault with Stuck Breaker on ASH121 2 69.000 (547536) 69 kV Bus a. Apply Fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASH121 2 (547536) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 b.2. ASH121 2 (547536) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_422 | Single Phase Fault with Stuck Breaker on AUR124 2 69.000 (547537) 69 kV Bus a. Apply Fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 b.2. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_423 | Single Phase Fault with Stuck Breaker on MON152 2 69.000 (547540) 69 kV Bus a. Apply Fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON152 2 (547540) 69.0 kV to AUR124 2 (547537) 69.0 kV Transmission Circuit #1 b.2. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_424 | Single Phase Fault with Stuck Breaker on FRP217 2 69.000 (547545) 69 kV Bus a. Apply Fault at the FRP217 2 69.000 (547545) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRP217 2 (547545) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 b.2. FRP217 2 (547545) 69.0 kV to BOL602 2 (547612) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_425 | Single Phase Fault with Stuck Breaker on BIL221 2 69.000 (547546) 69 kV Bus a. Apply Fault at the BIL221 2 69.000 (547546) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIL221 2 (547546) 69.0 kV to 2BILLNG (300658) 69.0 kV Transmission Circuit #1 b.2. BIL221 2 (547546) 69.0 kV to 2CLEVER (300665) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_426 | Single Phase Fault with Stuck Breaker on MTV351 2 69.000 (547577) 69 kV Bus a. Apply Fault at the MTV351 2 69.000 (547577) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MTV351 2 (547577) 69.0 kV to MTV420 2 (547606) 69.0 kV Transmission Circuit #1 b.2. MTV351 2 (547577) 69.0 kV to MTV463 2 (547619) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_427 | Single Phase Fault with Stuck Breaker on AUR355 2 69.000 (547578) 69 kV Bus a. Apply Fault at the AUR355 2 69.000 (547578) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR355 2 (547578) 69.0 kV to AUR124 2 (547537) 69.0 kV Transmission Circuit #1 b.2. AUR355 2 (547578) 69.0 kV to MTV420 2 (547606) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_428 | Single Phase Fault with Stuck Breaker on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply Fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STK418 2 (547605) 69.0 kV to 5STKAEC (300118) 161.0 kV to STK418 1 (547719) 12.5 kV Three Winding #1 b.2. STK418 2 (547605) 69.0 kV to STK324J2 (547616) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_429 | Single Phase Fault with Stuck Breaker on G16-046-TAP 345.00 (560080) 345 kV Bus a. Apply Fault at the G16-046-TAP 345.00 (560080) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046-TAP (560080) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. G16-046-TAP (560080) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_430 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_431 | Single Phase Fault with Stuck Breaker on G14-001-TAP 345.00 (562476) 345 kV Bus a. Apply Fault at the G14-001-TAP 345.00 (562476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G14-001-TAP (562476) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. G14-001-TAP (562476) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_432 | Single Phase Fault with Stuck Breaker on GEN-2016-153345.00 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153345.00 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to G16-153XFMR1 (588361) 34.5 kV Two Winding #1 b.2. GEN-2016-153 (588360) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_433 | Single Phase Fault with Stuck Breaker on G16-153-TAP 345.00 (588364) 345 kV Bus a. Apply Fault at the G16-153-TAP 345.00 (588364) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-153-TAP (588364) 345.0 kV to GEN-2017-086 (589240) 345.0 kV Transmission Circuit #1 b.2. G16-153-TAP (588364) 345.0 kV to GEN-2016-153 (588360) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_434 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 b.2. 5MORGANXF2 (301622) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_435 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 b.2. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_436 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 b.2. 2GEORGE (300531) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_437 | Single Phase Fault with Stuck Breaker on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply Fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MORGAN (300782) 69.0 kV to 5MORGAN (300101) 161.0 kV Two Winding #1 b.2. 2MORGAN (300782) 69.0 kV to 2EUDORA (300774) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_438 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 b.2. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_439 | Single Phase Fault with Stuck Breaker on 5REEDSP 161.00 (301521) 161 kV Bus a. Apply Fault at the 5REEDSP 161.00 (301521) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2REEDSP (300725) 69.0 kV to 5REEDSP (301521) 161.0 kV Two Winding #1 b.2. 2REEDSP (300725) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_440 | Single Phase Fault with Stuck Breaker on 5HYDERHL 161.00 (300793) 161 kV Bus a. Apply Fault at the 5HYDERHL 161.00 (300793) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2HYDERHL (300798) 69.0 kV to 5HYDERHL (300793) 161.0 kV Two Winding #1 b.2. 2HYDERHL (300798) 69.0 kV to 2ARNICA (300799) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_441 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NIXA 2 (505501) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 b.2. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_442 | Single Phase Fault with Stuck Breaker on BARBER 4 138.00 (539674) 138 kV Bus a. Apply Fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 3 (539760) 115.0 kV to SAWYER 3 (539649) 115.0 kV Transmission Circuit #1 b.2. BARBER 3 (539760) 115.0 kV to BARBER 4 (539674) 138.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_443 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_444 | Single Phase Fault with Stuck Breaker on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply Fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WBURGE 2 (541269) 69.0 kV to WBURGE 5 (541228) 161.0 kV Two Winding #1 b.2. WBURGE 2 (541269) 69.0 kV to WBURGP 2 (541268) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_445 | Single Phase Fault with Stuck Breaker on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply Fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ODESSA 2 (541267) 69.0 kV to ODESSA 5 (541229) 161.0 kV Two Winding #1 b.2. ODESSA 2 (541267) 69.0 kV to 13&40 2 (541266) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_446 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_447 | Single Phase Fault with Stuck Breaker on GEN-2016-046345.00 (587310) 345 kV Bus a. Apply Fault at the GEN-2016-046345.00 (587310) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-046 (587310) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-046 (587310) 345.0 kV to G16-046XFMR1 (587311) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_448 | Single Phase Fault with Stuck Breaker on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply Fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKTASW4 (520434) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_449 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_450 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARPER 4 (539668) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_451 | Single Phase Fault with Stuck Breaker on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply Fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_452 | Single Phase Fault with Stuck Breaker on RVS438 5 161.00 (547497) 161 kV Bus a. Apply Fault at the RVS438 5 161.00 (547497) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RVS438 5 (547497) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. RVS438 5 (547497) 161.0 kV to BRN413 5 (547489) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_453 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON383 2 (547591) 69.0 kV to MON383 5 (547480) 161.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 b.2. MON383 2 (547591) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_454 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_455 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_456 | Single Phase Fault with Stuck Breaker on 5HYDERHL 161.00 (300793) 161 kV Bus a. Apply Fault at the 5HYDERHL 161.00 (300793) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HYDERHL (300793) 161.0 kV to 2HYDERHL (300798) 69.0 kV Two Winding #1 b.2. 5HYDERHL (300793) 161.0 kV to 5STKAEC (300118) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_457 | Single Phase Fault with Stuck Breaker on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply Fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HOLDENB2 (300124) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5HOLDENB2 (300124) 161.0 kV to 2HOLDEN (300336) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_458 | Single Phase Fault with Stuck Breaker on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply Fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_459 | Single Phase Fault with Stuck Breaker on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply Fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDSR 5 (541217) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to 5SEDALA (300117) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_460 | Single Phase Fault with Stuck Breaker on CLINTON5 161.00 (541242) 161 kV Bus a. Apply Fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTON5 (541242) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #z1 b.2. CLINTON5 (541242) 161.0 kV to CLNTN N2 (541303) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_461 | Single Phase Fault with Stuck Breaker on G17-108-TAP 161.00 (761278) 161 kV Bus a. Apply Fault at the G17-108-TAP 161.00 (761278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-108-TAP (761278) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. G17-108-TAP (761278) 161.0 kV to ARCHIE 5 (541207) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_462 | Single Phase Fault with Stuck Breaker on 5NORTONTP 161.00 (301567) 161 kV Bus a. Apply Fault at the 5NORTONTP 161.00 (301567) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTONTP (301567) 161.0 kV to 5GEORGE (300082) 161.0 kV Transmission Circuit #1 b.2. 5NORTONTP (301567) 161.0 kV to 5NORTON (300105) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_463 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDLIAW_CAP5 (541146) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_464 | Single Phase Fault with Stuck Breaker on 5BTLFD 161.00 (300348) 161 kV Bus a. Apply Fault at the 5BTLFD 161.00 (300348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 b.2. 5BTLFD (300348) 161.0 kV to 5JAMESV (300089) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_465 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. 5MOCITYB1 (301563) 161.0 kV to 5MOCITYB2 (300098) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_466 | Single Phase Fault with Stuck Breaker on 2HUGHSV 69.000 (300533) 69 kV Bus a. Apply Fault at the 2HUGHSV 69.000 (300533) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2HUGHSV (300533) 69.0 kV to 2SWSPJC (300543) 69.0 kV Transmission Circuit #1 b.2. 2HUGHSV (300533) 69.0 kV to 2GEOGT1 (300529) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_467 | Single Phase Fault with Stuck Breaker on 2MTHULD 69.000 (300558) 69 kV Bus a. Apply Fault at the 2MTHULD 69.000 (300558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MTHULD (300558) 69.0 kV to 2LINCLN (300534) 69.0 kV Transmission Circuit #1 b.2. 2MTHULD (300558) 69.0 kV to 2IVYBND (300557) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_468 | Single Phase Fault with Stuck Breaker on 2SYLVAN 69.000 (300545) 69 kV Bus a. Apply Fault at the 2SYLVAN 69.000 (300545) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SYLVAN (300545) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2SYLVAN (300545) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_469 | Single Phase Fault with Stuck Breaker on CPK446 5 161.00 (547499) 161 kV Bus a. Apply Fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CPK446 2 (547618) 69.0 kV to CPK446 5 (547499) 161.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 b.2. CPK446 2 (547618) 69.0 kV to 2BILLNG (300658) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_470 | Single Phase Fault with Stuck Breaker on 2FLTCRK 69.000 (300671) 69 kV Bus a. Apply Fault at the 2FLTCRK 69.000 (300671) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2FLTCRK (300671) 69.0 kV to 2CAPEFR (300662) 69.0 kV Transmission Circuit #1 b.2. 2FLTCRK (300671) 69.0 kV to 2JENKIN (300821) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_471 | Single Phase Fault with Stuck Breaker on 2STONBR 69.000 (300733) 69 kV Bus a. Apply Fault at the 2STONBR 69.000 (300733) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STONBR (300733) 69.0 kV to 2LAKE-K (300722) 69.0 kV Transmission Circuit #1 b.2. 2STONBR (300733) 69.0 kV to 2KMBRLNTP (300721) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_472 | Single Phase Fault with Stuck Breaker on 2T.ROCKSW 69.000 (301360) 69 kV Bus a. Apply Fault at the 2T.ROCKSW 69.000 (301360) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2T.ROCKSW (301360) 69.0 kV to 2SILDOL (300730) 69.0 kV Transmission Circuit #1 b.2. 2T.ROCKSW (301360) 69.0 kV to TABLE R2 (505474) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_473 | Single Phase Fault with Stuck Breaker on 5RENOHLW 161.00 (301129) 161 kV Bus a. Apply Fault at the 5RENOHLW 161.00 (301129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2RENOHLW (300738) 69.0 kV to 5RENOHLW (301129) 161.0 kV Two Winding #1 b.2. 2RENOHLW (300738) 69.0 kV to 2SPOKAN (300732) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_474 | Single Phase Fault with Stuck Breaker on STOCKTN5 161.00 (505498) 161 kV Bus a. Apply Fault at the STOCKTN5 161.00 (505498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STOCKTN5 (505498) 161.0 kV to 5STKAEC (300118) 161.0 kV Transmission Circuit #1 b.2. STOCKTN5 (505498) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_475 | Single Phase Fault with Stuck Breaker on 5MCBAIN T 161.00 (345071) 161 kV Bus a. Apply Fault at the 5MCBAIN T 161.00 (345071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 5MCBAIN T (345071) 161.0 kV to 5MCBAINB2 (301489) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_476 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 161.00 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 161.00 (344234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CALIF UE 2 (344234) 161.0 kV to 5CALIF UE 1 (344233) 161.0 kV Transmission Circuit #z b.2. 5CALIF UE 2 (344234) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_477 | Single Phase Fault with Stuck Breaker on GEN-2017-164345.00 (762321) 345 kV Bus a. Apply Fault at the GEN-2017-164345.00 (762321) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-164 (762321) 345.0 kV to WOODRNG7 (514715) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-164 (762321) 345.0 kV to GEN-2017-178 (762342) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_478 | Single Phase Fault with Stuck Breaker on G07621119-20345.00 (515599) 345 kV Bus a. Apply Fault at the G07621119-20345.00 (515599) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. None to None Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_479 | Single Phase Fault with Stuck Breaker on G16-003-TAP 345.00 (560071) 345 kV Bus a. Apply Fault at the G16-003-TAP 345.00 (560071) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_480 | Single Phase Fault with Stuck Breaker on WWDBORDT 345.00 (755000) 345 kV Bus a. Apply Fault at the WWDBORDT 345.00 (755000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDBORDT (755000) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. WWDBORDT (755000) 345.0 kV to CHISHOLM7 (511553) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_481 | Single Phase Fault with Stuck Breaker on GEN-2019-012345.00 (763527) 345 kV Bus a. Apply Fault at the GEN-2019-012345.00 (763527) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-012 (763527) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. GEN-2019-012 (763527) 345.0 kV to G19-012-XFM1 (763528) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_482 | Single Phase Fault with Stuck Breaker on GEN-2017-203345.00 (760809) 345 kV Bus a. Apply Fault at the GEN-2017-203345.00 (760809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-203 (760809) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-203 (760809) 345.0 kV to G17-203XFMR1 (760810) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_483 | Single Phase Fault with Stuck Breaker on G18-128-TAP 345.00 (763421) 345 kV Bus a. Apply Fault at the G18-128-TAP 345.00 (763421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-128-TAP (763421) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. G18-128-TAP (763421) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_484 | Single Phase Fault with Stuck Breaker on VINEDE_S 115.00 (530722) 115 kV Bus a. Apply Fault at the VINEDE_S 115.00 (530722) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINEDE_S (530722) 115.0 kV to VINE2 3 (530694) 115.0 kV Transmission Circuit #z1 b.2. VINEDE_S (530722) 115.0 kV to HAYS 3 (530562) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_485 | Single Phase Fault with Stuck Breaker on G16-111-TAP 345.00 (587884) 345 kV Bus a. Apply Fault at the G16-111-TAP 345.00 (587884) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-111-TAP (587884) 345.0 kV to RENO 7 (532771) 345.0 kV Transmission Circuit #1 b.2. G16-111-TAP (587884) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_486 | Single Phase Fault with Stuck Breaker on GEN-2017-220345.00 (760284) 345 kV Bus a. Apply Fault at the GEN-2017-220345.00 (760284) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-220 (760284) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-220 (760284) 345.0 kV to G17-220-XFM1 (760285) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_487 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_488 | Single Phase Fault with Stuck Breaker on FR3HV 345.00 (578530) 345 kV Bus a. Apply Fault at the FR3HV 345.00 (578530) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FR3HV (578530) 345.0 kV to FR2WEST7 (532795) 345.0 kV Transmission Circuit #1 b.2. FR3HV (578530) 345.0 kV to FR3LV1 (578531) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_489 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_490 | Single Phase Fault with Stuck Breaker on GILL 4 138.00 (533047) 138 kV Bus a. Apply Fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_491 | Single Phase Fault with Stuck Breaker on GEN-2017-226138.00 (760641) 138 kV Bus a. Apply Fault at the GEN-2017-226138.00 (760641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-226 (760641) 138.0 kV to G17-226XFMR1 (760642) 34.5 kV Two Winding #1 b.2. GEN-2017-226 (760641) 138.0 kV to G17-227XFMR1 (760662) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_492 | Single Phase Fault with Stuck Breaker on MANVILE3 115.00 (533426) 115 kV Bus a. Apply Fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to EMCPHER3 (533417) 115.0 kV Transmission Circuit #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_493 | Single Phase Fault with Stuck Breaker on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply Fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MCPHER 3 (533428) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_494 | Single Phase Fault with Stuck Breaker on BARBER 4 138.00 (539674) 138 kV Bus a. Apply Fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 4 (539674) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_495 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_496 | Single Phase Fault with Stuck Breaker on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply Fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROLLHLS3 (539643) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_497 | Single Phase Fault with Stuck Breaker on 2ND-KS 3 115.00 (539689) 115 kV Bus a. Apply Fault at the 2ND-KS 3 115.00 (539689) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ND-KS 3 (539689) 115.0 kV to 24-FREY3 (539661) 115.0 kV Transmission Circuit #1 b.2. 2ND-KS 3 (539689) 115.0 kV to GBENDTP3 (539666) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_498 | Single Phase Fault with Stuck Breaker on SSTARTP3 115.00 (539763) 115 kV Bus a. Apply Fault at the SSTARTP3 115.00 (539763) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SSTARTP3 (539763) 115.0 kV to GRNBURG3 (539664) 115.0 kV Transmission Circuit #1 b.2. SSTARTP3 (539763) 115.0 kV to FORD 3 (539758) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_499 | Single Phase Fault with Stuck Breaker on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply Fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_500 | Single Phase Fault with Stuck Breaker on GEN-2017-018345.00 (588630) 345 kV Bus a. Apply Fault at the GEN-2017-018345.00 (588630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-018 (588630) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-018 (588630) 345.0 kV to G17-018XFMR1 (588631) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_501 | Single Phase Fault with Stuck Breaker on GEN-2018-049345.00 (762834) 345 kV Bus a. Apply Fault at the GEN-2018-049345.00 (762834) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-049 (762834) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-049 (762834) 345.0 kV to G18-108XFM1 (763285) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_502 | Single Phase Fault with Stuck Breaker on GEN-2008-124345.00 (579480) 345 kV Bus a. Apply Fault at the GEN-2008-124345.00 (579480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2008-124 (579480) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. GEN-2008-124 (579480) 345.0 kV to G08-124XFMR1 (579481) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_503 | Single Phase Fault with Stuck Breaker on G-2011-008-1345.00 (539841) 345 kV Bus a. Apply Fault at the G-2011-008-1345.00 (539841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G-2011-008-1 (539841) 345.0 kV to GEN-2011-008 (539840) 345.0 kV Transmission Circuit #1 b.2. G-2011-008-1 (539841) 345.0 kV to G11-008XFMR2 (539849) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_504 | Single Phase Fault with Stuck Breaker on G-2011-008-2345.00 (539855) 345 kV Bus a. Apply Fault at the G-2011-008-2345.00 (539855) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G-2011-008-2 (539855) 345.0 kV to G11-008XFMR4 (539856) 34.5 kV Two Winding #1 b.2. G-2011-008-2 (539855) 345.0 kV to GEN-2011-008 (539840) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_505 | Single Phase Fault with Stuck Breaker on G-2011-008-3345.00 (539857) 345 kV Bus a. Apply Fault at the G-2011-008-3345.00 (539857) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G-2011-008-3 (539857) 345.0 kV to GEN-2011-008 (539840) 345.0 kV Transmission Circuit #1 b.2. G-2011-008-3 (539857) 345.0 kV to G11-008XFMR5 (539861) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_506 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to SIBLEY 5 (541202) 161.0 kV Transmission Circuit #1 b.2. SIBLEYPL (541250) 161.0 kV to SIBLEY 5 (541202) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_507 | Single Phase Fault with Stuck Breaker on STROTHR5 161.00 (541246) 161 kV Bus a. Apply Fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STROTHR5 (541246) 161.0 kV to PRALEE 5 (541206) 161.0 kV Transmission Circuit #1 b.2. STROTHR5 (541246) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_508 | Single Phase Fault with Stuck Breaker on LBRTYWT5 161.00 (541247) 161 kV Bus a. Apply Fault at the LBRTYWT5 161.00 (541247) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYWT5 (541247) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 b.2. LBRTYWT5 (541247) 161.0 kV to HLLMRK 5 (541215) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_509 | Single Phase Fault with Stuck Breaker on FROSTRD5 161.00 (541220) 161 kV Bus a. Apply Fault at the FROSTRD5 161.00 (541220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FROSTRD5 (541220) 161.0 kV to FROSTRD_CAP5 (541139) 161.0 kV Transmission Circuit #r b.2. FROSTRD5 (541220) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_510 | Single Phase Fault with Stuck Breaker on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply Fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LKWOOD 5 (541238) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 b.2. LKWOOD 5 (541238) 161.0 kV to RAYTOWN5 (541219) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_511 | Single Phase Fault with Stuck Breaker on LEX161 5 161.00 (541232) 161 kV Bus a. Apply Fault at the LEX161 5 161.00 (541232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. LEX161 5 (541232) 161.0 kV to LEX69 2 (541264) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_512 | Single Phase Fault with Stuck Breaker on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply Fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_513 | Single Phase Fault with Stuck Breaker on NUCOR5 161.00 (541395) 161 kV Bus a. Apply Fault at the NUCOR5 161.00 (541395) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUCOR5 (541395) 161.0 kV to NUCOR_D1 (541396) 13.8 kV Two Winding #1 b.2. NUCOR5 (541395) 161.0 kV to NUCOR_S1 (541398) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_514 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_515 | Single Phase Fault with Stuck Breaker on G18-063-TAP 69.000 (762992) 69 kV Bus a. Apply Fault at the G18-063-TAP 69.000 (762992) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-063-TAP (762992) 69.0 kV to KELHYS 2 (541273) 69.0 kV Transmission Circuit #1 b.2. G18-063-TAP (762992) 69.0 kV to SEDN 2 (541271) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_516 | Single Phase Fault with Stuck Breaker on WARSAWTP 69.000 (541281) 69 kV Bus a. Apply Fault at the WARSAWTP 69.000 (541281) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARSAWTP (541281) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 b.2. WARSAWTP (541281) 69.0 kV to WARSAW 2 (541277) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_517 | Single Phase Fault with Stuck Breaker on LAKCTY 2 69.000 (543092) 69 kV Bus a. Apply Fault at the LAKCTY 2 69.000 (543092) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTY 2 (543092) 69.0 kV to LAKCTYJ2 (543087) 69.0 kV Transmission Circuit #1 b.2. LAKCTY 2 (543092) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_518 | Single Phase Fault with Stuck Breaker on LAKCTYK2 69.000 (543093) 69 kV Bus a. Apply Fault at the LAKCTYK2 69.000 (543093) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYK2 (543093) 69.0 kV to DUNCNRD2 (543091) 69.0 kV Transmission Circuit #1 b.2. LAKCTYK2 (543093) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_519 | Single Phase Fault with Stuck Breaker on GEN-2019-04869.000 (763802) 69 kV Bus a. Apply Fault at the GEN-2019-04869.000 (763802) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-048 (763802) 69.0 kV to DUNCNRD2 (543091) 69.0 kV Transmission Circuit #1 b.2. GEN-2019-048 (763802) 69.0 kV to G19-048-XFM1 (763803) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_520 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAD368 2 (547585) 69.0 kV to DAD368 5 (547478) 161.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 b.2. DAD368 2 (547585) 69.0 kV to ASH121 2 (547536) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_521 | Single Phase Fault with Stuck Breaker on GRN614 2 69.000 (547613) 69 kV Bus a. Apply Fault at the GRN614 2 69.000 (547613) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRN614 2 (547613) 69.0 kV to ARC250 2 (547549) 69.0 kV Transmission Circuit #1 b.2. GRN614 2 (547613) 69.0 kV to CUPTAP 2 (547436) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_522 | Single Phase Fault with Stuck Breaker on GEN-2017-060161.00 (588980) 161 kV Bus a. Apply Fault at the GEN-2017-060161.00 (588980) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-060 (588980) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. GEN-2017-060 (588980) 161.0 kV to G17-060XFMR1 (588981) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_523 | Single Phase Fault with Stuck Breaker on LAW260 2 69.000 (547552) 69 kV Bus a. Apply Fault at the LAW260 2 69.000 (547552) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAW260 2 (547552) 69.0 kV to ASH121 2 (547536) 69.0 kV Transmission Circuit #1 b.2. LAW260 2 (547552) 69.0 kV to HTC338 2 (547573) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_524 | Single Phase Fault with Stuck Breaker on WIL482 69.000 (547726) 69 kV Bus a. Apply Fault at the WIL482 69.000 (547726) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WIL482 (547726) 69.0 kV to ASH121 2 (547536) 69.0 kV Transmission Circuit #1 b.2. WIL482 (547726) 69.0 kV to WIL479 (547727) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_525 | Single Phase Fault with Stuck Breaker on MAR437 2 69.000 (547611) 69 kV Bus a. Apply Fault at the MAR437 2 69.000 (547611) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAR437 2 (547611) 69.0 kV to AUR124 2 (547537) 69.0 kV Transmission Circuit #1 b.2. MAR437 2 (547611) 69.0 kV to BIL221 2 (547546) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_526 | Single Phase Fault with Stuck Breaker on BOL602 2 69.000 (547612) 69 kV Bus a. Apply Fault at the BOL602 2 69.000 (547612) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL602 2 (547612) 69.0 kV to FRP217 2 (547545) 69.0 kV Transmission Circuit #1 b.2. BOL602 2 (547612) 69.0 kV to BOL367 2 (547584) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_527 | Single Phase Fault with Stuck Breaker on MTV420 2 69.000 (547606) 69 kV Bus a. Apply Fault at the MTV420 2 69.000 (547606) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MTV420 2 (547606) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 b.2. MTV420 2 (547606) 69.0 kV to MTV351 2 (547577) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_528 | Single Phase Fault with Stuck Breaker on STK324J2 69.000 (547616) 69 kV Bus a. Apply Fault at the STK324J2 69.000 (547616) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STK324J2 (547616) 69.0 kV to STK418 2 (547605) 69.0 kV Transmission Circuit #1 b.2. STK324J2 (547616) 69.0 kV to ARC250 2 (547549) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_529 | Single Phase Fault with Stuck Breaker on GEN-2016-050345.00 (587350) 345 kV Bus a. Apply Fault at the GEN-2016-050345.00 (587350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-050 (587350) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-050 (587350) 345.0 kV to G16-050XFMR1 (587351) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_530 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_531 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583850) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583850) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583850) 345.0 kV to G14-001XFMR1 (583851) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_532 | Single Phase Fault with Stuck Breaker on GEN-2017-086345.00 (589240) 345 kV Bus a. Apply Fault at the GEN-2017-086345.00 (589240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-086 (589240) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-086 (589240) 345.0 kV to G17-086XFMR1 (589241) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_533 | Single Phase Fault with Stuck Breaker on G19-035-TAP 161.00 (763696) 161 kV Bus a. Apply Fault at the G19-035-TAP 161.00 (763696) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-035-TAP (763696) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. G19-035-TAP (763696) 161.0 kV to AUR124 5 (547468) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_534 | Single Phase Fault with Stuck Breaker on 5REEDSP 161.00 (301521) 161 kV Bus a. Apply Fault at the 5REEDSP 161.00 (301521) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to 2REEDSP (300725) 69.0 kV Two Winding #1 b.2. 5REEDSP (301521) 161.0 kV to BRN412 5 (547488) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_535 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NIXA 5 (505496) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.2. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_536 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_537 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_538 | Single Phase Fault with Stuck Breaker on G16-046XFMR1115.00 (587311) 115 kV Bus a. Apply Fault at the G16-046XFMR1115.00 (587311) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046XFMR1 (587311) 115.0 kV to GEN-2016-046 (587310) 345.0 kV Two Winding #1 b.2. G16-046XFMR1 (587311) 115.0 kV to G16-046XFMR3 (587315) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_539 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_540 | Single Phase Fault with Stuck Breaker on SEDPLT 2 69.00 (541275) 69 kV Bus a. Apply Fault at the SEDPLT 2 69.00 (541275) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDPLT 2 (541275) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_541 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_542 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON 2 (345411) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_543 | Single Phase Fault with Stuck Breaker on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_544 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N-GBEND3 (539681) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_545 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_546 | Single Phase Fault with Stuck Breaker on FR2EAST7 345.00 (532792) 345 kV Bus a. Apply Fault at the FR2EAST7 345.00 (532792) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FR2EAST7 (532792) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_547 | Single Phase Fault with Stuck Breaker on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_548 | Single Phase Fault with Stuck Breaker on RENFROW4 138.00 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_549 | Single Phase Fault with Stuck Breaker on EVANS N4 138.00 (533040) 138 kV Bus a. Apply Fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_550 | Single Phase Fault with Stuck Breaker on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply Fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_551 | Single Phase Fault with Stuck Breaker on BROOKLINE 5 161.00 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 161.00 (549969) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 5 (549969) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_552 | Single Phase Fault with Stuck Breaker on RICE 6 230.00 (530686) 230 kV Bus a. Apply Fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_553 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_554 | Single Phase Fault with Stuck Breaker on NFTDODG3 115.00 (539771) 115 kV Bus a. Apply Fault at the NFTDODG3 115.00 (539771) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NFTDODG3 (539771) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_555 | Single Phase Fault with Stuck Breaker on SPEARVL3 115.00 (539694) 115 kV Bus a. Apply Fault at the SPEARVL3 115.00 (539694) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL3 (539694) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_556 | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB 230.00 (539117) 230 kV Bus a. Apply Fault at the SPRVILL-EHVB 230.00 (539117) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_557 | Single Phase Fault with Stuck Breaker on 2REEDSP 69.00 (300725) 69 kV Bus a. Apply Fault at the 2REEDSP 69.00 (300725) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2REEDSP (300725) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_558 | Single Phase Fault with Stuck Breaker on 2LAKE-K 69.00 (300722) 69 kV Bus a. Apply Fault at the 2LAKE-K 69.00 (300722) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LAKE-K (300722) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_559 | Single Phase Fault with Stuck Breaker on BRN412 5 161.00 (547488) 161 kV Bus a. Apply Fault at the BRN412 5 161.00 (547488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRN412 5 (547488) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_560 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_561 | Single Phase Fault with Stuck Breaker on AUR124 2 69.00 (547537) 69 kV Bus a. Apply Fault at the AUR124 2 69.00 (547537) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 2 (547537) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_562 | Single Phase Fault with Stuck Breaker on W-DODGE3 115.00 (539699) 115 kV Bus a. Apply Fault at the W-DODGE3 115.00 (539699) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W-DODGE3 (539699) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_563 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_564 | Single Phase Fault with Stuck Breaker on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply Fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPE 5 (541205) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_565 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_566 | Single Phase Fault with Stuck Breaker on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply Fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_567 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_568 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_569 | Single Phase Fault with Stuck Breaker on JTEC 5161.00 (549954) 161 kV Bus a. Apply Fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 b.2. JTEC GEN#1 1 (549890) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.3. JTEC CTS 1 (549891) 12.5 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.4. JTEC GEN#2 1 (549893) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.5. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.6. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.7. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_570 | Single Phase Fault with Stuck Breaker on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_571 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_572 | Single Phase Fault with Stuck Breaker on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply Fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_573 | Single Phase Fault with Stuck Breaker on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 b.4. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_574 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.4. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_575 | Single Phase Fault with Stuck Breaker on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply Fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_576 | Single Phase Fault with Stuck Breaker on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.3. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_577 | Single Phase Fault with Stuck Breaker on NORTON 5161.00 (549967) 161 kV Bus a. Apply Fault at the NORTON 5161.00 (549967) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 b.2. NORTON 5 (549967) 161.0 kV to NORTON 2 (549928) 69.0 kV to NORTON XF1 1 (549942) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_578 | Single Phase Fault with Stuck Breaker on MC CARTNEY 5161.00 (549968) 161 kV Bus a. Apply Fault at the MC CARTNEY 5161.00 (549968) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCCARTNEY (301568) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #z1 b.2. MAC GT1&2 1 (549892) 13.8 kV to MC CARTNEY 5 (549968) 161.0 kV Two Winding #1 b.3. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.4. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_579 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.5. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.6. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_580 | Single Phase Fault with Stuck Breaker on PIC WEST 5161.00 (549971) 161 kV Bus a. Apply Fault at the PIC WEST 5161.00 (549971) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_581 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.4. SPF X3 1 (505495) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_582 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 b.2. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.5. SPF X1 1 (505491) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_583 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ASHGRV (300657) 69.0 kV to 2CAVESP (300664) 69.0 kV Transmission Circuit #1 b.2. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 b.3. 2ASHGRV (300657) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 b.4. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 b.5. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 b.6. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #2 b.7. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_584 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.5. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.6. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.7. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_585 | Single Phase Fault with Stuck Breaker on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply Fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #2 b.2. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_586 | Single Phase Fault with Stuck Breaker on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply Fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 2 (547528) 69.0 kV to BOL 73 5 (547464) 161.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 b.2. BOL 73 2 (547528) 69.0 kV to EXP450T2 (547440) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_587 | Single Phase Fault with Stuck Breaker on ASH121 2 69.000 (547536) 69 kV Bus a. Apply Fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASH121 2 (547536) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 b.2. ASH121 2 (547536) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_588 | Single Phase Fault with Stuck Breaker on NIC170 2 69.000 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NIC170 2 (547542) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 b.2. NIC170 2 (547542) 69.0 kV to SED 80 2 (547529) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_589 | Single Phase Fault with Stuck Breaker on GOLDEN 269.000 (549911) 69 kV Bus a. Apply Fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 b.2. GOLDEN 2 (549911) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_590 | Single Phase Fault with Stuck Breaker on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAIN STREET2 (549921) 69.0 kV to MAIN STREET5 (549958) 161.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 b.2. MAIN STREET2 (549921) 69.0 kV to MAIN STREET5 (549958) 161.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_591 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.2. NICHOLS 2 (549925) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_592 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.2. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_593 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_594 | Single Phase Fault with Stuck Breaker on BUF342 2 69.000 (547575) 69 kV Bus a. Apply Fault at the BUF342 2 69.000 (547575) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUF342 2 (547575) 69.0 kV to BOL 73 2 (547528) 69.0 kV Transmission Circuit #1 b.2. BUF342 2 (547575) 69.0 kV to BUF243J2 (547432) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_595 | Single Phase Fault with Stuck Breaker on FRG397 2 69.000 (547596) 69 kV Bus a. Apply Fault at the FRG397 2 69.000 (547596) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRG397 2 (547596) 69.0 kV to SED 80 2 (547529) 69.0 kV Transmission Circuit #1 b.2. FRG397 2 (547596) 69.0 kV to BUF243J2 (547432) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_596 | Single Phase Fault with Stuck Breaker on BRT323 2 69.000 (547567) 69 kV Bus a. Apply Fault at the BRT323 2 69.000 (547567) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRT323 2 (547567) 69.0 kV to EXP450T2 (547440) 69.0 kV Transmission Circuit #1 b.2. BRT323 2 (547567) 69.0 kV to SED 80 2 (547529) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_597 | Single Phase Fault with Stuck Breaker on WIL479 69.000 (547727) 69 kV Bus a. Apply Fault at the WIL479 69.000 (547727) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WIL479 (547727) 69.0 kV to WIL482 (547726) 69.0 kV Transmission Circuit #1 b.2. WIL479 (547727) 69.0 kV to SED 80 2 (547529) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_598 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAD368 2 (547585) 69.0 kV to DAD368 5 (547478) 161.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 b.2. DAD368 2 (547585) 69.0 kV to CUPTAP 2 (547436) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_599 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_600 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 5 (549969) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.2. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_601 | Single Phase Fault with Stuck Breaker on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NIC170 2 (547542) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_602 | Single Phase Fault with Stuck Breaker on SED 80 2 (547529) 69 kV Bus a. Apply Fault at the SED 80 2 (547529) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SED 80 2 (547529) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_603 | Single Phase Fault with Stuck Breaker on FRG397 2 (547596) 69 kV Bus a. Apply Fault at the FRG397 2 (547596) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRG397 2 (547596) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_604 | Single Phase Fault with Stuck Breaker on ASH121 2 (547536) 69 kV Bus a. Apply Fault at the ASH121 2 (547536) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASH121 2 (547536) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_605 | Single Phase Fault with Stuck Breaker on BOL 73 2 (547528) 69 kV Bus a. Apply Fault at the BOL 73 2 (547528) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 2 (547528) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_606 | Single Phase Fault with Stuck Breaker on MILL 2 (549918) 69 kV Bus a. Apply Fault at the MILL 2 (549918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILL 2 (549918) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_607 | Single Phase Fault with Stuck Breaker on NICHOLS 2 (549925) 69 kV Bus a. Apply Fault at the NICHOLS 2 (549925) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 2 (549925) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_608 | Single Phase Fault with Stuck Breaker on BHJ415 2 (547604) 69 kV Bus a. Apply Fault at the BHJ415 2 (547604) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BHJ415 2 (547604) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 b.2. 5MORGANXF2 (301622) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on GEN-2018-032345.00 (762680) 345 kV Bus a. Apply Fault at the GEN-2018-032345.00 (762680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-032 (762680) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-032 (762680) 345.0 kV to G18-032XFM1 (762681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on G15-052T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15-052T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-052T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. G15-052T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on G16-153-TAP 345.00 (588364) 345 kV Bus a. Apply Fault at the G16-153-TAP 345.00 (588364) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-153-TAP (588364) 345.0 kV to GEN-2017-086 (589240) 345.0 kV Transmission Circuit #1 b.2. G16-153-TAP (588364) 345.0 kV to GEN-2016-153 (588360) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on G18-128-TAP 345.00 (763421) 345 kV Bus a. Apply Fault at the G18-128-TAP 345.00 (763421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-128-TAP (763421) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. G18-128-TAP (763421) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on GEN-2017-018345.00 (588630) 345 kV Bus a. Apply Fault at the GEN-2017-018345.00 (588630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-018 (588630) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-018 (588630) 345.0 kV to G17-018XFMR1 (588631) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GEN-2018-049345.00 (762834) 345 kV Bus a. Apply Fault at the GEN-2018-049345.00 (762834) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-049 (762834) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-049 (762834) 345.0 kV to G18-108XFM1 (763285) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_SUNC_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EMDE_FAULT_001 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.3. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. JOP389 5 (547483) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.7. TIP292 5 (547472) 161.0 kV to Load #1 b.8. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EMDE_FAULT_002 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 b.3. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.4. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.6. TIP292 5 (547472) 161.0 kV to Load #1 b.7. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EMDE_FAULT_003 | Single Phase Fault with Stuck Breaker on L1G382 1 13.200 (547651) 161 kV Bus a. Apply Fault at the L1G382 1 13.200 (547651) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. LAR382 5 (547479) 161.0 kV to L1G382 1 (547651) 13.2 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.4. L1G382 1 (547651) 13.2 kV to Generator #1 b.5. L1G382 1 (547651) 13.2 kV to Load #S1 b.6. L1G382 1 (547651) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_SWPA_FAULT_001 | Single Phase Fault with Stuck Breaker on Table Rock (505472) 161 kV Bus a. Apply Fault at the Table Rock (505472) 161 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. NIXA 5 (505496) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. TABLE R5 (505472) 161.0 kV to remove bus # b.3. TBR1&2 1 (505476) 13.8 kV to Generator #1 b.4. TBR1&2 1 (505476) 13.8 kV to Generator #2 b.5. TBR3&4 1 (505478) 13.8 kV to Generator #3 b.6. TBR3&4 1 (505478) 13.8 kV to Generator #4 b.7. TBR X1 1 (505473) 13.8 kV to remove bus # b.8. TBR X2 1 (505475) 13.8 kV to remove bus # b.9. TBR1&2 1 (505476) 13.8 kV to remove bus # b.10. TBR3&4 1 (505478) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_SWPA_FAULT_002 | Single Phase Fault with Stuck Breaker on Table Rock (505472) 161 kV Bus a. Apply Fault at the Table Rock (505472) 161 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. RVS438 5 (547497) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. TABLE R5 (505472) 161.0 kV to remove bus # b.3. TBR1&2 1 (505476) 13.8 kV to Generator #1 b.4. TBR1&2 1 (505476) 13.8 kV to Generator #2 b.5. TBR3&4 1 (505478) 13.8 kV to Generator #3 b.6. TBR3&4 1 (505478) 13.8 kV to Generator #4 b.7. TBR X1 1 (505473) 13.8 kV to remove bus # b.8. TBR X2 1 (505475) 13.8 kV to remove bus # b.9. TBR1&2 1 (505476) 13.8 kV to remove bus # b.10. TBR3&4 1 (505478) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_GRDA_FAULT_001 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_WFEC_FAULT_001 | Single Phase Fault with Stuck Breaker on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.3. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.4. CHRKCTY4 (520431) 138.0 kV to Load #1 b.5. SALTPLN4 (520437) 138.0 kV to Load #1 b.6. SALTPLN4 (520437) 138.0 kV to Load #2 b.7. CHRKCTY4 (520431) 138.0 kV to remove bus # b.8. SALTPLN4 (520437) 138.0 kV to remove bus # b.9. ROSEVLY4 (520436) 138.0 kV to Load #1 b.10. AVARD 4 (520601) 138.0 kV to Load #1 b.11. ROSEVLY4 (520436) 138.0 kV to remove bus # b.12. AVARD 4 (520601) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_WFEC_FAULT_002 | Single Phase Fault with Stuck Breaker on WAKTASW4 (520434) 138 kV Bus a. Apply Fault at the WAKTASW4 (520434) 138 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WAKTASW4 (520434) 138.0 kV to remove bus # b.3. WFEC_RNFRO4 (520409) 138.0 kV to Load #1 b.4. WFEC_RNFRO4 (520409) 138.0 kV to Load #1A b.5. WFEC_RNFRO4 (520409) 138.0 kV to remove bus # b.6. WAKITA_13.8 (520435) 13.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_WFEC_FAULT_003 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 b.4. SEILING4 (520553) 138.0 kV to Load #1 b.5. SEILING4 (520553) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_WFEC_FAULT_004 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear Fault after 6 cycles and trip the following elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. ROSEVLY4 (520436) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 b.4. SEILING4 (520553) 138.0 kV to Load #1 b.5. SEILING4 (520553) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_SPS_FAULT_001 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DUNES23 (523061) 0.7 kV to Generator #1 b.12. BUFF_DUNES13 (523062) 0.7 kV to Generator #1 b.13. BUFF_DUNES23 (523061) 0.7 kV to remove bus # b.14. BUFF_DUNES13 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNES22 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNES12 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_SPRM_FAULT_001 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161 (549959) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 b.2. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 b.3. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_001 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_002 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_003 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_004 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_005 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_006 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_007 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_008 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_009 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_001 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. COLBY 3 (530555) 115.0 kV to remove bus #1 b.6. CLBYT1 1 (530645) 13.8 kV to remove bus #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_002 | Single Phase Fault with Stuck Breaker on BEACH 3 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 (530557) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HOXIE 3 (530556) 115.0 kV Transmission Circuit #1 b.5. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.6. BEACH 3 (530557) 115.0 kV to remove bus #1 b.7. HILLCTY3 (531387) 34.5 kV to Generator #1 b.8. HILLCTY3 (531387) 34.5 kV to Generator #2 b.9. HILLCTY3 (531387) 34.5 kV to Generator #3 b.10. HILLCTY3 (531387) 34.5 kV to Generator #4 b.11. HILLCTY3 (531387) 34.5 kV to Generator #5 b.12. HILLCTY3 (531387) 34.5 kV to Generator #6 b.13. HILLCTY3 (531387) 34.5 kV to remove bus # b.14. REDLIN 3 (530605) 115.0 kV to remove bus # b.15. HOXIE 3 (530556) 115.0 kV to remove bus # b.16. REDLIN 3 (530605) 115.0 kV to Load #71 b.17. HOXIE 3 (530556) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_003 | Single Phase Fault with Stuck Breaker on ATWOOD 3 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 (530554) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to remove bus #1 b.5. ATWOOD 3 (530554) 115.0 kV to Generator #1 b.6. HILLCTY3 (531387) 34.5 kV to Generator #1 b.7. HILLCTY3 (531387) 34.5 kV to Generator #2 b.8. HILLCTY3 (531387) 34.5 kV to Generator #3 b.9. HILLCTY3 (531387) 34.5 kV to Generator #4 b.10. HILLCTY3 (531387) 34.5 kV to Generator #5 b.11. HILLCTY3 (531387) 34.5 kV to Generator #6 b.12. ATWOOD 3 (530554) 115.0 kV to Load #1 b.13. ATWOOD 3 (530554) 115.0 kV to Load #41 b.14. ATWOOD 3 (530554) 115.0 kV to remove bus # b.15. HILLCTY3 (531387) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_004 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_005 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.4. CLBYT1 1 (530645) 13.8 kV to remove bus #1 b.5. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Load #99 b.12. COLBY 3 (530555) 115.0 kV to Generator #C8 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_006 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. CLBYT1 1 (530645) 13.8 kV to remove bus #1 b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Generator #C8 b.12. COLBY 3 (530555) 115.0 kV to Load #99 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_007 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_008 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Transmission Circuit #1 b.4. REDLIN 3 (530605) 115.0 kV to Load #71 b.5. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_009 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 25 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. REDLIN 3 (530605) 115.0 kV to Load #71 b.5. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_010 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. GMECG1 1 (530674) 13.8 kV to remove bus # b.4. GMECG2 1 (530675) 13.8 kV to remove bus # b.5. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_011 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. GMECG1 1 (530674) 13.8 kV to remove bus #1 b.2. GMECG2 1 (530675) 13.8 kV to remove bus #1 b.3. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.5. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.6. N HAYS3 (530581) 115.0 kV to remove bus #1 b.7. VINETAP3 (530693) 115.0 kV to remove bus #1 b.8. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_012 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to remove bus #1 b.4. VINETAP3 (530693) 115.0 kV to remove bus #1 b.5. GMECG1 1 (530674) 13.8 kV to remove bus #1 b.6. GMECG2 1 (530675) 13.8 kV to remove bus #1 b.7. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_013 | Single Phase Fault with Stuck Breaker on S HAYS 3 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 (530553) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. ANGUS 3 (530714) 115.0 kV to GORHAM 3 (530552) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.5. ANGUS 3 (530714) 115.0 kV to Load #1 b.6. PFEIFER 3 (530725) 115.0 kV to Load #1 b.7. ANGUS 3 (530714) 115.0 kV to remove bus # b.8. PFEIFER 3 (530725) 115.0 kV to remove bus # b.9. GORHAM 3 (530552) 115.0 kV to Load #1 b.10. RUSLPMP3 (530684) 115.0 kV to Load #1 b.11. GORHAM 3 (530552) 115.0 kV to remove bus # b.12. RUSLPMP3 (530684) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_014 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_015 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_016 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_017 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_018 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_019 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_020 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_021 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_022 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_023 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_024 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_025 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_026 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. SMOKYHL6 (530592) 230.0 kV to SMKYP2 6 (530599) 230.0 kV Transmission Circuit #1 b.4. SHG2 34 1 (530715) 34.5 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus #1 b.6. SMKYP2 6 (530599) 230.0 kV to remove bus # b.7. SHP234 1 (530604) 34.5 kV to remove bus # b.8. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_027 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to remove bus #1 b.4. SMKYP1G1 (530594) 0.7 kV to remove bus #1 b.5. SMKYP2G1 (530600) 0.6 kV to remove bus #1 b.6. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_028 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.3. SMKYT2 1 (530634) 13.9 kV to Generator #1 b.4. SMKYT2 1 (530634) 13.9 kV to remove bus # b.5. SMKYP1G1 (530594) 0.7 kV to remove bus #1 b.6. SMKYP1 6 (530593) 230.0 kV to remove bus # b.7. SHP134 1 (530595) 34.5 kV to remove bus # b.8. SMKYT1 1 (530633) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_029 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 5.6 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus #1 b.3. SMKYP1 6 (530593) 230.0 kV to remove bus #1 b.4. SMKYP1G1 (530594) 0.7 kV to remove bus #1 b.5. SMKYP2G1 (530600) 0.6 kV to remove bus #1 b.6. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_030 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_031 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_032 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_033 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_034 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.2. LACROS 3 (530603) 115.0 kV to remove bus #1 b.3. NEKOMA 3 (530608) 115.0 kV to remove bus #1 b.4. ALXNDR 3 (530606) 115.0 kV to remove bus #1 b.5. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.6. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.7. HZRNGPL3 (530609) 115.0 kV to remove bus # b.8. ALEXNDR1 (539702) 34.5 kV to Load #1 b.9. LAXTAP 3 (530602) 115.0 kV to remove bus # b.10. NKMA2 1 (530630) 12.5 kV to remove bus # b.11. ALEXNDR1 (539702) 34.5 kV to remove bus # b.12. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_035 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_036 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LACROS 3 (530603) 115.0 kV to remove bus #1 b.4. NEKOMA 3 (530608) 115.0 kV to remove bus #1 b.5. ALXNDR 3 (530606) 115.0 kV to remove bus #1 b.7. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.8. ALEXNDR1 (539702) 34.5 kV to Load #1 b.9. LAXTAP 3 (530602) 115.0 kV to remove bus # b.10. NKMA2 1 (530630) 12.5 kV to remove bus # b.11. ALEXNDR1 (539702) 34.5 kV to remove bus # b.12. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_037 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to HEIZER 3 (530601) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_038 | Single Phase Fault with Stuck Breaker on RICE 3 (530623) 115 kV Bus a. Apply Fault at the RICE 3 (530623) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. BUSHTON3 (530681) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_039 | Single Phase Fault with Stuck Breaker on RICE 3 (530623) 115 kV Bus a. Apply Fault at the RICE 3 (530623) 115 kV Bus b. Clear Fault after 19 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 3 (530623) 115.0 kV to Load #1 b.3. RICE 3 (530623) 115.0 kV to Load #K1 b.4. RICE 3 (530623) 115.0 kV to Load #K2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_040 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 6 (530686) 230.0 kV to remove bus #1 b.3. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. PRWINDG1 (530690) 0.7 kV to Generator #1 b.6. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.7. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.8. PRWINDG1 (530690) 0.7 kV to remove bus # b.9. BUFCRKT11 (530691) 12.5 kV to remove bus # b.10. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_041 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_042 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_001 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_002 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_003 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_004 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #1 b.4. EMPEC121 (532740) 13.8 kV to Generator #2 b.5. EMPEC121 (532740) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_005 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.2. EMPEC121 (532740) 13.8 kV to Generator #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #2 b.4. EMPEC121 (532740) 13.8 kV to remove bus # b.5. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_006 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_007 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.2. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.3. EMPEC7 1 (532744) 18.0 kV to remove bus # b.4. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_008 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_009 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_010 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_011 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_012 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_013 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_014 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_015 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_016 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_017 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. IAT G1 1 (542957) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_018 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_019 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_020 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_021 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_022 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_023 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_024 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_025 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_026 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_027 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_028 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_029 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_030 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_031 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_032 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_033 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IAT G1 1 (542957) 24.0 kV to remove bus # b.2. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_034 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_035 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 35.25 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. HAWTHN5 (543665) 161.0 kV to LEVEE 5 (542976) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to remove bus # b.4. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_036 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 35.25 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. HAWTHN5 (543665) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.3. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.4. HAWTHN5 (543665) 161.0 kV to LEVEE 5 (542976) 161.0 kV Transmission Circuit #1 b.5. HAW G5 1 (542951) 22.0 kV to remove bus # b.6. RANDLPH5 (543027) 161.0 kV to Load #1 b.7. RANDLPH5 (543027) 161.0 kV to Load #4 b.8. RANDLPH5 (543027) 161.0 kV to remove bus # b.9. HAWTHN5 (543665) 161.0 kV to LEVEE 5 (542976) 161.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP3_P1_LOCAL_FAULT_237 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP3_P1_LOCAL_FAULT_239 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP3_P1_LOCAL_FAULT_272 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP3_P1_LOCAL_FAULT_273 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP3_P1_LOCAL_FAULT_474 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP3_P1_LOCAL_FAULT_476 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25S | Base | GROUP3_P1_REGIONAL_FAULT_023 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_237 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_239 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_272 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_273 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_474 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_476 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2018-002 / DISIS-2019-001 | 25W | Base | GROUP3_P1_REGIONAL_FAULT_023 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscilations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_001 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_002 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_003 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_004 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_005 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_006 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_007 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_008 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_009 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_010 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_011 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_012 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_013 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_014 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_015 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_016 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_017 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_018 | 3 Phase fault on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_019 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_020 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_021 | 3 Phase fault on PLNTYWD7 115.00 (661077) 115 kV Bus a. Apply fault at the PLNTYWD7 115.00 (661077) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLNTYWD7 (661077) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_022 | 3 Phase fault on LEMARST5 161.00 (635260) 161 kV Bus a. Apply fault at the LEMARST5 161.00 (635260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_023 | 3 Phase fault on LTL SIOUX 5 161.00 (635360) 161 kV Bus a. Apply fault at the LTL SIOUX 5 161.00 (635360) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.2. CLIPPER5 (635350) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.3. LTL SIOUX 5 (635360) 161.0 kV to LTL SIOUX 8 (635361) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_025 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_026 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_027 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_028 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_029 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_030 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_031 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_032 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_033 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_034 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON1AG (608891), BISON 4G (608894), BISON5BG (608895), BISON1BG (608897) and BISON5AG (608898). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_035 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_036 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_037 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_038 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_039 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_040 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_041 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_042 | 3 Phase fault on LKFLDXL3 345.00 (601029) 345 kV Bus a. Apply fault at the LKFLDXL3 345.00 (601029) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LKFLDXL3 (601029) 345.0 kV to CRANDAL 3 (601074) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_043 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_044 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_045 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_046 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to ROCK CO5 (602039) 161.0 kV Transmission Circuit #1 b.2. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_047 | 3 Phase fault on CAYLER5 161.00 (631183) 161 kV Bus a. Apply fault at the CAYLER5 161.00 (631183) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_050 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_051 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_052 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_053 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_054 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_055 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_056 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_057 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_058 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_059 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_060 | 3 Phase fault on BVISTA 5 161.00 (635280) 161 kV Bus a. Apply fault at the BVISTA 5 161.00 (635280) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_063 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_064 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_065 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_066 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_067 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on DENISON5 161.00 (652561) 161 kV Bus a. Apply fault at the DENISON5 161.00 (652561) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_069 | 3 Phase fault on OSGOOD5 161.00 (656527) 161 kV Bus a. Apply fault at the OSGOOD5 161.00 (656527) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_070 | 3 Phase fault on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_071 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_072 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_073 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_074 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_075 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_076 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_077 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_078 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_079 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_080 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_081 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_082 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_083 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_084 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_085 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_086 | 3 Phase fault on DENISONWEST869.000 (658030) 69 kV Bus a. Apply fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_087 | 3 Phase fault on TERRY TAP 115.00 (652394) 115 kV Bus a. Apply fault at the TERRY TAP 115.00 (652394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY TAP (652394) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_088 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_089 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_090 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_091 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_092 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. ARMOUR 7 (652501) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_093 | 3 Phase fault on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_094 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_095 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_096 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_097 | 3 Phase fault on E.SIDNEY-LY7115.00 (659186) 115 kV Bus a. Apply fault at the E.SIDNEY-LY7115.00 (659186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.3. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_098 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_099 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_101 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_102 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_103 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_104 | 3 Phase fault on HAZLTON L2 5161.00 (631051) 161 kV Bus a. Apply fault at the HAZLTON L2 5161.00 (631051) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.4. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.5. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.6. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.7. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.8. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.9. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.10. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.11. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_105 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_106 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_107 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_108 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_109 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_110 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_111 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_112 | 3 Phase fault on NEWSALEM-MG7115.00 (655748) 115 kV Bus a. Apply fault at the NEWSALEM-MG7115.00 (655748) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_113 | 3 Phase fault on WOONSKT7 115.00 (652528) 115 kV Bus a. Apply fault at the WOONSKT7 115.00 (652528) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.3. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.4. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_114 | 3 Phase fault on ABERDN JCT 7115.00 (660000) 115 kV Bus a. Apply fault at the ABERDN JCT 7115.00 (660000) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_115 | 3 Phase fault on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_116 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_117 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_118 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_119 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_120 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_121 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_122 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_123 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_124 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_125 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_126 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_127 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_129 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_130 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_131 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from PS_RCP.B-BEG (659432 and 659431). Disabling the dynamic controller model allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_132 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_133 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_134 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_135 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_136 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_137 | 3 Phase fault on N.WILSTN-MW7115.00 (655936) 115 kV Bus a. Apply fault at the N.WILSTN-MW7115.00 (655936) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_138 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to SE.WLSTN-MW7 (655938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_139 | 3 Phase fault on ALKABO -SH7115.00 (655776) 115 kV Bus a. Apply fault at the ALKABO -SH7115.00 (655776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_140 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_141 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_142 | 3 Phase fault on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_143 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN-LNX3 (652829) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_144 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_145 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_146 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_147 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_148 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_149 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_150 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_151 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_152 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_153 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_154 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_155 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_156 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_157 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_158 | 3 Phase fault on J1620 POI 115.00 (46207) 115 kV Bus a. Apply fault at the J1620 POI 115.00 (46207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1620 POI (46207) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_159 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_160 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_161 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_162 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_163 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_164 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_165 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_166 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_167 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_168 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_169 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_170 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to MERRIL 8 (635393) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_171 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to SIOUXCY8 (652574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_172 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_173 | 3 Phase fault on LOGANPK8 69.000 (635245) 69 kV Bus a. Apply fault at the LOGANPK8 69.000 (635245) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGANPK8 (635245) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_174 | 3 Phase fault on EASTSID8 69.000 (635247) 69 kV Bus a. Apply fault at the EASTSID8 69.000 (635247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTSID8 (635247) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_175 | 3 Phase fault on LEMARS S 8 69.000 (635262) 69 kV Bus a. Apply fault at the LEMARS S 8 69.000 (635262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEMARS S 8 (635262) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_176 | 3 Phase fault on MERRIL 8 69.000 (635393) 69 kV Bus a. Apply fault at the MERRIL 8 69.000 (635393) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIL 8 (635393) 69.0 kV to MERRILN8 (635394) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_177 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_178 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_179 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_180 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_181 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_182 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_183 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_184 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_185 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_186 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_187 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_188 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to FERNEY-ER8 (655256) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_189 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON-ER8 (655267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_190 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to NWPS509-ER8 (655395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_191 | 3 Phase fault on GROTON2 869.000 (652253) 69 kV Bus a. Apply fault at the GROTON2 869.000 (652253) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON (660430) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_192 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_193 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_194 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_195 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_196 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_197 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_198 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_199 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_200 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_201 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_202 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_203 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_204 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_205 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_206 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_207 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_208 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_209 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_210 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_211 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_212 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_213 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_214 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_215 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_216 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_217 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_218 | 3 Phase fault on SUMMIT-7 115.00 (652522) 115 kV Bus a. Apply fault at the SUMMIT-7 115.00 (652522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_219 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_220 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_221 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_222 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_223 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_224 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_225 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_226 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_227 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_228 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_229 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_230 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K216LIBE-NI8 (659946) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_231 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_232 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K301HINT-NI8 (659971) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_233 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K135CONC-NI8 (659980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_234 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_235 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_236 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to BEAVRHIL-GW4 (659535) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_237 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_238 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_239 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_240 | 3 Phase fault on MOS-RDFL-ER869.000 (655054) 69 kV Bus a. Apply fault at the MOS-RDFL-ER869.000 (655054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-RDFL-ER8 (655054) 69.0 kV to REDFELD-ER8 (655482) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_241 | 3 Phase fault on MOS-ASHT-ER869.000 (655059) 69 kV Bus a. Apply fault at the MOS-ASHT-ER869.000 (655059) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-ASHT-ER8 (655059) 69.0 kV to REDFELD-ER8 (655482) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_242 | 3 Phase fault on MOS-CLRM-ER869.000 (655082) 69 kV Bus a. Apply fault at the MOS-CLRM-ER869.000 (655082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CLRM-ER8 (655082) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_243 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to SW870-ER8 (655145) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_244 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_245 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_246 | 3 Phase fault on SW833-ER8 69.000 (655137) 69 kV Bus a. Apply fault at the SW833-ER8 69.000 (655137) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW833-ER8 (655137) 69.0 kV to MOS-JEFF-ER8 (655147) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_247 | 3 Phase fault on SW870-ER8 69.000 (655145) 69 kV Bus a. Apply fault at the SW870-ER8 69.000 (655145) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW870-ER8 (655145) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_248 | 3 Phase fault on SW873-ER8 69.000 (655146) 69 kV Bus a. Apply fault at the SW873-ER8 69.000 (655146) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW873-ER8 (655146) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_249 | 3 Phase fault on MOS-JEFF-ER869.000 (655147) 69 kV Bus a. Apply fault at the MOS-JEFF-ER869.000 (655147) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-JEFF-ER8 (655147) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_250 | 3 Phase fault on ABERDEEN-ER869.000 (655262) 69 kV Bus a. Apply fault at the ABERDEEN-ER869.000 (655262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDEEN-ER8 (655262) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_251 | 3 Phase fault on BATH-ER8 69.000 (655269) 69 kV Bus a. Apply fault at the BATH-ER8 69.000 (655269) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATH-ER8 (655269) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_252 | 3 Phase fault on MANSWTCH-MG7115.00 (655749) 115 kV Bus a. Apply fault at the MANSWTCH-MG7115.00 (655749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANSWTCH-MG7 (655749) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_253 | 3 Phase fault on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_254 | 3 Phase fault on ALKABO -SH7115.00 (655776) 115 kV Bus a. Apply fault at the ALKABO -SH7115.00 (655776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALKABO -SH7 (655776) 115.0 kV to FORTUNA -SH7 (655777) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_255 | 3 Phase fault on HELMUT -LY7115.00 (655790) 115 kV Bus a. Apply fault at the HELMUT -LY7115.00 (655790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_256 | 3 Phase fault on MARLEY -LY7115.00 (655793) 115 kV Bus a. Apply fault at the MARLEY -LY7115.00 (655793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLEY -LY7 (655793) 115.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_257 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to GRASSYBT-MK7 (655834) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_258 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_259 | 3 Phase fault on OAKDALE -MK7115.00 (655836) 115 kV Bus a. Apply fault at the OAKDALE -MK7115.00 (655836) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKDALE -MK7 (655836) 115.0 kV to BEARCREK-MK7 (655853) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_260 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_261 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_262 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_263 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_264 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_265 | 3 Phase fault on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTON8 (656247) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_266 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_267 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_268 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_269 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_270 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_271 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_272 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_273 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_274 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_275 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_276 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_277 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_278 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_279 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_280 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_281 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_282 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_283 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_284 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to 32STREET-RR7 (659442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_285 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to PRNGHORN-RR7 (659544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_286 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_287 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_288 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_289 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_290 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_291 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_292 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_293 | 3 Phase fault on K125DUNL-NI869.000 (659853) 69 kV Bus a. Apply fault at the K125DUNL-NI869.000 (659853) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K125DUNL-NI8 (659853) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_294 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_295 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_296 | 3 Phase fault on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K308EARL-NI8 (659856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_297 | 3 Phase fault on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_298 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_299 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_300 | 3 Phase fault on K313HALB-NI869.000 (659863) 69 kV Bus a. Apply fault at the K313HALB-NI869.000 (659863) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K313HALB-NI8 (659863) 69.0 kV to K317MANN-NI8 (659906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_301 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to K326OTTE-NI8 (659886) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_302 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_303 | 3 Phase fault on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_304 | 3 Phase fault on J12_____-NI869.000 (659918) 69 kV Bus a. Apply fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J12_____-NI8 (659918) 69.0 kV to K106CHAR-NI8 (659999) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_305 | 3 Phase fault on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_306 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_307 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_308 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_309 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_310 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_311 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_312 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_313 | 3 Phase fault on FALLON 7 115.00 (652407) 115 kV Bus a. Apply fault at the FALLON 7 115.00 (652407) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FALLON 7 (652407) 115.0 kV to FALLON 8 (652213) 69.0 kV to FALLON 9 (652214) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_314 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_315 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_316 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_317 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_318 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_319 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_320 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_321 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_322 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_323 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_324 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_325 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_326 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_327 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_328 | 3 Phase fault on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_329 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_330 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_331 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_332 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_333 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_334 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_335 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_336 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_337 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_338 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_339 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_340 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_341 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_342 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_343 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_344 | 3 Phase fault on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_345 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_346 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_347 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_348 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_349 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_350 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_351 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_352 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_353 | 3 Phase fault on BEAVRHIL-GW4230.00 (659535) 230 kV Bus a. Apply fault at the BEAVRHIL-GW4230.00 (659535) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVRHIL-GW4 (659535) 230.0 kV to BEAVRHIL-GW7 (659536) 115.0 kV to BEAVRHIL-GW9 (659537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_354 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_355 | 3 Phase fault on BAKER 4 230.00 (661004) 230 kV Bus a. Apply fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_356 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_357 | 3 Phase fault on MI CTYW4 230.00 (652402) 230 kV Bus a. Apply fault at the MI CTYW4 230.00 (652402) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYW4 (652402) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_358 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_359 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_360 | 3 Phase fault on MI CTYE7 115.00 (652412) 115 kV Bus a. Apply fault at the MI CTYE7 115.00 (652412) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE7 (652412) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_361 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_362 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_363 | 3 Phase fault on REDFELD-ER8 69.000 (655482) 69 kV Bus a. Apply fault at the REDFELD-ER8 69.000 (655482) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDFELD-ER8 (655482) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_364 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_365 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_366 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_001 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_002 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_004 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_005 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_007 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_009 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_010 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_017 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_020 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_021 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.3. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_022 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_023 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_024 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_025 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_026 | 3 Phase fault on NUNDRWD-LNX3230.00 (652884) 230 kV Bus a. Apply fault at the NUNDRWD-LNX3230.00 (652884) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_028 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_029 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_030 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_031 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_032 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_033 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_035 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_036 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_037 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_041 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_050 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_051 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_052 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_053 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_057 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_058 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_059 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_060 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply Fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.5. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.6. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LEWIS 7 115.00 (661056) 115 kV Bus a. Apply Fault at the LEWIS 7 115.00 (661056) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.2. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.3. LEWIS 7 (661056) 115.0 kV to LEWIS71G (661055) 13.8 kV Two Winding #1 b.4. LEWIS 7 (661056) 115.0 kV to LEWIS72G (661104) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. BEULAH 7 (661008) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #z b.5. BEULAH 7 (661008) 115.0 kV to COYOTE 7 (661018) 115.0 kV Transmission Circuit #1 b.6. BEULAH 7 (661008) 115.0 kV to COYOTETAP 7 (661057) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply Fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 b.3. GLENDCT7 (661032) 115.0 kV to Load #Y0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply Fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 b.3. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.4. GLENDCT7 (661032) 115.0 kV to GLNDCT1G (661100) 13.8 kV Two Winding #1 b.5. GLENDCT7 (661032) 115.0 kV to GLNDCT2G (661101) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LTLMUDY7 115.00 (661089) 115 kV Bus a. Apply Fault at the LTLMUDY7 115.00 (661089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.3. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.4. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.5. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.6. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.7. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply Fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.4. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.5. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on CRESTON5 161.00 (652560) 161 kV Bus a. Apply Fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.5. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON 9 (652612) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.2. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.3. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.6. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.7. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.5. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.6. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.7. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.8. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.9. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.10. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.2. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.3. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.6. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.7. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.3. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.4. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 b.5. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.4. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.5. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply Fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply Fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on HAZLTON L2 5161.00 (631051) 161 kV Bus a. Apply Fault at the HAZLTON L2 5161.00 (631051) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.4. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.5. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.6. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.7. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.8. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.9. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.10. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.11. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on GU CTR 5 161.00 (631072) 161 kV Bus a. Apply Fault at the GU CTR 5 161.00 (631072) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. HD WIND 5 (628910) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.3. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #1 b.4. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #2 b.5. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.6. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.7. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.8. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.9. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.10. SCRANTN5 (631071) 161.0 kV to SCRANTN9 (629111) 34.5 kV Two Winding #1 b.11. SCRANTN5 (631071) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.12. SCRANTN5 (631071) 161.0 kV to GR JCT 5 (631074) 161.0 kV Transmission Circuit #1 b.13. GU CTR 5 (631072) 161.0 kV to GU CTR 9 (629113) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply Fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. HEBRON 4 (652468) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.3. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to None Three Winding #1 b.4. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DK.KW1A_-BE9 (659197) 13.8 kV Three Winding #1 b.5. DICKINSN-BE4 (659124) 230.0 kV to DICKINS2-BE7 (659195) 115.0 kV to DK.KW1A_-BE9 (659196) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 b.3. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 b.4. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.5. BASIN___-BE7 (659109) 115.0 kV to BASIN___-BE4 (659199) 230.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply Fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.4. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. DAWSONC7 (652404) 115.0 kV to DAWSONC4 (652403) 230.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY9 (652322) 41.6 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.4. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.5. EDGELEY 19 (652328) 13.2 kV to EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.2. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.3. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.4. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.5. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.6. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.9. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on ECKLUND1-PP934.500 (659322) 34.5 kV Bus a. Apply Fault at the ECKLUND1-PP934.500 (659322) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.6. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.7. ECKLUND1-PP9 (659322) 34.5 kV to WILTON_1-PPW (659294) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7 115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7 115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to Load #BB b.6. GARRISN7 (652442) 115.0 kV to Load #BW b.7. GARRISN7 (652442) 115.0 kV to Load #R0 b.8. GARRISN7 (652442) 115.0 kV to Load #W0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.3. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.4. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.6. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.7. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply Fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. ROCKRPDMUNI8 (658122) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.3. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 b.4. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.5. RKRPDTAP-LO8 (659714) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.6. LESTERSS-LO8 (659722) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.7. STEEN -LO8 (659726) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.8. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. EXIRA 5 (652603) 161.0 kV to EXIRA 2G (658001) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.11. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.3. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.4. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.5. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.6. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.7. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.5. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.6. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 b.7. SIOUXF29 (652233) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on SPENCER5 161.00 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.2. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.3. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.4. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.5. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.6. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply Fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.4. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 b.2. GRENORA_-UM7 (659145) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. GRENORA_-UM7 (659145) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on FORTUNA -SH7115.00 (655777) 115 kV Bus a. Apply Fault at the FORTUNA -SH7115.00 (655777) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to FORTUNA -SH7 (655777) 115.0 kV Transmission Circuit #1 b.2. FORTUNA -SH7 (655777) 115.0 kV to AMBROSE -BD7 (655784) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply Fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.5. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.7. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.8. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.9. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply Fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. E.NEWTWN-MW7 (655907) 115.0 kV to BIGBEND -MW7 (655960) 115.0 kV Transmission Circuit #1 b.4. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on CRESTON5 161.00 (652560) 161 kV Bus a. Apply Fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. BROOKS 5 (635037) 161.0 kV to ADAMS 5 (635056) 161.0 kV Transmission Circuit #1 b.5. ADAMS 5 (635056) 161.0 kV to ADAMS B1 9 (635057) 34.5 kV Two Winding #1 b.6. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.7. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON29 (652615) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. NBCS_10_-PPR (659278) 12.5 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on CROCKER_-BE3345.00 (659165) 345 kV Bus a. Apply Fault at the CROCKER_-BE3345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.3. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 b.3. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.9. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 b.10. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.5. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.6. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.7. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.10. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.9. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 b.10. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.4. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.2. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on HOSPERS8 69.000 (635371) 69 kV Bus a. Apply Fault at the HOSPERS8 69.000 (635371) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSPERS8 (635371) 69.0 kV to K213HOSP-NI8 (659955) 69.0 kV Transmission Circuit #1 b.2. HOSPERS8 (635371) 69.0 kV to SHELDON8 (635370) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply Fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RCKVALY8 (635380) 69.0 kV to DOONTAP8 (635377) 69.0 kV Transmission Circuit #1 b.2. RCKVALY8 (635380) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on RKVALTT8 69.000 (635381) 69 kV Bus a. Apply Fault at the RKVALTT8 69.000 (635381) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RKVALTT8 (635381) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit #1 b.2. RKVALTT8 (635381) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on INWOODT8 69.000 (635383) 69 kV Bus a. Apply Fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INWOODT8 (635383) 69.0 kV to HUDSON 8 (635385) 69.0 kV Transmission Circuit #1 b.2. INWOODT8 (635383) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply Fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. HUDSON 8 (635385) 69.0 kV to INWOODT8 (635383) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on IRETONT8 69.000 (635391) 69 kV Bus a. Apply Fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. IRETONT8 (635391) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #z2 b.2. GROTONSOUTH7 (652568) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. DENISON8 (652583) 69.0 kV to DENISON4 (652567) 230.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply Fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply Fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to FINSTAD345 (659060) 345.0 kV Two Winding #1 b.2. FINSTAD -MW7 (655906) 115.0 kV to FINSTAD345 (659060) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply Fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEMPLTON8 (656247) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 b.2. TEMPLTON8 (656247) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on DENISONWEST869.000 (658030) 69 kV Bus a. Apply Fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply Fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.2. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply Fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 b.2. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on L6OC E MUNI869.000 (658904) 69 kV Bus a. Apply Fault at the L6OC E MUNI869.000 (658904) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L6OC E MUNI8 (658904) 69.0 kV to L7OC W MUNI8 (658906) 69.0 kV Transmission Circuit #1 b.2. L6OC E MUNI8 (658904) 69.0 kV to L14OCINDMUN8 (658903) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on L7OC W MUNI869.000 (658906) 69 kV Bus a. Apply Fault at the L7OC W MUNI869.000 (658906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L7OC W MUNI8 (658906) 69.0 kV to L8______-NI8 (659905) 69.0 kV Transmission Circuit #1 b.2. L7OC W MUNI8 (658906) 69.0 kV to L6OC E MUNI8 (658904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply Fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #1 b.2. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.2. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on K125DUNL-NI869.000 (659853) 69 kV Bus a. Apply Fault at the K125DUNL-NI869.000 (659853) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K125DUNL-NI8 (659853) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 b.2. K125DUNL-NI8 (659853) 69.0 kV to K126MEC -NI8 (659852) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply Fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. K335AMAI-NI8 (659854) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply Fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 b.2. K318MEC -NI8 (659855) 69.0 kV to K308EARL-NI8 (659856) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply Fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. K307DENI-NI8 (659862) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on K313HALB-NI869.000 (659863) 69 kV Bus a. Apply Fault at the K313HALB-NI869.000 (659863) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K313HALB-NI8 (659863) 69.0 kV to K307DENI-NI8 (659862) 69.0 kV Transmission Circuit #1 b.2. K313HALB-NI8 (659863) 69.0 kV to K317MANN-NI8 (659906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply Fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. K306SCHL-NI8 (659885) 69.0 kV to K326OTTE-NI8 (659886) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on K228WSTB-NI869.000 (659896) 69 kV Bus a. Apply Fault at the K228WSTB-NI869.000 (659896) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K228WSTB-NI8 (659896) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 b.2. K228WSTB-NI8 (659896) 69.0 kV to L8______-NI8 (659905) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to EAGLE___-NI4 (659900) 230.0 kV Two Winding #2 b.2. EAGLE___-NI8 (659901) 69.0 kV to EAGLE___-NI4 (659900) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on L1______-NI869.000 (659902) 69 kV Bus a. Apply Fault at the L1______-NI869.000 (659902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 b.2. L1______-NI8 (659902) 69.0 kV to K213HOSP-NI8 (659955) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on L3______-NI869.000 (659904) 69 kV Bus a. Apply Fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L3______-NI8 (659904) 69.0 kV to K228WSTB-NI8 (659896) 69.0 kV Transmission Circuit #1 b.2. L3______-NI8 (659904) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on L8______-NI869.000 (659905) 69 kV Bus a. Apply Fault at the L8______-NI869.000 (659905) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L8______-NI8 (659905) 69.0 kV to L7OC W MUNI8 (658906) 69.0 kV Transmission Circuit #1 b.2. L8______-NI8 (659905) 69.0 kV to K228WSTB-NI8 (659896) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply Fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. J1CENTER-NI8 (659907) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply Fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. J6BOYER_-NI8 (659912) 69.0 kV to K335AMAI-NI8 (659854) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on J12_____-NI869.000 (659918) 69 kV Bus a. Apply Fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J12_____-NI8 (659918) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. J12_____-NI8 (659918) 69.0 kV to K125DUNL-NI8 (659853) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on J15_____-NI869.000 (659921) 69 kV Bus a. Apply Fault at the J15_____-NI869.000 (659921) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J15_____-NI8 (659921) 69.0 kV to L4SXCTNMUNI8 (658900) 69.0 kV Transmission Circuit #1 b.2. J15_____-NI8 (659921) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on K202PRES-NI869.000 (659944) 69 kV Bus a. Apply Fault at the K202PRES-NI869.000 (659944) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K202PRES-NI8 (659944) 69.0 kV to K226MERR-NI8 (659945) 69.0 kV Transmission Circuit #1 b.2. K202PRES-NI8 (659944) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on K214____-NI869.000 (659948) 69 kV Bus a. Apply Fault at the K214____-NI869.000 (659948) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K214____-NI8 (659948) 69.0 kV to K211SENY-NI8 (659949) 69.0 kV Transmission Circuit #1 b.2. K214____-NI8 (659948) 69.0 kV to K221ALTO-NI8 (659947) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 b.2. ORDWAY__-BE7 (659310) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply Fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EFORK_-BE334 (659600) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC7 (652404) 115.0 kV to DAWSONC4 (652403) 230.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 b.2. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to WILLISTON27 (652391) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.2. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.2. FTTHOM2-LNX3 (652807) 345.0 kV to FTTHOMP3 (652506) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply Fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY-LNX3 (652864) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply Fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.2. AV.LS-BD-BE3 (659420) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply Fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #1 b.2. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND-BE3 (659120) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply Fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.2. LO.LS-GR-BE3 (659422) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply Fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to GROTON__-BE3 (659160) 345.0 kV Transmission Circuit #z b.2. GR.LS-LO-BE3 (659423) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.2. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #1 b.2. CC.LS-LO-BE3 (659428) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on K213HOSP-NI869.000 (659955) 69 kV Bus a. Apply Fault at the K213HOSP-NI869.000 (659955) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K213HOSP-NI8 (659955) 69.0 kV to L1______-NI8 (659902) 69.0 kV Transmission Circuit #1 b.2. K213HOSP-NI8 (659955) 69.0 kV to HOSPERS8 (635371) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on K218ROCK-NI869.000 (659977) 69 kV Bus a. Apply Fault at the K218ROCK-NI869.000 (659977) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K218ROCK-NI8 (659977) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 b.2. K218ROCK-NI8 (659977) 69.0 kV to RKVALTT8 (635381) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE4 (659334) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. JUDSON__-BE4 (659334) 230.0 kV to JUDSON__-BE3 (659333) 345.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE7 (659187) 115.0 kV to GROTON__-BE3 (659160) 345.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 b.2. GROTON__-BE7 (659187) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on MANNINGTAP 869.000 (656267) 69 kV Bus a. Apply Fault at the MANNINGTAP 869.000 (656267) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANNINGTAP 8 (656267) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. MANNINGTAP 8 (656267) 69.0 kV to TEMPLTON8 (656247) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on DENSOUMAIN8 69.000 (658031) 69 kV Bus a. Apply Fault at the DENSOUMAIN8 69.000 (658031) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENSOUMAIN8 (658031) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. DENSOUMAIN8 (658031) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on OSBORN -MW7115.00 (655919) 115 kV Bus a. Apply Fault at the OSBORN -MW7115.00 (655919) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSBORN -MW7 (655919) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.2. OSBORN -MW7 (655919) 115.0 kV to E.NEWTWN-MW7 (655907) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on K338WTCT-NI869.000 (659897) 69 kV Bus a. Apply Fault at the K338WTCT-NI869.000 (659897) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K338WTCT-NI8 (659897) 69.0 kV to K335AMAI-NI8 (659854) 69.0 kV Transmission Circuit #1 b.2. K338WTCT-NI8 (659897) 69.0 kV to K318MEC -NI8 (659855) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on K308EARL-NI869.000 (659856) 69 kV Bus a. Apply Fault at the K308EARL-NI869.000 (659856) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K308EARL-NI8 (659856) 69.0 kV to K318MEC -NI8 (659855) 69.0 kV Transmission Circuit #1 b.2. K308EARL-NI8 (659856) 69.0 kV to K321MEC -NI8 (659857) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on K317MANN-NI869.000 (659906) 69 kV Bus a. Apply Fault at the K317MANN-NI869.000 (659906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K317MANN-NI8 (659906) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 b.2. K317MANN-NI8 (659906) 69.0 kV to K330MANM-NI8 (659864) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on K326OTTE-NI869.000 (659886) 69 kV Bus a. Apply Fault at the K326OTTE-NI869.000 (659886) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K326OTTE-NI8 (659886) 69.0 kV to K306SCHL-NI8 (659885) 69.0 kV Transmission Circuit #1 b.2. K326OTTE-NI8 (659886) 69.0 kV to K333SCHL-NI8 (659887) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on K217HWDN-NI869.000 (659942) 69 kV Bus a. Apply Fault at the K217HWDN-NI869.000 (659942) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K217HWDN-NI8 (659942) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. K217HWDN-NI8 (659942) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply Fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K222HULL-NI8 (659941) 69.0 kV to L4SXCTNMUNI8 (658900) 69.0 kV Transmission Circuit #1 b.2. K222HULL-NI8 (659941) 69.0 kV to L1______-NI8 (659902) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on K207OC N-NI869.000 (659943) 69 kV Bus a. Apply Fault at the K207OC N-NI869.000 (659943) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K207OC N-NI8 (659943) 69.0 kV to L1______-NI8 (659902) 69.0 kV Transmission Circuit #1 b.2. K207OC N-NI8 (659943) 69.0 kV to L8______-NI8 (659905) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply Fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K223SIOU-NI8 (659940) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 b.2. K223SIOU-NI8 (659940) 69.0 kV to L5SXCTWMUNI8 (658902) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on K106CHAR-NI869.000 (659999) 69 kV Bus a. Apply Fault at the K106CHAR-NI869.000 (659999) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K106CHAR-NI8 (659999) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 b.2. K106CHAR-NI8 (659999) 69.0 kV to K105UTE_-NI8 (659998) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on K226MERR-NI869.000 (659945) 69 kV Bus a. Apply Fault at the K226MERR-NI869.000 (659945) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K226MERR-NI8 (659945) 69.0 kV to K225ADAV-NI8 (659899) 69.0 kV Transmission Circuit #1 b.2. K226MERR-NI8 (659945) 69.0 kV to K202PRES-NI8 (659944) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #1 b.2. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to KILDEER7 (652419) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE4 (659337) 230.0 kV to TANDE___-BE3 (659336) 345.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 b.2. TANDE___-BE4 (659337) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on MONT -MW7 115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7 115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7 115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7 115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply Fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on DENISON8 69.00 (652583) 69 kV Bus a. Apply Fault at the DENISON8 69.00 (652583) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on J6BOYER_-NI8 69.00 (659912) 69 kV Bus a. Apply Fault at the J6BOYER_-NI8 69.00 (659912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on EAGLE___-NI8 69.00 (659901) 69 kV Bus a. Apply Fault at the EAGLE___-NI8 69.00 (659901) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on J1CENTER-NI8 69.00 (659907) 69 kV Bus a. Apply Fault at the J1CENTER-NI8 69.00 (659907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on L1______-NI8 69.00 (659902) 69 kV Bus a. Apply Fault at the L1______-NI8 69.00 (659902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L1______-NI8 (659902) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3 345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3 345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on MAPLE R3 345.00 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 345.00 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.4. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.3. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BROWNSV4 230.00 (620325) 230 kV Bus a. Apply Fault at the BROWNSV4 230.00 (620325) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 41.6 kV Transmission Circuit #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.2. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.5. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.6. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.7. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.8. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.11. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.12. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.14. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.15. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.19. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.20. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.21. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.23. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply Fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. RUGBY T (620179) 13.8 kV to RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. HRDLKCOL9 (620114) 34.5 kV to G380 RUGBY W (620115) 0.6 kV Two Winding #1 b.3. HRDLKCOL9 (620114) 34.5 kV to RGBYCOL9 (620168) 34.5 kV Transmission Circuit #1 b.4. RGBYWND4 (620368) 230.0 kV to RGBYCOL9 (620168) 34.5 kV Two Winding #1 b.5. RGBYWND4 (620368) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4230.00 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4230.00 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.3. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.4. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.5. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.7. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply Fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on ASTORIA 3 345.00 (620483) 345 kV Bus a. Apply Fault at the ASTORIA 3 345.00 (620483) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASTORIA 3 (620483) 345.0 kV to BRKNGCO3 (601031) 345.0 kV Transmission Circuit #1 b.2. ASTORIA 3 (620483) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on BDV 4230.00 (672603) 230 kV Bus a. Apply Fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to CSLTNET7 (620180) 115.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_UMZ_FAULT_001 | Single Phase Fault with Stuck Breaker on AVS 345 (659420) 345 kV Bus a. Apply Fault at the AVS 345 (659420) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to remove bus #1 b.2. COTEAU_1-RR8 (659222) 69.0 kV to Load #BB b.3. COTEAU_1-RR8 (659222) 69.0 kV to Load #BW b.4. DGC UREA-BE8 (659236) 69.0 kV to Load #BG b.5. COTEAU 1-RR9 (659219) 13.8 kV to remove bus # b.6. COTEAU 2-RR9 (659231) 13.8 kV to remove bus # b.7. COTEAU_1-RR8 (659222) 69.0 kV to remove bus # b.8. COTEAU__-RR3 (659218) 345.0 kV to remove bus # b.9. DGC UREA-BE8 (659236) 69.0 kV to remove bus # b.10. AV.LS-BD-BE3 (659420) 345.0 kV to remove bus # b.11. AV.LS-BD-BE3 (659420) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_UMZ_FAULT_002 | Single Phase Fault with Stuck Breaker on LOS 345 (659424) 345 kV Bus a. Apply Fault at the LOS 345 (659424) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #Z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to Switched Shunt Device # b.3. CC.LS-LO-BE3 (659428) 345.0 kV to Switched Shunt Device # b.4. LELAND_2-BEG (659111) 20.0 kV to Load #S0 b.5. LELAND_2-BEG (659111) 20.0 kV to Generator #2 b.6. LELAND_2-BEG (659111) 20.0 kV to remove bus # b.7. CC.LS-LO-BE3 (659428) 345.0 kV to remove bus # b.8. LO.LS-FT-BE3 (659424) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_UMZ_FAULT_003 | Single Phase Fault with Stuck Breaker on LOS 345 (659422) 345 kV Bus a. Apply Fault at the LOS 345 (659422) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to GROTON__-BE3 (659160) 345.0 kV Transmission Circuit #Z b.2. GR.LS-LO-BE3 (659423) 345.0 kV to Switched Shunt Device # b.3. LO.LS-GR-BE3 (659422) 345.0 kV to Switched Shunt Device # b.4. LO.KU1A_-BE9 (659201) 13.8 kV to Switched Shunt Device # b.5. LO.LS-GR-BE3 (659422) 345.0 kV to remove bus # b.6. GR.LS-LO-BE3 (659423) 345.0 kV to remove bus # b.7. LO.KU1A_-BE9 (659201) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_UMZ_FAULT_004 | Single Phase Fault with Stuck Breaker on LOS 230 (659106) 230 kV Bus a. Apply Fault at the LOS 230 (659106) 230 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to Load #BB b.3. BASIN___-BE7 (659109) 115.0 kV to Load #BW b.4. BASIN___-BE7 (659109) 115.0 kV to Load #W0 b.5. LELAND_1-BEG (659110) 22.0 kV to Load #S0 b.6. LELAND_1-BEG (659110) 22.0 kV to Generator #1 b.7. NEWSALEM-MG7 (655748) 115.0 kV to Load #BB b.8. NEWSALEM-MG7 (655748) 115.0 kV to Load #BW b.9. ROUGHRDR-MG7 (655750) 115.0 kV to Load #BB b.10. ROUGHRDR-MG7 (655750) 115.0 kV to Load #BW b.11. NRWSTMDN-MG7 (655751) 115.0 kV to Load #BB b.12. NRWSTMDN-MG7 (655751) 115.0 kV to Load #BW b.13. DEVAUL -MG8 (655746) 69.0 kV to Load #W0 b.14. CANNON -MG8 (655740) 69.0 kV to Load #BB b.15. CANNON -MG8 (655740) 69.0 kV to Load #BW b.16. CEDAR -MG8 (655741) 69.0 kV to Load #BB b.17. CEDAR -MG8 (655741) 69.0 kV to Load #BW b.18. GRANT -MG8 (655742) 69.0 kV to Load #BB b.19. GRANT -MG8 (655742) 69.0 kV to Load #BW b.20. FLASHER -MG8 (655732) 69.0 kV to Load #BB b.21. FLASHER -MG8 (655732) 69.0 kV to Load #BW b.22. LO.KU1A_-BE9 (659201) 13.8 kV to remove bus # b.23. LO.KVA2_-BE9 (659202) 13.8 kV to remove bus # b.24. BAL.KY1A-BE9 (659200) 13.8 kV to remove bus # b.25. LELAND_O-BE4 (659106) 230.0 kV to remove bus # b.26. BASIN___-BE7 (659109) 115.0 kV to remove bus # b.27. BASIN___-BE4 (659199) 230.0 kV to remove bus # b.28. LELAND_1-BEG (659110) 22.0 kV to remove bus # b.30. NEWSALEM-MG7 (655748) 115.0 kV to remove bus # b.31. MANSWTCH-MG7 (655749) 115.0 kV to remove bus # b.32. ROUGHRDR-MG7 (655750) 115.0 kV to remove bus # b.33. NRWSTMDN-MG7 (655751) 115.0 kV to remove bus # b.34. NWMDNTAP-MG7 (655752) 115.0 kV to remove bus # b.35. DEVAUL -MG8 (655746) 69.0 kV to remove bus # b.36. DEVALTP -MG8 (655744) 69.0 kV to remove bus # b.37. DEVAUL 8 (652257) 69.0 kV to remove bus # b.38. LARK -MG8 (655731) 69.0 kV to remove bus # b.39. CANNON -MG8 (655740) 69.0 kV to remove bus # b.40. CEDAR -MG8 (655741) 69.0 kV to remove bus # b.41. GRANT -MG8 (655742) 69.0 kV to remove bus # b.42. FLASHER -MG8 (655732) 69.0 kV to remove bus # b.44. DEVAUL -MG7 (655747) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_UMZ_FAULT_005 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_UMZ_FAULT_006 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_UMZ_FAULT_007 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 b.2. CCR.KV4A-BE9 (659319) 13.8 kV to remove bus # b.3. CCR.KV3A-BE9 (659318) 13.8 kV to remove bus # b.4. CHARL_CK-BE4 (659302) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP1_P4_UMZ_FAULT_008 | Single Phase Fault with Stuck Breaker on JDS 345 (659333) 345 kV Bus a. Apply Fault at the JDS 345 (659333) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to remove bus # b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_001 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_002 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_003 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_004 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_005 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_006 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_007 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_008 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_009 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_010 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_011 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_012 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_013 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_014 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_015 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_016 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_017 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_018 | 3 Phase fault on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_019 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_020 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_021 | 3 Phase fault on PLNTYWD7 115.00 (661077) 115 kV Bus a. Apply fault at the PLNTYWD7 115.00 (661077) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLNTYWD7 (661077) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_022 | 3 Phase fault on LEMARST5 161.00 (635260) 161 kV Bus a. Apply fault at the LEMARST5 161.00 (635260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_023 | 3 Phase fault on LTL SIOUX 5 161.00 (635360) 161 kV Bus a. Apply fault at the LTL SIOUX 5 161.00 (635360) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.2. CLIPPER5 (635350) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.3. LTL SIOUX 5 (635360) 161.0 kV to LTL SIOUX 8 (635361) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_025 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_026 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_027 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_028 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_029 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_030 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_031 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_032 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_033 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_034 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON1AG (608891), BISON 4G (608894), BISON5BG (608895), BISON1BG (608897) and BISON5AG (608898). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_035 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_036 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_037 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_038 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_039 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_040 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_041 | 3 Phase fault on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_042 | 3 Phase fault on LKFLDXL3 345.00 (601029) 345 kV Bus a. Apply fault at the LKFLDXL3 345.00 (601029) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LKFLDXL3 (601029) 345.0 kV to CRANDAL 3 (601074) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_043 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_044 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_045 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_046 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to ROCK CO5 (602039) 161.0 kV Transmission Circuit #1 b.2. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_047 | 3 Phase fault on CAYLER5 161.00 (631183) 161 kV Bus a. Apply fault at the CAYLER5 161.00 (631183) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_050 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_051 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_052 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_053 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_054 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_055 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_056 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_057 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_058 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_059 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_060 | 3 Phase fault on BVISTA 5 161.00 (635280) 161 kV Bus a. Apply fault at the BVISTA 5 161.00 (635280) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_063 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_064 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_065 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_066 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_067 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on DENISON5 161.00 (652561) 161 kV Bus a. Apply fault at the DENISON5 161.00 (652561) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_069 | 3 Phase fault on OSGOOD5 161.00 (656527) 161 kV Bus a. Apply fault at the OSGOOD5 161.00 (656527) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_070 | 3 Phase fault on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_071 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_072 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_073 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_074 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_075 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_076 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_077 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_078 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_079 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_080 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_081 | 3 Phase fault on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRENORA_-UM7 (659145) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_082 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_083 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_084 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_085 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_086 | 3 Phase fault on DENISONWEST869.000 (658030) 69 kV Bus a. Apply fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_087 | 3 Phase fault on TERRY TAP 115.00 (652394) 115 kV Bus a. Apply fault at the TERRY TAP 115.00 (652394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY TAP (652394) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_088 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_089 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_090 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_091 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_092 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. ARMOUR 7 (652501) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_093 | 3 Phase fault on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_094 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_095 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_096 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_097 | 3 Phase fault on E.SIDNEY-LY7115.00 (659186) 115 kV Bus a. Apply fault at the E.SIDNEY-LY7115.00 (659186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.3. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_098 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_099 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_101 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_102 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_103 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_104 | 3 Phase fault on HAZLTON L2 5161.00 (631051) 161 kV Bus a. Apply fault at the HAZLTON L2 5161.00 (631051) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.4. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.5. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.6. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.7. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.8. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.9. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.10. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.11. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_105 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_106 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_107 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_108 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_109 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_110 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_111 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_112 | 3 Phase fault on NEWSALEM-MG7115.00 (655748) 115 kV Bus a. Apply fault at the NEWSALEM-MG7115.00 (655748) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_113 | 3 Phase fault on WOONSKT7 115.00 (652528) 115 kV Bus a. Apply fault at the WOONSKT7 115.00 (652528) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.3. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.4. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_114 | 3 Phase fault on ABERDN JCT 7115.00 (660000) 115 kV Bus a. Apply fault at the ABERDN JCT 7115.00 (660000) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_115 | 3 Phase fault on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_116 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_117 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_118 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_119 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_120 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_121 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_122 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_123 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_124 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_125 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_126 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_127 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_129 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_130 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_131 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from PS_RCP.B-BEG (659432 and 659431). Disabling the dynamic controller model allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_132 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_133 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_134 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_135 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_136 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_137 | 3 Phase fault on N.WILSTN-MW7115.00 (655936) 115 kV Bus a. Apply fault at the N.WILSTN-MW7115.00 (655936) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_138 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to SE.WLSTN-MW7 (655938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_139 | 3 Phase fault on ALKABO -SH7115.00 (655776) 115 kV Bus a. Apply fault at the ALKABO -SH7115.00 (655776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_140 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_141 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_142 | 3 Phase fault on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_143 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN-LNX3 (652829) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_144 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_145 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_146 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_147 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_148 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_149 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_150 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_151 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_152 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_153 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_154 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_155 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_156 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_157 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_158 | 3 Phase fault on J1620 POI 115.00 (46207) 115 kV Bus a. Apply fault at the J1620 POI 115.00 (46207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1620 POI (46207) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_159 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_160 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_161 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_162 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_163 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_164 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_165 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_166 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_167 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_168 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_169 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_170 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to MERRIL 8 (635393) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_171 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to SIOUXCY8 (652574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_172 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_173 | 3 Phase fault on LOGANPK8 69.000 (635245) 69 kV Bus a. Apply fault at the LOGANPK8 69.000 (635245) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGANPK8 (635245) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_174 | 3 Phase fault on EASTSID8 69.000 (635247) 69 kV Bus a. Apply fault at the EASTSID8 69.000 (635247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTSID8 (635247) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_175 | 3 Phase fault on LEMARS S 8 69.000 (635262) 69 kV Bus a. Apply fault at the LEMARS S 8 69.000 (635262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEMARS S 8 (635262) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_176 | 3 Phase fault on MERRIL 8 69.000 (635393) 69 kV Bus a. Apply fault at the MERRIL 8 69.000 (635393) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIL 8 (635393) 69.0 kV to MERRILN8 (635394) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_177 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_178 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_179 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_180 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_181 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_182 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_183 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_184 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_185 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_186 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_187 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_188 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to FERNEY-ER8 (655256) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_189 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON-ER8 (655267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_190 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to NWPS509-ER8 (655395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_191 | 3 Phase fault on GROTON2 869.000 (652253) 69 kV Bus a. Apply fault at the GROTON2 869.000 (652253) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON (660430) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_192 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_193 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_194 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_195 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_196 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_197 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_198 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_199 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_200 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_201 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_202 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_203 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_204 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_205 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_206 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_207 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_208 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_209 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_210 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_211 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_212 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_213 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_214 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_215 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_216 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_217 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_218 | 3 Phase fault on SUMMIT-7 115.00 (652522) 115 kV Bus a. Apply fault at the SUMMIT-7 115.00 (652522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_219 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_220 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_221 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_222 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_223 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_224 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_225 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_226 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_227 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_228 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_229 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_230 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K216LIBE-NI8 (659946) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_231 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_232 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K301HINT-NI8 (659971) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_233 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K135CONC-NI8 (659980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_234 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_235 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_236 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to BEAVRHIL-GW4 (659535) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_237 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_238 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_239 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_240 | 3 Phase fault on MOS-RDFL-ER869.000 (655054) 69 kV Bus a. Apply fault at the MOS-RDFL-ER869.000 (655054) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-RDFL-ER8 (655054) 69.0 kV to REDFELD-ER8 (655482) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_241 | 3 Phase fault on MOS-ASHT-ER869.000 (655059) 69 kV Bus a. Apply fault at the MOS-ASHT-ER869.000 (655059) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-ASHT-ER8 (655059) 69.0 kV to REDFELD-ER8 (655482) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_242 | 3 Phase fault on MOS-CLRM-ER869.000 (655082) 69 kV Bus a. Apply fault at the MOS-CLRM-ER869.000 (655082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CLRM-ER8 (655082) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_243 | 3 Phase fault on MOS-VERM-ER869.000 (655126) 69 kV Bus a. Apply fault at the MOS-VERM-ER869.000 (655126) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VERM-ER8 (655126) 69.0 kV to SW870-ER8 (655145) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_244 | 3 Phase fault on SW808-ER8 69.000 (655130) 69 kV Bus a. Apply fault at the SW808-ER8 69.000 (655130) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW808-ER8 (655130) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_245 | 3 Phase fault on SW832-ER8 69.000 (655136) 69 kV Bus a. Apply fault at the SW832-ER8 69.000 (655136) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW832-ER8 (655136) 69.0 kV to SW873-ER8 (655146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_246 | 3 Phase fault on SW833-ER8 69.000 (655137) 69 kV Bus a. Apply fault at the SW833-ER8 69.000 (655137) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW833-ER8 (655137) 69.0 kV to MOS-JEFF-ER8 (655147) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_247 | 3 Phase fault on SW870-ER8 69.000 (655145) 69 kV Bus a. Apply fault at the SW870-ER8 69.000 (655145) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW870-ER8 (655145) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_248 | 3 Phase fault on SW873-ER8 69.000 (655146) 69 kV Bus a. Apply fault at the SW873-ER8 69.000 (655146) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW873-ER8 (655146) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_249 | 3 Phase fault on MOS-JEFF-ER869.000 (655147) 69 kV Bus a. Apply fault at the MOS-JEFF-ER869.000 (655147) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-JEFF-ER8 (655147) 69.0 kV to RASMUSN-ER8 (655485) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_250 | 3 Phase fault on ABERDEEN-ER869.000 (655262) 69 kV Bus a. Apply fault at the ABERDEEN-ER869.000 (655262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDEEN-ER8 (655262) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_251 | 3 Phase fault on BATH-ER8 69.000 (655269) 69 kV Bus a. Apply fault at the BATH-ER8 69.000 (655269) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATH-ER8 (655269) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_252 | 3 Phase fault on MANSWTCH-MG7115.00 (655749) 115 kV Bus a. Apply fault at the MANSWTCH-MG7115.00 (655749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANSWTCH-MG7 (655749) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_253 | 3 Phase fault on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_254 | 3 Phase fault on ALKABO -SH7115.00 (655776) 115 kV Bus a. Apply fault at the ALKABO -SH7115.00 (655776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALKABO -SH7 (655776) 115.0 kV to FORTUNA -SH7 (655777) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_255 | 3 Phase fault on HELMUT -LY7115.00 (655790) 115 kV Bus a. Apply fault at the HELMUT -LY7115.00 (655790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_256 | 3 Phase fault on MARLEY -LY7115.00 (655793) 115 kV Bus a. Apply fault at the MARLEY -LY7115.00 (655793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLEY -LY7 (655793) 115.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_257 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to GRASSYBT-MK7 (655834) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_258 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_259 | 3 Phase fault on OAKDALE -MK7115.00 (655836) 115 kV Bus a. Apply fault at the OAKDALE -MK7115.00 (655836) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKDALE -MK7 (655836) 115.0 kV to BEARCREK-MK7 (655853) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_260 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_261 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_262 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_263 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_264 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_265 | 3 Phase fault on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEMPLTON8 (656247) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_266 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_267 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_268 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_269 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_270 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_271 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_272 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_273 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_274 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_275 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_276 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_277 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_278 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_279 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_280 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_281 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_282 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_283 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_284 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to 32STREET-RR7 (659442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_285 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to PRNGHORN-RR7 (659544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_286 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_287 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_288 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_289 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_290 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_291 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_292 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_293 | 3 Phase fault on K125DUNL-NI869.000 (659853) 69 kV Bus a. Apply fault at the K125DUNL-NI869.000 (659853) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K125DUNL-NI8 (659853) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_294 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_295 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_296 | 3 Phase fault on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K308EARL-NI8 (659856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_297 | 3 Phase fault on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_298 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_299 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_300 | 3 Phase fault on K313HALB-NI869.000 (659863) 69 kV Bus a. Apply fault at the K313HALB-NI869.000 (659863) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K313HALB-NI8 (659863) 69.0 kV to K317MANN-NI8 (659906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_301 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to K326OTTE-NI8 (659886) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_302 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_303 | 3 Phase fault on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_304 | 3 Phase fault on J12_____-NI869.000 (659918) 69 kV Bus a. Apply fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J12_____-NI8 (659918) 69.0 kV to K106CHAR-NI8 (659999) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_305 | 3 Phase fault on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_306 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_307 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_308 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_309 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_310 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_311 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_312 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_313 | 3 Phase fault on FALLON 7 115.00 (652407) 115 kV Bus a. Apply fault at the FALLON 7 115.00 (652407) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FALLON 7 (652407) 115.0 kV to FALLON 8 (652213) 69.0 kV to FALLON 9 (652214) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_314 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_315 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_316 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_317 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_318 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_319 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_320 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_321 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_322 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_323 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_324 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_325 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_326 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_327 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_328 | 3 Phase fault on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_329 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_330 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_331 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_332 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_333 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_334 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037-GEN1 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_335 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_336 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_337 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_338 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_339 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_340 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_341 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_342 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_343 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_344 | 3 Phase fault on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_345 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_346 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_347 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_348 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_349 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_350 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_351 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_352 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_353 | 3 Phase fault on BEAVRHIL-GW4230.00 (659535) 230 kV Bus a. Apply fault at the BEAVRHIL-GW4230.00 (659535) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVRHIL-GW4 (659535) 230.0 kV to BEAVRHIL-GW7 (659536) 115.0 kV to BEAVRHIL-GW9 (659537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_354 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_355 | 3 Phase fault on BAKER 4 230.00 (661004) 230 kV Bus a. Apply fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_356 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_357 | 3 Phase fault on MI CTYW4 230.00 (652402) 230 kV Bus a. Apply fault at the MI CTYW4 230.00 (652402) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYW4 (652402) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_358 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_359 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_360 | 3 Phase fault on MI CTYE7 115.00 (652412) 115 kV Bus a. Apply fault at the MI CTYE7 115.00 (652412) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE7 (652412) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_361 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_362 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_363 | 3 Phase fault on REDFELD-ER8 69.000 (655482) 69 kV Bus a. Apply fault at the REDFELD-ER8 69.000 (655482) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDFELD-ER8 (655482) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_364 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_365 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_366 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_001 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_002 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_004 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_005 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_007 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_009 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_010 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_017 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_020 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_021 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.3. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_022 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_023 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_024 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_025 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_026 | 3 Phase fault on NUNDRWD-LNX3230.00 (652884) 230 kV Bus a. Apply fault at the NUNDRWD-LNX3230.00 (652884) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_028 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_029 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_030 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_031 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_032 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_033 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_035 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_036 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_037 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_041 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_050 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_051 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_052 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_053 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). The issue is also present in the base case and is not impacted by CQ units. Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_057 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_058 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_059 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_060 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply Fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.5. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.6. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.4. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LEWIS 7 115.00 (661056) 115 kV Bus a. Apply Fault at the LEWIS 7 115.00 (661056) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.2. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.3. LEWIS 7 (661056) 115.0 kV to LEWIS71G (661055) 13.8 kV Two Winding #1 b.4. LEWIS 7 (661056) 115.0 kV to LEWIS72G (661104) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. BEULAH 7 (661008) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #z b.5. BEULAH 7 (661008) 115.0 kV to COYOTE 7 (661018) 115.0 kV Transmission Circuit #1 b.6. BEULAH 7 (661008) 115.0 kV to COYOTETAP 7 (661057) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply Fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 b.3. GLENDCT7 (661032) 115.0 kV to Load #Y0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply Fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 b.3. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.4. GLENDCT7 (661032) 115.0 kV to GLNDCT1G (661100) 13.8 kV Two Winding #1 b.5. GLENDCT7 (661032) 115.0 kV to GLNDCT2G (661101) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LTLMUDY7 115.00 (661089) 115 kV Bus a. Apply Fault at the LTLMUDY7 115.00 (661089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.3. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.4. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.5. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.6. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.7. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ANTA TP5 161.00 (631069) 161 kV Bus a. Apply Fault at the ANTA TP5 161.00 (631069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.4. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.5. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on CRESTON5 161.00 (652560) 161 kV Bus a. Apply Fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.5. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON 9 (652612) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.2. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.3. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.6. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.7. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.5. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.6. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.7. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.8. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.9. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.10. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to GARISN4G (652460) 13.8 kV Two Winding #1 b.2. GARRISN7 (652442) 115.0 kV to GARISN5G (652461) 13.8 kV Two Winding #1 b.3. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.6. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 b.7. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.3. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to GARISN2G (652458) 13.8 kV Two Winding #1 b.3. GARRISN4 (652441) 230.0 kV to GARISN3G (652459) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.4. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 b.5. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.4. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.5. HURON429 (652282) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply Fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply Fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on HAZLTON L2 5161.00 (631051) 161 kV Bus a. Apply Fault at the HAZLTON L2 5161.00 (631051) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.3. HAZLTON J2 8 (630256) 69.0 kV to HAZLTON L2 5 (631051) 161.0 kV Two Winding #1 b.4. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.5. HAZLTON L1 5 (631050) 161.0 kV to HAZLTON L2 5 (631051) 161.0 kV Transmission Circuit #1 b.6. HAZLTON L2 5 (631051) 161.0 kV to DUNDEE 5 (631101) 161.0 kV Transmission Circuit #1 b.7. HAZLTON L2 5 (631051) 161.0 kV to HAZLTON3 (631139) 345.0 kV Two Winding #2 b.8. HAZLTON L2 5 (631051) 161.0 kV to GILBERTVLL5 (636212) 161.0 kV Transmission Circuit #1 b.9. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.10. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.11. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on GU CTR 5 161.00 (631072) 161 kV Bus a. Apply Fault at the GU CTR 5 161.00 (631072) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HD WIND 5 (628910) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. HD WIND 5 (628910) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.3. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #1 b.4. GU CTR J1 8 (629411) 69.0 kV to GU CTR 5 (631072) 161.0 kV Two Winding #2 b.5. ANITA 8 (630009) 69.0 kV to ANITA 5 (631070) 161.0 kV Two Winding #1 b.6. TURK RV8 (630282) 69.0 kV to TRK RIV5 (631060) 161.0 kV Two Winding #1 b.7. TRK RIV5 (631060) 161.0 kV to LORE L1 5 (631223) 161.0 kV Transmission Circuit #1 b.8. TRK RIV5 (631060) 161.0 kV to STONEMAN (681519) 161.0 kV Transmission Circuit #1 b.9. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.10. SCRANTN5 (631071) 161.0 kV to SCRANTN9 (629111) 34.5 kV Two Winding #1 b.11. SCRANTN5 (631071) 161.0 kV to GU CTR 5 (631072) 161.0 kV Transmission Circuit #1 b.12. SCRANTN5 (631071) 161.0 kV to GR JCT 5 (631074) 161.0 kV Transmission Circuit #1 b.13. GU CTR 5 (631072) 161.0 kV to GU CTR 9 (629113) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply Fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. HEBRON 4 (652468) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.3. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to None Three Winding #1 b.4. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DK.KW1A_-BE9 (659197) 13.8 kV Three Winding #1 b.5. DICKINSN-BE4 (659124) 230.0 kV to DICKINS2-BE7 (659195) 115.0 kV to DK.KW1A_-BE9 (659196) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.2. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 b.3. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 b.4. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.5. BASIN___-BE7 (659109) 115.0 kV to BASIN___-BE4 (659199) 230.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply Fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.4. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. DAWSONC7 (652404) 115.0 kV to DAWSONC4 (652403) 230.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY9 (652322) 41.6 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.4. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.5. EDGELEY 19 (652328) 13.2 kV to EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.2. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.3. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.4. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.5. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.6. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.9. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on ECKLUND1-PP934.500 (659322) 34.5 kV Bus a. Apply Fault at the ECKLUND1-PP934.500 (659322) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.6. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.7. ECKLUND1-PP9 (659322) 34.5 kV to WILTON_1-PPW (659294) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7 115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7 115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to Load #BB b.6. GARRISN7 (652442) 115.0 kV to Load #BW b.7. GARRISN7 (652442) 115.0 kV to Load #R0 b.8. GARRISN7 (652442) 115.0 kV to Load #W0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.3. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.4. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.6. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.7. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply Fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. ROCKRPDMUNI8 (658122) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.3. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 b.4. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.5. RKRPDTAP-LO8 (659714) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.6. LESTERSS-LO8 (659722) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.7. STEEN -LO8 (659726) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.8. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. EXIRA 5 (652603) 161.0 kV to EXIRA 2G (658001) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.11. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.3. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.4. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.5. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.6. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.7. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.5. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.6. SIOUXF19 (652232) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 b.7. SIOUXF29 (652233) 13.2 kV to SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on SPENCER5 161.00 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.2. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.3. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.4. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.5. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.6. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply Fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.4. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 b.2. GRENORA_-UM7 (659145) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. GRENORA_-UM7 (659145) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. GRENORA_-UM7 (659145) 115.0 kV to PLNTYWD7 (661077) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on FORTUNA -SH7115.00 (655777) 115 kV Bus a. Apply Fault at the FORTUNA -SH7115.00 (655777) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALKABO -SH7 (655776) 115.0 kV to FORTUNA -SH7 (655777) 115.0 kV Transmission Circuit #1 b.2. FORTUNA -SH7 (655777) 115.0 kV to AMBROSE -BD7 (655784) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply Fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.5. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.7. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.8. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.9. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply Fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. E.NEWTWN-MW7 (655907) 115.0 kV to BIGBEND -MW7 (655960) 115.0 kV Transmission Circuit #1 b.4. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on CRESTON5 161.00 (652560) 161 kV Bus a. Apply Fault at the CRESTON5 161.00 (652560) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTA TP5 (631069) 161.0 kV to ANITA 5 (631070) 161.0 kV Transmission Circuit #1 b.2. ANTA TP5 (631069) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.3. ANTA TP5 (631069) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.4. BROOKS 5 (635037) 161.0 kV to ADAMS 5 (635056) 161.0 kV Transmission Circuit #1 b.5. ADAMS 5 (635056) 161.0 kV to ADAMS B1 9 (635057) 34.5 kV Two Winding #1 b.6. ADAMS 5 (635056) 161.0 kV to CRESTON5 (652560) 161.0 kV Transmission Circuit #1 b.7. CRESTON5 (652560) 161.0 kV to CRESTON8 (652569) 69.0 kV to CRESTON29 (652615) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. NBCS_10_-PPR (659278) 12.5 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on CROCKER_-BE3345.00 (659165) 345 kV Bus a. Apply Fault at the CROCKER_-BE3345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.3. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 b.3. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.9. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 b.10. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.5. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.6. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.7. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.10. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.9. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 b.10. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.4. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.2. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on HOSPERS8 69.000 (635371) 69 kV Bus a. Apply Fault at the HOSPERS8 69.000 (635371) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSPERS8 (635371) 69.0 kV to K213HOSP-NI8 (659955) 69.0 kV Transmission Circuit #1 b.2. HOSPERS8 (635371) 69.0 kV to SHELDON8 (635370) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on RCKVALY8 69.000 (635380) 69 kV Bus a. Apply Fault at the RCKVALY8 69.000 (635380) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RCKVALY8 (635380) 69.0 kV to DOONTAP8 (635377) 69.0 kV Transmission Circuit #1 b.2. RCKVALY8 (635380) 69.0 kV to IRETONT8 (635391) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on RKVALTT8 69.000 (635381) 69 kV Bus a. Apply Fault at the RKVALTT8 69.000 (635381) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RKVALTT8 (635381) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit #1 b.2. RKVALTT8 (635381) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on INWOODT8 69.000 (635383) 69 kV Bus a. Apply Fault at the INWOODT8 69.000 (635383) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INWOODT8 (635383) 69.0 kV to HUDSON 8 (635385) 69.0 kV Transmission Circuit #1 b.2. INWOODT8 (635383) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply Fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. HUDSON 8 (635385) 69.0 kV to INWOODT8 (635383) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on IRETONT8 69.000 (635391) 69 kV Bus a. Apply Fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. IRETONT8 (635391) 69.0 kV to RCKVALY8 (635380) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #z2 b.2. GROTONSOUTH7 (652568) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. DENISON8 (652583) 69.0 kV to DENISON4 (652567) 230.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply Fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply Fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to FINSTAD345 (659060) 345.0 kV Two Winding #1 b.2. FINSTAD -MW7 (655906) 115.0 kV to FINSTAD345 (659060) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on TEMPLTON8 69.000 (656247) 69 kV Bus a. Apply Fault at the TEMPLTON8 69.000 (656247) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEMPLTON8 (656247) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 b.2. TEMPLTON8 (656247) 69.0 kV to TOYNE8 (656249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on DENISONWEST869.000 (658030) 69 kV Bus a. Apply Fault at the DENISONWEST869.000 (658030) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISONWEST8 (658030) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. DENISONWEST8 (658030) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on L4SXCTNMUNI869.000 (658900) 69 kV Bus a. Apply Fault at the L4SXCTNMUNI869.000 (658900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L4SXCTNMUNI8 (658900) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 b.2. L4SXCTNMUNI8 (658900) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on L5SXCTWMUNI869.000 (658902) 69 kV Bus a. Apply Fault at the L5SXCTWMUNI869.000 (658902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L5SXCTWMUNI8 (658902) 69.0 kV to K223SIOU-NI8 (659940) 69.0 kV Transmission Circuit #1 b.2. L5SXCTWMUNI8 (658902) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on L6OC E MUNI869.000 (658904) 69 kV Bus a. Apply Fault at the L6OC E MUNI869.000 (658904) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L6OC E MUNI8 (658904) 69.0 kV to L7OC W MUNI8 (658906) 69.0 kV Transmission Circuit #1 b.2. L6OC E MUNI8 (658904) 69.0 kV to L14OCINDMUN8 (658903) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on L7OC W MUNI869.000 (658906) 69 kV Bus a. Apply Fault at the L7OC W MUNI869.000 (658906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L7OC W MUNI8 (658906) 69.0 kV to L8______-NI8 (659905) 69.0 kV Transmission Circuit #1 b.2. L7OC W MUNI8 (658906) 69.0 kV to L6OC E MUNI8 (658904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply Fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #1 b.2. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.2. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on K125DUNL-NI869.000 (659853) 69 kV Bus a. Apply Fault at the K125DUNL-NI869.000 (659853) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K125DUNL-NI8 (659853) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 b.2. K125DUNL-NI8 (659853) 69.0 kV to K126MEC -NI8 (659852) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply Fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. K335AMAI-NI8 (659854) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on K318MEC -NI869.000 (659855) 69 kV Bus a. Apply Fault at the K318MEC -NI869.000 (659855) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K318MEC -NI8 (659855) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 b.2. K318MEC -NI8 (659855) 69.0 kV to K308EARL-NI8 (659856) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply Fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. K307DENI-NI8 (659862) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on K313HALB-NI869.000 (659863) 69 kV Bus a. Apply Fault at the K313HALB-NI869.000 (659863) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K313HALB-NI8 (659863) 69.0 kV to K307DENI-NI8 (659862) 69.0 kV Transmission Circuit #1 b.2. K313HALB-NI8 (659863) 69.0 kV to K317MANN-NI8 (659906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply Fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. K306SCHL-NI8 (659885) 69.0 kV to K326OTTE-NI8 (659886) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on K228WSTB-NI869.000 (659896) 69 kV Bus a. Apply Fault at the K228WSTB-NI869.000 (659896) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K228WSTB-NI8 (659896) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 b.2. K228WSTB-NI8 (659896) 69.0 kV to L8______-NI8 (659905) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to EAGLE___-NI4 (659900) 230.0 kV Two Winding #2 b.2. EAGLE___-NI8 (659901) 69.0 kV to EAGLE___-NI4 (659900) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on L1______-NI869.000 (659902) 69 kV Bus a. Apply Fault at the L1______-NI869.000 (659902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L1______-NI8 (659902) 69.0 kV to K222HULL-NI8 (659941) 69.0 kV Transmission Circuit #1 b.2. L1______-NI8 (659902) 69.0 kV to K213HOSP-NI8 (659955) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on L3______-NI869.000 (659904) 69 kV Bus a. Apply Fault at the L3______-NI869.000 (659904) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L3______-NI8 (659904) 69.0 kV to K228WSTB-NI8 (659896) 69.0 kV Transmission Circuit #1 b.2. L3______-NI8 (659904) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on L8______-NI869.000 (659905) 69 kV Bus a. Apply Fault at the L8______-NI869.000 (659905) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L8______-NI8 (659905) 69.0 kV to L7OC W MUNI8 (658906) 69.0 kV Transmission Circuit #1 b.2. L8______-NI8 (659905) 69.0 kV to K228WSTB-NI8 (659896) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on J1CENTER-NI869.000 (659907) 69 kV Bus a. Apply Fault at the J1CENTER-NI869.000 (659907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. J1CENTER-NI8 (659907) 69.0 kV to K218ROCK-NI8 (659977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply Fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. J6BOYER_-NI8 (659912) 69.0 kV to K335AMAI-NI8 (659854) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on J12_____-NI869.000 (659918) 69 kV Bus a. Apply Fault at the J12_____-NI869.000 (659918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J12_____-NI8 (659918) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 b.2. J12_____-NI8 (659918) 69.0 kV to K125DUNL-NI8 (659853) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on J15_____-NI869.000 (659921) 69 kV Bus a. Apply Fault at the J15_____-NI869.000 (659921) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J15_____-NI8 (659921) 69.0 kV to L4SXCTNMUNI8 (658900) 69.0 kV Transmission Circuit #1 b.2. J15_____-NI8 (659921) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on K202PRES-NI869.000 (659944) 69 kV Bus a. Apply Fault at the K202PRES-NI869.000 (659944) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K202PRES-NI8 (659944) 69.0 kV to K226MERR-NI8 (659945) 69.0 kV Transmission Circuit #1 b.2. K202PRES-NI8 (659944) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on K214____-NI869.000 (659948) 69 kV Bus a. Apply Fault at the K214____-NI869.000 (659948) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K214____-NI8 (659948) 69.0 kV to K211SENY-NI8 (659949) 69.0 kV Transmission Circuit #1 b.2. K214____-NI8 (659948) 69.0 kV to K221ALTO-NI8 (659947) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 b.2. ORDWAY__-BE7 (659310) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply Fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EFORK_-BE334 (659600) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC7 (652404) 115.0 kV to DAWSONC4 (652403) 230.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 b.2. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to WILLISTON27 (652391) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.2. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.2. FTTHOM2-LNX3 (652807) 345.0 kV to FTTHOMP3 (652506) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply Fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY-LNX3 (652864) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply Fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.2. AV.LS-BD-BE3 (659420) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply Fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #1 b.2. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND-BE3 (659120) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply Fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.2. LO.LS-GR-BE3 (659422) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply Fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to GROTON__-BE3 (659160) 345.0 kV Transmission Circuit #z b.2. GR.LS-LO-BE3 (659423) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.2. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #1 b.2. CC.LS-LO-BE3 (659428) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on K213HOSP-NI869.000 (659955) 69 kV Bus a. Apply Fault at the K213HOSP-NI869.000 (659955) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K213HOSP-NI8 (659955) 69.0 kV to L1______-NI8 (659902) 69.0 kV Transmission Circuit #1 b.2. K213HOSP-NI8 (659955) 69.0 kV to HOSPERS8 (635371) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on K218ROCK-NI869.000 (659977) 69 kV Bus a. Apply Fault at the K218ROCK-NI869.000 (659977) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K218ROCK-NI8 (659977) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 b.2. K218ROCK-NI8 (659977) 69.0 kV to RKVALTT8 (635381) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE4 (659334) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. JUDSON__-BE4 (659334) 230.0 kV to JUDSON__-BE3 (659333) 345.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE7 (659187) 115.0 kV to GROTON__-BE3 (659160) 345.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 b.2. GROTON__-BE7 (659187) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on MANNINGTAP 869.000 (656267) 69 kV Bus a. Apply Fault at the MANNINGTAP 869.000 (656267) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANNINGTAP 8 (656267) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. MANNINGTAP 8 (656267) 69.0 kV to TEMPLTON8 (656247) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on DENSOUMAIN8 69.000 (658031) 69 kV Bus a. Apply Fault at the DENSOUMAIN8 69.000 (658031) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENSOUMAIN8 (658031) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 b.2. DENSOUMAIN8 (658031) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on OSBORN -MW7115.00 (655919) 115 kV Bus a. Apply Fault at the OSBORN -MW7115.00 (655919) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSBORN -MW7 (655919) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.2. OSBORN -MW7 (655919) 115.0 kV to E.NEWTWN-MW7 (655907) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on K338WTCT-NI869.000 (659897) 69 kV Bus a. Apply Fault at the K338WTCT-NI869.000 (659897) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K338WTCT-NI8 (659897) 69.0 kV to K335AMAI-NI8 (659854) 69.0 kV Transmission Circuit #1 b.2. K338WTCT-NI8 (659897) 69.0 kV to K318MEC -NI8 (659855) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on K308EARL-NI869.000 (659856) 69 kV Bus a. Apply Fault at the K308EARL-NI869.000 (659856) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K308EARL-NI8 (659856) 69.0 kV to K318MEC -NI8 (659855) 69.0 kV Transmission Circuit #1 b.2. K308EARL-NI8 (659856) 69.0 kV to K321MEC -NI8 (659857) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on K317MANN-NI869.000 (659906) 69 kV Bus a. Apply Fault at the K317MANN-NI869.000 (659906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K317MANN-NI8 (659906) 69.0 kV to K313HALB-NI8 (659863) 69.0 kV Transmission Circuit #1 b.2. K317MANN-NI8 (659906) 69.0 kV to K330MANM-NI8 (659864) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on K326OTTE-NI869.000 (659886) 69 kV Bus a. Apply Fault at the K326OTTE-NI869.000 (659886) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K326OTTE-NI8 (659886) 69.0 kV to K306SCHL-NI8 (659885) 69.0 kV Transmission Circuit #1 b.2. K326OTTE-NI8 (659886) 69.0 kV to K333SCHL-NI8 (659887) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on K217HWDN-NI869.000 (659942) 69 kV Bus a. Apply Fault at the K217HWDN-NI869.000 (659942) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K217HWDN-NI8 (659942) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 b.2. K217HWDN-NI8 (659942) 69.0 kV to L3______-NI8 (659904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on K222HULL-NI869.000 (659941) 69 kV Bus a. Apply Fault at the K222HULL-NI869.000 (659941) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K222HULL-NI8 (659941) 69.0 kV to L4SXCTNMUNI8 (658900) 69.0 kV Transmission Circuit #1 b.2. K222HULL-NI8 (659941) 69.0 kV to L1______-NI8 (659902) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on K207OC N-NI869.000 (659943) 69 kV Bus a. Apply Fault at the K207OC N-NI869.000 (659943) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K207OC N-NI8 (659943) 69.0 kV to L1______-NI8 (659902) 69.0 kV Transmission Circuit #1 b.2. K207OC N-NI8 (659943) 69.0 kV to L8______-NI8 (659905) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on K223SIOU-NI869.000 (659940) 69 kV Bus a. Apply Fault at the K223SIOU-NI869.000 (659940) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K223SIOU-NI8 (659940) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 b.2. K223SIOU-NI8 (659940) 69.0 kV to L5SXCTWMUNI8 (658902) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on K106CHAR-NI869.000 (659999) 69 kV Bus a. Apply Fault at the K106CHAR-NI869.000 (659999) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K106CHAR-NI8 (659999) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 b.2. K106CHAR-NI8 (659999) 69.0 kV to K105UTE_-NI8 (659998) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on K226MERR-NI869.000 (659945) 69 kV Bus a. Apply Fault at the K226MERR-NI869.000 (659945) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. K226MERR-NI8 (659945) 69.0 kV to K225ADAV-NI8 (659899) 69.0 kV Transmission Circuit #1 b.2. K226MERR-NI8 (659945) 69.0 kV to K202PRES-NI8 (659944) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #1 b.2. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to KILDEER7 (652419) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE4 (659337) 230.0 kV to TANDE___-BE3 (659336) 345.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 b.2. TANDE___-BE4 (659337) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on MONT -MW7 115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7 115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on GRENORA_-UM7 115.00 (659145) 115 kV Bus a. Apply Fault at the GRENORA_-UM7 115.00 (659145) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRENORA_-UM7 (659145) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply Fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on DENISON8 69.00 (652583) 69 kV Bus a. Apply Fault at the DENISON8 69.00 (652583) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON8 (652583) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on J6BOYER_-NI8 69.00 (659912) 69 kV Bus a. Apply Fault at the J6BOYER_-NI8 69.00 (659912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on EAGLE___-NI8 69.00 (659901) 69 kV Bus a. Apply Fault at the EAGLE___-NI8 69.00 (659901) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on J1CENTER-NI8 69.00 (659907) 69 kV Bus a. Apply Fault at the J1CENTER-NI8 69.00 (659907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1CENTER-NI8 (659907) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on L1______-NI8 69.00 (659902) 69 kV Bus a. Apply Fault at the L1______-NI8 69.00 (659902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L1______-NI8 (659902) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3 345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3 345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on MAPLE R3 345.00 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 345.00 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.4. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.3. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BROWNSV4 230.00 (620325) 230 kV Bus a. Apply Fault at the BROWNSV4 230.00 (620325) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 41.6 kV Transmission Circuit #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.2. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.5. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.6. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.7. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.8. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.11. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.12. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.14. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.15. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.19. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.20. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.21. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.23. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply Fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. RUGBY T (620179) 13.8 kV to RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. HRDLKCOL9 (620114) 34.5 kV to G380 RUGBY W (620115) 0.6 kV Two Winding #1 b.3. HRDLKCOL9 (620114) 34.5 kV to RGBYCOL9 (620168) 34.5 kV Transmission Circuit #1 b.4. RGBYWND4 (620368) 230.0 kV to RGBYCOL9 (620168) 34.5 kV Two Winding #1 b.5. RGBYWND4 (620368) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4230.00 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4230.00 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.3. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.4. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.5. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.7. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply Fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on ASTORIA 3 345.00 (620483) 345 kV Bus a. Apply Fault at the ASTORIA 3 345.00 (620483) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASTORIA 3 (620483) 345.0 kV to BRKNGCO3 (601031) 345.0 kV Transmission Circuit #1 b.2. ASTORIA 3 (620483) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on BDV 4230.00 (672603) 230 kV Bus a. Apply Fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to CSLTNET7 (620180) 115.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_UMZ_FAULT_001 | Single Phase Fault with Stuck Breaker on AVS 345 (659420) 345 kV Bus a. Apply Fault at the AVS 345 (659420) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to remove bus #1 b.2. COTEAU_1-RR8 (659222) 69.0 kV to Load #BB b.3. COTEAU_1-RR8 (659222) 69.0 kV to Load #BW b.4. DGC UREA-BE8 (659236) 69.0 kV to Load #BG b.5. COTEAU 1-RR9 (659219) 13.8 kV to remove bus # b.6. COTEAU 2-RR9 (659231) 13.8 kV to remove bus # b.7. COTEAU_1-RR8 (659222) 69.0 kV to remove bus # b.8. COTEAU__-RR3 (659218) 345.0 kV to remove bus # b.9. DGC UREA-BE8 (659236) 69.0 kV to remove bus # b.10. AV.LS-BD-BE3 (659420) 345.0 kV to remove bus # b.11. AV.LS-BD-BE3 (659420) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_UMZ_FAULT_002 | Single Phase Fault with Stuck Breaker on LOS 345 (659424) 345 kV Bus a. Apply Fault at the LOS 345 (659424) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #Z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to Switched Shunt Device # b.3. CC.LS-LO-BE3 (659428) 345.0 kV to Switched Shunt Device # b.4. LELAND_2-BEG (659111) 20.0 kV to Load #S0 b.5. LELAND_2-BEG (659111) 20.0 kV to Generator #2 b.6. LELAND_2-BEG (659111) 20.0 kV to remove bus # b.7. CC.LS-LO-BE3 (659428) 345.0 kV to remove bus # b.8. LO.LS-FT-BE3 (659424) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_UMZ_FAULT_003 | Single Phase Fault with Stuck Breaker on LOS 345 (659422) 345 kV Bus a. Apply Fault at the LOS 345 (659422) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to GROTON__-BE3 (659160) 345.0 kV Transmission Circuit #Z b.2. GR.LS-LO-BE3 (659423) 345.0 kV to Switched Shunt Device # b.3. LO.LS-GR-BE3 (659422) 345.0 kV to Switched Shunt Device # b.4. LO.KU1A_-BE9 (659201) 13.8 kV to Switched Shunt Device # b.5. LO.LS-GR-BE3 (659422) 345.0 kV to remove bus # b.6. GR.LS-LO-BE3 (659423) 345.0 kV to remove bus # b.7. LO.KU1A_-BE9 (659201) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_UMZ_FAULT_004 | Single Phase Fault with Stuck Breaker on LOS 230 (659106) 230 kV Bus a. Apply Fault at the LOS 230 (659106) 230 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to Load #BB b.3. BASIN___-BE7 (659109) 115.0 kV to Load #BW b.4. BASIN___-BE7 (659109) 115.0 kV to Load #W0 b.5. LELAND_1-BEG (659110) 22.0 kV to Load #S0 b.6. LELAND_1-BEG (659110) 22.0 kV to Generator #1 b.7. NEWSALEM-MG7 (655748) 115.0 kV to Load #BB b.8. NEWSALEM-MG7 (655748) 115.0 kV to Load #BW b.9. ROUGHRDR-MG7 (655750) 115.0 kV to Load #BB b.10. ROUGHRDR-MG7 (655750) 115.0 kV to Load #BW b.11. NRWSTMDN-MG7 (655751) 115.0 kV to Load #BB b.12. NRWSTMDN-MG7 (655751) 115.0 kV to Load #BW b.13. DEVAUL -MG8 (655746) 69.0 kV to Load #W0 b.14. CANNON -MG8 (655740) 69.0 kV to Load #BB b.15. CANNON -MG8 (655740) 69.0 kV to Load #BW b.16. CEDAR -MG8 (655741) 69.0 kV to Load #BB b.17. CEDAR -MG8 (655741) 69.0 kV to Load #BW b.18. GRANT -MG8 (655742) 69.0 kV to Load #BB b.19. GRANT -MG8 (655742) 69.0 kV to Load #BW b.20. FLASHER -MG8 (655732) 69.0 kV to Load #BB b.21. FLASHER -MG8 (655732) 69.0 kV to Load #BW b.22. LO.KU1A_-BE9 (659201) 13.8 kV to remove bus # b.23. LO.KVA2_-BE9 (659202) 13.8 kV to remove bus # b.24. BAL.KY1A-BE9 (659200) 13.8 kV to remove bus # b.25. LELAND_O-BE4 (659106) 230.0 kV to remove bus # b.26. BASIN___-BE7 (659109) 115.0 kV to remove bus # b.27. BASIN___-BE4 (659199) 230.0 kV to remove bus # b.28. LELAND_1-BEG (659110) 22.0 kV to remove bus # b.30. NEWSALEM-MG7 (655748) 115.0 kV to remove bus # b.31. MANSWTCH-MG7 (655749) 115.0 kV to remove bus # b.32. ROUGHRDR-MG7 (655750) 115.0 kV to remove bus # b.33. NRWSTMDN-MG7 (655751) 115.0 kV to remove bus # b.34. NWMDNTAP-MG7 (655752) 115.0 kV to remove bus # b.35. DEVAUL -MG8 (655746) 69.0 kV to remove bus # b.36. DEVALTP -MG8 (655744) 69.0 kV to remove bus # b.37. DEVAUL 8 (652257) 69.0 kV to remove bus # b.38. LARK -MG8 (655731) 69.0 kV to remove bus # b.39. CANNON -MG8 (655740) 69.0 kV to remove bus # b.40. CEDAR -MG8 (655741) 69.0 kV to remove bus # b.41. GRANT -MG8 (655742) 69.0 kV to remove bus # b.42. FLASHER -MG8 (655732) 69.0 kV to remove bus # b.44. DEVAUL -MG7 (655747) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_UMZ_FAULT_005 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_UMZ_FAULT_006 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_UMZ_FAULT_007 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 b.2. CCR.KV4A-BE9 (659319) 13.8 kV to remove bus # b.3. CCR.KV3A-BE9 (659318) 13.8 kV to remove bus # b.4. CHARL_CK-BE4 (659302) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP1_P4_UMZ_FAULT_008 | Single Phase Fault with Stuck Breaker on JDS 345 (659333) 345 kV Bus a. Apply Fault at the JDS 345 (659333) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to remove bus # b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_131 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from PS_RCP.B-BEG (659432 and 659431). Disabling the dynamic controller model allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_159 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_160 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_163 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_164 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_165 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_LOCAL_FAULT_177 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_131 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from PS_RCP.B-BEG (659432 and 659431). Disabling the dynamic controller model allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_159 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_160 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_163 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_164 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_165 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_LOCAL_FAULT_177 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
01 NORTH | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to oscillations from ASH3GEN9 (657737), ASH1GEN9 (657985) and ASH2GEN9 (657964). Disabling their dynamic controllers allows the simulation to reach the end without any stability issues being observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_001 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_002 | 3 Phase fault on W LINCOLN 7 115.00 (650208) 115 kV Bus a. Apply fault at the W LINCOLN 7 115.00 (650208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_003 | 3 Phase fault on NW70FAIRFD7 115.00 (650210) 115 kV Bus a. Apply fault at the NW70FAIRFD7 115.00 (650210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_004 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_005 | 3 Phase fault on 8&N 7 115.00 (650217) 115 kV Bus a. Apply fault at the 8&N 7 115.00 (650217) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_006 | 3 Phase fault on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.3. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_007 | 3 Phase fault on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_008 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_009 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_010 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_011 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_012 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_013 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_014 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_015 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_016 | 3 Phase fault on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.2. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_017 | 3 Phase fault on 93&O 7 115.00 (650273) 115 kV Bus a. Apply fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_018 | 3 Phase fault on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_019 | 3 Phase fault on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_020 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_021 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_022 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_023 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_024 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_025 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_026 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_027 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_028 | 3 Phase fault on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAVINS 7 (652511) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_029 | 3 Phase fault on COOPER1G 22.000 (640009) 22 kV Bus a. Apply fault at the COOPER1G 22.000 (640009) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER1G (640009) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_030 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_031 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_032 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_033 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_034 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_035 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_036 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_039 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_040 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_041 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_042 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_043 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_044 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_045 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_046 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_047 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_048 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_049 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_050 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_051 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_052 | 3 Phase fault on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_053 | 3 Phase fault on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.2. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_054 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_055 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_056 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_057 | 3 Phase fault on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_058 | 3 Phase fault on 40&BENNET 7 115.00 (650247) 115 kV Bus a. Apply fault at the 40&BENNET 7 115.00 (650247) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_059 | 3 Phase fault on NW56&MORTN7 115.00 (650207) 115 kV Bus a. Apply fault at the NW56&MORTN7 115.00 (650207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW70FAIRFD7 (650210) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_060 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.6. 2&N 7 (650230) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_061 | 3 Phase fault on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.2. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.6. 40&ROKEBY 7 (650250) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_062 | 3 Phase fault on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.6. 70&CALVERT7 (650270) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_063 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_064 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_065 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_066 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_067 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power Oscillations are oberserved at the Grand Prairie Wind Farm (645065, 645066, 645067 and 645068) following the fault and the units are tripped due to internal protection before reaching the 10 second post-fault time mark. The issue is resolved when the critical clearing time is reduced to 3 cycles. The issue is also observed in the PQ case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_068 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_069 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_070 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_071 | 3 Phase fault on SUB-H G 115.00 (642066) 115 kV Bus a. Apply fault at the SUB-H G 115.00 (642066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-H G (642066) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_072 | 3 Phase fault on SUB-C 7 115.00 (642070) 115 kV Bus a. Apply fault at the SUB-C 7 115.00 (642070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-C 7 (642070) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_073 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_074 | 3 Phase fault on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_075 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_076 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.2. STOCKVL7 (640365) 115.0 kV to STOCKVL8 (640366) 69.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 b.4. STOCKVLLET19 (643146) 13.8 kV to STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_077 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_078 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_079 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_080 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_081 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_082 | 3 Phase fault on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to FAIRBRYG (640170) 34.5 kV to FAIRBURY T19 (643056) 13.8 kV Three Winding #1 b.4. FAIRBURY T19 (643056) 13.8 kV to FAIRBRYG (640170) 34.5 kV to FAIRBRY7 (640169) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_083 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_084 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_085 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_086 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_087 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_088 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_089 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_090 | 3 Phase fault on WINSLOW7 115.00 (640409) 115 kV Bus a. Apply fault at the WINSLOW7 115.00 (640409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_091 | 3 Phase fault on STANTON7 115.00 (640357) 115 kV Bus a. Apply fault at the STANTON7 115.00 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_092 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_093 | 3 Phase fault on PETRSBG7 115.00 (640318) 115 kV Bus a. Apply fault at the PETRSBG7 115.00 (640318) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_094 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_095 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_096 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_097 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_098 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. COLMBS19 (640135) 13.2 kV to KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_099 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_100 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_101 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_102 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_103 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_104 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_105 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_106 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_107 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_108 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_109 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_110 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_111 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_112 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_113 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_114 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_115 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_116 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_117 | 3 Phase fault on HASTING4 230.00 (640214) 230 kV Bus a. Apply fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_118 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_119 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_120 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_121 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_122 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_123 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_124 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_125 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_126 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_127 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 b.2. STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_128 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_129 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_130 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_131 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_132 | 3 Phase fault on CREITON8 69.000 (640150) 69 kV Bus a. Apply fault at the CREITON8 69.000 (640150) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_133 | 3 Phase fault on GENOA 7 115.00 (640181) 115 kV Bus a. Apply fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENOA 7 (640181) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_134 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_135 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_136 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_137 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_138 | 3 Phase fault on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_139 | 3 Phase fault on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHUYLR7 (640336) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_140 | 3 Phase fault on SILVRCK8 69.000 (640346) 69 kV Bus a. Apply fault at the SILVRCK8 69.000 (640346) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_141 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_142 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_143 | 3 Phase fault on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETERSBRG.N7 (640444) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_144 | 3 Phase fault on COOPER 869.000 (640446) 69 kV Bus a. Apply fault at the COOPER 869.000 (640446) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_145 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_146 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_147 | 3 Phase fault on HOSKINS4 230.00 (640227) 345 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_148 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_149 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_150 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_151 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_152 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_153 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_154 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_155 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_156 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_157 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_158 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_159 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_160 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_161 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_162 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_163 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_164 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_165 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_166 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_167 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_168 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_169 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_170 | 3 Phase fault on S1398 5 161.00 (646398) 161 kV Bus a. Apply fault at the S1398 5 161.00 (646398) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_171 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_172 | 3 Phase fault on NCU903 8 69.000 (647401) 69 kV Bus a. Apply fault at the NCU903 8 69.000 (647401) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCU903 8 (647401) 69.0 kV to S962 8 (647962) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_173 | 3 Phase fault on S977 8 69.000 (647977) 69 kV Bus a. Apply fault at the S977 8 69.000 (647977) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCU903 8 (647401) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.2. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_174 | 3 Phase fault on S965 8 69.000 (647965) 69 kV Bus a. Apply fault at the S965 8 69.000 (647965) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_175 | 3 Phase fault on S967 8 69.000 (647967) 69 kV Bus a. Apply fault at the S967 8 69.000 (647967) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_176 | 3 Phase fault on S969 8 69.000 (647969) 69 kV Bus a. Apply fault at the S969 8 69.000 (647969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.2. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.3. S968 8 (647968) 69.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_177 | 3 Phase fault on S973 8 69.000 (647973) 69 kV Bus a. Apply fault at the S973 8 69.000 (647973) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.2. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_178 | 3 Phase fault on FREM D 8 69.000 (647424) 69 kV Bus a. Apply fault at the FREM D 8 69.000 (647424) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM D 8 (647424) 69.0 kV to FREM E 8 (647425) 69.0 kV Transmission Circuit #1 b.2. FREM D 8 (647424) 69.0 kV to S976 8 (647976) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_179 | 3 Phase fault on HYDCAP 8 69.000 (647102) 69 kV Bus a. Apply fault at the HYDCAP 8 69.000 (647102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_180 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_181 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_182 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_183 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_184 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_185 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_186 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_187 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_188 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_189 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_190 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_191 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_192 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_193 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-LR-MB3 (659426) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_194 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV Switched Shunt Device #//1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_195 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_196 | 3 Phase fault on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAVINS 7 (652511) 115.0 kV to SPIRIT_M-BE7 (659121) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_197 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_198 | 3 Phase fault on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_199 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_200 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_201 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_202 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_203 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_204 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_205 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_206 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_207 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_208 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_209 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_210 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_211 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_212 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_213 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_214 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_215 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_216 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_217 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_218 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_219 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_220 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_221 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_222 | 3 Phase fault on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_223 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_224 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_225 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_226 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_227 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_228 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_229 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_230 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_231 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_232 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_233 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_234 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_235 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_236 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_237 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_238 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_239 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_240 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_241 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_242 | 3 Phase fault on BEAT. S7 115.00 (640074) 115 kV Bus a. Apply fault at the BEAT. S7 115.00 (640074) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_243 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_244 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_245 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_246 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_247 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_248 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_249 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_250 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_251 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_252 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_253 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_254 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_255 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_256 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_257 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_258 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_259 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_260 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_261 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_262 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_263 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_264 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_265 | 3 Phase fault on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_266 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_267 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_268 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_269 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_270 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_271 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_272 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_273 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_274 | 3 Phase fault on COOPER_ESST869.000 (640141) 69 kV Bus a. Apply fault at the COOPER_ESST869.000 (640141) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_ESST8 (640141) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_275 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_276 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_277 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_278 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_279 | 3 Phase fault on FRIEND 7 115.00 (640174) 115 kV Bus a. Apply fault at the FRIEND 7 115.00 (640174) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_280 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_281 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_282 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_283 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_284 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_285 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_286 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_287 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_288 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_289 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_290 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_291 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_292 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_293 | 3 Phase fault on HARBINE7 115.00 (640208) 115 kV Bus a. Apply fault at the HARBINE7 115.00 (640208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_294 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_295 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_296 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_297 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_298 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_299 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_300 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_301 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_302 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_303 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_304 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_305 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_306 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_307 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_308 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_309 | 3 Phase fault on MALONEY7 115.00 (640265) 115 kV Bus a. Apply fault at the MALONEY7 115.00 (640265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_310 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_311 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_312 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_313 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_314 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_315 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_316 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_317 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_318 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_319 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Post fault steady state voltages at STERLNG7 (640362), FIRTH 7 (640171), GEN-2013-019 (583700), GEN-2019-041 (763725), G13-002-TAP (560746), and MONOLITH 7 (640591) do not recover above 0.9 p.u. No CQ units meet the PTDF criteria to be contingent on the upgrade. Issue also observed in the base case. Stable response observed after the upgrade is in-service. | Multi - Sheldon - Monolith 115 kV
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_320 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_321 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_322 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_323 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_324 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_325 | 3 Phase fault on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_326 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_327 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_328 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_329 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_330 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_331 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_332 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_333 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_334 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_335 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_336 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_337 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_338 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_339 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_340 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 3 (640520) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_341 | 3 Phase fault on BOBCAT.C 3345.00 (640529) 345 kV Bus a. Apply fault at the BOBCAT.C 3345.00 (640529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT.C 3 (640529) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_342 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_343 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_344 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_345 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_346 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | The Laramie generating site (659118) loses synchronism after the fault. The issue is resolved when the critical clearing time is reduced to 5 cycles. The issue is also observed in the PQ case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_347 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_348 | 3 Phase fault on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_349 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_350 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_351 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_352 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR8 (640073) 69.0 kV to BATTLCR7 (640072) 115.0 kV to BATTLECRKT19 (643011) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_353 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_354 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_355 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_356 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 8 (640085) 69.0 kV to BLMFLD 7 (640084) 115.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_357 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_358 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_359 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_360 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 8 (640273) 69.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_361 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT8 (640288) 69.0 kV to N.PLATT7 (640287) 115.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_362 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_363 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_364 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_365 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT19 (643137) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_366 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT29 (643138) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_367 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 8 (640360) 69.0 kV to STAPLETON 7 (640359) 115.0 kV to STAPLETONT19 (643175) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_368 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY8 (640417) 69.0 kV to RISNGCY7 (640328) 115.0 kV to RISINGCTYT29 (643127) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_369 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 8 (640443) 69.0 kV to YORK 7 (640411) 115.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_370 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_371 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_372 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAMORA 8 (640468) 69.0 kV to TAMORA 7 (640375) 115.0 kV to TAMORA T2 9 (643181) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_373 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_374 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_375 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_376 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S966 8 (647966) 69.0 kV to STEINER7 (640361) 115.0 kV to STEINER T1 9 (643143) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_377 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_378 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_379 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_380 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_381 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_001 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_002 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_004 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_005 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_006 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_007 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_008 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_009 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_010 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_011 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_012 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_015 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_017 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_018 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_020 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_021 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_022 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_023 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_024 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_025 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_026 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_027 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_028 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_029 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_030 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_031 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_032 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_033 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_036 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_037 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_041 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_042 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_043 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_044 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_045 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_046 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_047 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_048 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_049 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_051 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on MADISON3 345.00 (635635) 345 kV Bus a. Apply Fault at the MADISON3 345.00 (635635) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORIENT 3 (635570) 345.0 kV to MADISON3 (635635) 345.0 kV Transmission Circuit #1 b.2. BOONVIL3 (635630) 345.0 kV to MADISON3 (635635) 345.0 kV Transmission Circuit #1 b.3. MADISON3 (635635) 345.0 kV to NORWLK3 (635640) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.2. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply Fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 b.2. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on SALIX 5 161.00 (635235) 161 kV Bus a. Apply Fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.3. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on MONONA 5 161.00 (635300) 161 kV Bus a. Apply Fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.4. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.4. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply Fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 b.2. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.3. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.4. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.7. S1366 5 (646366) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. HOSK.T89 (640230) 34.5 kV to HOSKINS4 (640227) 230.0 kV Two Winding #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply Fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.3. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT19 (643039) 13.8 kV Three Winding #1 b.4. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT29 (643040) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.3. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.4. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.5. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.3. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.4. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.4. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.5. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T1 9 (643004) 13.8 kV Three Winding #1 b.6. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T2 9 (643005) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.4. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.4. BELDEN 7 (640080) 115.0 kV to BELDEN 8 (640081) 69.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 b.2. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 b.4. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CENCITY7 115.00 (640107) 115 kV Bus a. Apply Fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.3. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT19 (643032) 13.8 kV Three Winding #1 b.4. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT29 (643033) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply Fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 b.2. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.3. CREITON7 (640149) 115.0 kV to CREITON8 (640150) 69.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on CRESTON7 115.00 (640151) 115 kV Bus a. Apply Fault at the CRESTON7 115.00 (640151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.2. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.3. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T1 9 (643046) 4.2 kV Three Winding #1 b.4. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T2 9 (643047) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on CRETE__7 115.00 (640153) 115 kV Bus a. Apply Fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.3. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T1 9 (643048) 13.8 kV Three Winding #1 b.4. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T2 9 (643049) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FREMONT7 115.00 (640173) 115 kV Bus a. Apply Fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.3. FREMONT7 (640173) 115.0 kV to S976 8 (647976) 69.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 b.4. FREMONT7 (640173) 115.0 kV to S976 8 (647976) 69.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply Fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.2. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.3. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.4. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 b.5. GENEVA 7 (640178) 115.0 kV to GENEVA 8 (640179) 69.0 kV to GENEVA T2 9 (643062) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T1 9 (643064) 13.8 kV Three Winding #1 b.4. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T2 9 (643065) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HARBINE7 115.00 (640208) 115 kV Bus a. Apply Fault at the HARBINE7 115.00 (640208) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.3. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to KINGSLY7 (640255) 115.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.3. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to MCCOOK G (640017) 13.8 kV Two Winding #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.4. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.5. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 b.6. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply Fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.4. MCCOOL 7 (640272) 115.0 kV to MCCOOL 8 (640273) 69.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on MINDEN 7 115.00 (640275) 115 kV Bus a. Apply Fault at the MINDEN 7 115.00 (640275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. MINDEN 7 (640275) 115.0 kV to MINDEN 9 (640276) 34.5 kV to MINDEN T1 9 (643102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.3. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.4. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.5. NELIGH 7 (640293) 115.0 kV to NELIGH 8 (640294) 69.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 b.6. NELIGH 7 (640293) 115.0 kV to NELIGH 9 (640295) 34.5 kV to NELIGH T1 9 (643109) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T1 9 (643112) 13.8 kV Three Winding #1 b.5. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T2 9 (643113) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply Fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT19 (643110) 13.8 kV Three Winding #1 b.5. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT29 (643111) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.4. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.5. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply Fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.3. RISNGCY7 (640328) 115.0 kV to RISNGCY9 (640329) 34.5 kV to RISINGCTYT19 (643126) 13.8 kV Three Winding #1 b.4. RISNGCY7 (640328) 115.0 kV to RISNGCY8 (640417) 69.0 kV to RISINGCTYT29 (643127) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply Fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.3. SCHUYLR7 (640336) 115.0 kV to SCHUYLR9 (640337) 34.5 kV to SCHUYLER T19 (643131) 13.8 kV Three Winding #1 b.4. SCHUYLR7 (640336) 115.0 kV to SCHUYLR9 (640337) 34.5 kV to SCHUYLER T29 (643132) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SEWARD 7 115.00 (640340) 115 kV Bus a. Apply Fault at the SEWARD 7 115.00 (640340) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.3. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 b.4. SEWARD 7 (640340) 115.0 kV to SEWARD 9 (640341) 34.5 kV to SEWARD T1 9 (643134) 13.8 kV Three Winding #1 b.5. SEWARD 7 (640340) 115.0 kV to SEWARD 9 (640341) 34.5 kV to SEWARD T2 9 (643135) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply Fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.2. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.3. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T19 (643139) 13.8 kV Three Winding #1 b.4. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T29 (643169) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on STNTN.N7 115.00 (640363) 115 kV Bus a. Apply Fault at the STNTN.N7 115.00 (640363) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. STNTN.N7 (640363) 115.0 kV to STNTN.N9 (640364) 34.5 kV to STANTN.N T19 (643145) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.2. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.3. THEDFRD7 (640381) 115.0 kV to THEDFRD9 (640382) 34.5 kV to THEDFORD T19 (643153) 13.8 kV Three Winding #1 b.4. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WAHOO 7 115.00 (640402) 115 kV Bus a. Apply Fault at the WAHOO 7 115.00 (640402) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAVEY 7 (640155) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 b.3. WAHOO 29 (648402) 13.8 kV to WAHOO 7 (640402) 115.0 kV Two Winding #1 b.4. WAHOO 7 (640402) 115.0 kV to WAHOO G (640403) 34.5 kV to WAHOO T1 9 (643163) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on YORK 7 115.00 (640411) 115 kV Bus a. Apply Fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.3. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.4. YORK 7 (640411) 115.0 kV to YORK 9 (640412) 34.5 kV to YORK T1 9 (643166) 13.8 kV Three Winding #1 b.5. YORK 7 (640411) 115.0 kV to YORK 8 (640443) 69.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on YORK SW7 115.00 (640413) 115 kV Bus a. Apply Fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.2. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. YORK SW7 (640413) 115.0 kV to YORK SW9 (640414) 34.5 kV to YORK.SW T1 9 (643168) 13.8 kV Three Winding #1 b.4. YORK SW7 (640413) 115.0 kV to YORK.SW T2 8 (640447) 69.0 kV to YORK.SW T2 9 (643176) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.2. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to Load #NW b.2. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.3. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.4. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to Load #NW b.2. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.3. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.4. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS9 (640137) 34.5 kV to Load #N0 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.5. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T69 (643042) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply Fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. E.COL. 4 (640126) 230.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.4. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT19 (643037) 13.8 kV Three Winding #1 b.5. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT29 (643038) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.3. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.5. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS9 (640229) 34.5 kV to Load #N2 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS9 (640229) 34.5 kV to Load #N2 b.2. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.4. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEARNEY9 (640251) 34.5 kV to Load #N0 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 b.8. KEARNEY7 (640250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.3. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 b.5. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to NORTHPLT T79 (643107) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply Fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.2. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z b.3. OGALALA9 (640303) 34.5 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T29 (643116) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 b.2. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on STEELEC7 115.00 (640426) 115 kV Bus a. Apply Fault at the STEELEC7 115.00 (640426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.2. STEELEC9 (640427) 4.2 kV to STEELEC7 (640426) 115.0 kV Two Winding #1 b.3. STEELEC7 (640426) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.2. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.3. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.4. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.6. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 b.7. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply Fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.3. ELKRDG.PLT D (640419) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.4. CROFTN.PLT D (640423) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.5. BLMFLD 7 (640084) 115.0 kV to BLMFLD 8 (640085) 69.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS9 (640137) 34.5 kV to Load #N0 b.2. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. COLMBUS7 (640136) 115.0 kV to COLMBS1G (640006) 13.8 kV Two Winding #1 b.4. COLMBUS7 (640136) 115.0 kV to COLMBS2G (640007) 13.8 kV Two Winding #1 b.5. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.6. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.7. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.8. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.9. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.12. COLMBUS7 (640136) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.5. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.6. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.7. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.8. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T69 (643042) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on COL.COG7 115.00 (640119) 115 kV Bus a. Apply Fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #1 b.2. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply Fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.4. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 b.5. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.6. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT19 (643037) 13.8 kV Three Winding #1 b.7. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT29 (643038) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.4. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.5. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.6. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.7. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.8. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG9 (640225) 34.5 kV to Load #N0 b.2. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.3. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.5. HOLDREG7 (640224) 115.0 kV to HOLDREGE 8 (640448) 69.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 b.10. HOLDREG7 (640224) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.8. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.6. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 b.3. LAREDO.PLT 9 (640433) 34.5 kV to PETERSBRG.N7 (640444) 115.0 kV Two Winding #1 b.4. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on STEELEC7 115.00 (640426) 115 kV Bus a. Apply Fault at the STEELEC7 115.00 (640426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOB HL3 (533332) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.2. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.3. STEELEC7 (640426) 115.0 kV to S.FLATS.PLT7 (640558) 115.0 kV Transmission Circuit #1 b.4. STEELEC9 (640427) 4.2 kV to STEELEC7 (640426) 115.0 kV Two Winding #1 b.5. STEELEC_KXL9 (640440) 6.9 kV to STEELEC7 (640426) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.3. N.PLATTG (640018) 13.8 kV to N.PLATT9 (640289) 34.5 kV to N.PLATT7 (640287) 115.0 kV Three Winding #1 b.4. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 b.6. N.PLATT7 (640287) 115.0 kV to N.PLATT8 (640288) 69.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 b.7. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to N.PLATTG (640018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.2. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.6. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on FLTWTR1W 0.6900 (645061) 0.689999998 kV Bus a. Apply Fault at the FLTWTR1W 0.6900 (645061) 0.689999998 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. S1399 5 (646399) 161.0 kV to FLTWTRX9 (648500) 34.5 kV to FLTWTRY9 (648501) 13.8 kV Three Winding #1 b.6. FLTWTR1W (645061) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on KELLY 5 161.00 (532913) 161 kV Bus a. Apply Fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.4. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to HUMBOLT7 (640235) 115.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.3. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to HUMBOLT7 (640235) 115.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on S1258 5 161.00 (646258) 161 kV Bus a. Apply Fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on S1258 5 161.00 (646258) 161 kV Bus a. Apply Fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.4. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.5. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply Fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 b.2. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.3. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.4. GRANTNB_-TS7 (659800) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.5. OGALALA_-TS7 (659801) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.6. OGALALA_-TS7 (659801) 115.0 kV to MCONGHY_-TS7 (659824) 115.0 kV Transmission Circuit #1 b.7. ELSIETP_-TS7 (659807) 115.0 kV to PAXTON__-TS7 (659808) 115.0 kV Transmission Circuit #1 b.8. ELSIETP_-TS7 (659807) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.9. ELSIETP_-TS7 (659807) 115.0 kV to ELSIE___-TS7 (659822) 115.0 kV Transmission Circuit #1 b.10. MCONGHY_-TS7 (659824) 115.0 kV to ARTHUR__-TS7 (659825) 115.0 kV Transmission Circuit #1 b.11. BRULE 7 (640091) 115.0 kV to BRULE 9 (640092) 34.5 kV to BRULE T1 9 (643025) 13.8 kV Three Winding #1 b.12. OGALALA9 (640303) 34.5 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T29 (643116) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply Fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply Fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on 8&N 7 115.00 (650217) 115 kV Bus a. Apply Fault at the 8&N 7 115.00 (650217) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8&J 9 (650100) 34.5 kV to 171TERTIARY (650517) 34.5 kV Transmission Circuit #1 b.2. 8&N 7 (650217) 115.0 kV to 17&HOLDRGE7 (650219) 115.0 kV Transmission Circuit #1 b.3. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. 8&N 7 (650217) 115.0 kV to 8&N A9 (650317) 13.2 kV to 171TERTIARY (650517) 34.5 kV Three Winding #1 b.5. 8&N 7 (650217) 115.0 kV to 8&N B9 (650417) 13.2 kV to 172TERTIARY (650617) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply Fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.4. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply Fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.3. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.4. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply Fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.3. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply Fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&Q 7 (650260) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply Fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 30&A 7 (650252) 115.0 kV to 56&EVERETT7 (650256) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on 40&GERTIE 7 115.00 (650258) 115 kV Bus a. Apply Fault at the 40&GERTIE 7 115.00 (650258) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.5. 40&GERTIE 7 (650258) 115.0 kV to 40&GE A9 (650358) 13.2 kV to 581TERTIARY (650558) 7.2 kV Three Winding #1 b.6. 40&GERTIE 7 (650258) 115.0 kV to 40&GE B9 (650458) 13.2 kV to 582TERTIARY (650658) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply Fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.2. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.4. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.5. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.6. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.9. 70&CALVERT7 (650270) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.4. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.5. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.6. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 b.11. 70&CALVERT7 (650270) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 2G (650092) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 3G (650093) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 2G (650092) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 1G (650091) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.8. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.9. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply Fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.3. 27&PLR 7 (650229) 115.0 kV to 27&PLR A9 (650329) 12.5 kV to 291TERTIARY (650529) 7.2 kV Three Winding #1 b.4. 27&PLR 7 (650229) 115.0 kV to 27&PLR B9 (650429) 12.5 kV to 292TERTIARY (650629) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.2. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.5. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.6. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on 40&BENNET 7 115.00 (650247) 115 kV Bus a. Apply Fault at the 40&BENNET 7 115.00 (650247) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on 56&PLR 7 115.00 (650255) 115 kV Bus a. Apply Fault at the 56&PLR 7 115.00 (650255) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on NW12&ARBOR7 115.00 (650226) 115 kV Bus a. Apply Fault at the NW12&ARBOR7 115.00 (650226) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW70FAIRFD7 (650210) 115.0 kV Transmission Circuit #1 b.2. NW56&MORTN7 (650207) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.3. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.4. 19&ALVO 7 (650215) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.5. NW70FAIRFD7 (650210) 115.0 kV to NW70FAIRFD9 (650310) 12.5 kV to 101TERTIARY (650510) 7.2 kV Three Winding #1 b.6. NW12&ARBOR7 (650226) 115.0 kV to NW12&AR 9 (650326) 12.5 kV to 261TERTIARY (650526) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on NW5&BENTON7 115.00 (650212) 115 kV Bus a. Apply Fault at the NW5&BENTON7 115.00 (650212) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4&MORTON 7 (650205) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.2. W LINCOLN 7 (650208) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.3. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. W LINCOLN 7 (650208) 115.0 kV to WLINCOLN 9 (650308) 13.2 kV to 084TERTIARY (650508) 7.2 kV Three Winding #1 b.5. NW5&BENTON7 (650212) 115.0 kV to NW5BENTN 9 (650312) 12.5 kV to 121TERTIARY (650512) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.5. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.7. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.7. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.7. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.7. 40&ROKEBY 7 (650250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.4. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.7. 70&CALVERT7 (650270) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.2. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.7. 40&ROKEBY 7 (650250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.2. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.7. 40&ROKEBY 7 (650250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLM1G (640010) 23.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 8 (640446) 69.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. NCU903 8 (647401) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.4. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER_602 8 (640143) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #z1 b.2. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on S967 8 69.000 (647967) 69 kV Bus a. Apply Fault at the S967 8 69.000 (647967) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.2. TECUMSH8 (647400) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.3. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on S968 8 69.000 (647968) 69 kV Bus a. Apply Fault at the S968 8 69.000 (647968) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECUMSH8 (647400) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.2. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.3. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.4. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on HYDCAP 8 69.000 (647102) 69 kV Bus a. Apply Fault at the HYDCAP 8 69.000 (647102) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.4. NC SYRA8 (647402) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.5. NC SYRA8 (647402) 69.0 kV to S971 8 (647971) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on S974 8 69.000 (647974) 69 kV Bus a. Apply Fault at the S974 8 69.000 (647974) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.2. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.3. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.4. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.5. S968 8 (647968) 69.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on STERLNG7 115.00 (640362) 115 kV Bus a. Apply Fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.4. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.5. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.2. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.3. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 b.5. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on S993 8 69.000 (647993) 69 kV Bus a. Apply Fault at the S993 8 69.000 (647993) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.5. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.6. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.7. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on AUBRNT 8 69.000 (647101) 69 kV Bus a. Apply Fault at the AUBRNT 8 69.000 (647101) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.8. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.4. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.5. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.7. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z b.3. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.4. SIDNEY__-MB9 (659168) 13.8 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Three Winding #1 b.5. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.2. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.3. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 b.4. SIDNEY__-MB9 (659168) 13.8 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Three Winding #1 b.5. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 b.2. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on EAST 5 161.00 (541254) 161 kV Bus a. Apply Fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST 5 (541254) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 b.2. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on IND PRK5 161.00 (541256) 161 kV Bus a. Apply Fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 b.2. IND PRK5 (541256) 161.0 kV to LAKE RD5 (541255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on G13-002-TAP 115.00 (560746) 115 kV Bus a. Apply Fault at the G13-002-TAP 115.00 (560746) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G13-002-TAP (560746) 115.0 kV to GEN-2013-019 (583700) 115.0 kV Transmission Circuit #1 b.2. G13-002-TAP (560746) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply Fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-023 (584650) 345.0 kV to G15-023XFMR2 (584654) 34.5 kV to G15-023-TER2 (584659) 13.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on GEN-2015-088345.00 (585241) 345 kV Bus a. Apply Fault at the GEN-2015-088345.00 (585241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-088 (585241) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-088 (585241) 345.0 kV to G15-088-XF-2 (585249) 34.5 kV to G15-088-TR-1 (906007) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply Fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-074 (587680) 345.0 kV to G16-074XFMR1 (587681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply Fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 b.2. WESTBORO 3 (635018) 345.0 kV to ATCHSN 3 (635017) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RLHILLS3 (635100) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on S HILLS 3 345.00 (635568) 345 kV Bus a. Apply Fault at the S HILLS 3 345.00 (635568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HILLS 3 (635568) 345.0 kV to BOONVIL3 (635630) 345.0 kV Transmission Circuit #1 b.2. S HILLS 3 (635568) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply Fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply Fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #2 b.2. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on CLATONA7 115.00 (640111) 115 kV Bus a. Apply Fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLATONA7 (640111) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply Fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. CO.LINE7 (640115) 115.0 kV to BATTLCR7 (640072) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply Fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. SHELCRK3 (640342) 345.0 kV to COLMB.E3 (640125) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 7 (640521) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on TOBIAS 3345.00 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3345.00 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. TOBIAS 3 (640525) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to RTLSNAKE.W 4 (640561) 230.0 kV Transmission Circuit #1 b.2. WAKEFIELD 4 (640560) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3345.00 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3345.00 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to HAYSTACK.WD3 (640598) 345.0 kV Transmission Circuit #1 b.2. TURTLE.CRK 3 (640588) 345.0 kV to PLUMBCR.W 3 (643271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on GEN-2017-181345.00 (761292) 345 kV Bus a. Apply Fault at the GEN-2017-181345.00 (761292) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-181 (761292) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-181 (761292) 345.0 kV to GEN-2017-182 (761313) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on GEN-2017-183345.00 (761376) 345 kV Bus a. Apply Fault at the GEN-2017-183345.00 (761376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-183 (761376) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-183 (761376) 345.0 kV to G17-184XFMR2 (761401) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on G17-105TAP 161.00 (762069) 161 kV Bus a. Apply Fault at the G17-105TAP 161.00 (762069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to RAUN 5 (635201) 161.0 kV Transmission Circuit #1 b.2. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply Fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-065-TAP (763031) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 b.2. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply Fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT19 (643137) 13.8 kV Three Winding #1 b.2. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT29 (643138) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on CENCITY7 115.00 (640107) 115 kV Bus a. Apply Fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV to BLMFLD 7 (640084) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. GENOA 7 (640181) 115.0 kV to ALBION 7 (640054) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.2. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. NORFOLK7 (640298) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply Fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCHUYLR7 (640336) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. SCHUYLR7 (640336) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER_ESST8 (640141) 69.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #z b.2. GR ISLD-LNX3 (653871) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. SD.LS-KS-MB3 (659425) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to None Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to J748POI (87487) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on COOK 5 161.00 (541257) 161 kV Bus a. Apply Fault at the COOK 5 161.00 (541257) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOK 5 (541257) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. COOK 5 (541257) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on WOODBIN5 161.00 (541258) 161 kV Bus a. Apply Fault at the WOODBIN5 161.00 (541258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODBIN5 (541258) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. WOODBIN5 (541258) 161.0 kV to EAST 5 (541254) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on AVENUECTY 5 161.00 (541394) 161 kV Bus a. Apply Fault at the AVENUECTY 5 161.00 (541394) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVENUECTY 5 (541394) 161.0 kV to MIDWAY_5 (541369) 161.0 kV Transmission Circuit #1 b.2. AVENUECTY 5 (541394) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to EASTOWN7 (541400) 345.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 b.2. EASTOWN5 (541401) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on GEN-2016-050345.00 (587350) 345 kV Bus a. Apply Fault at the GEN-2016-050345.00 (587350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-050 (587350) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-050 (587350) 345.0 kV to G16-050XFMR1 (587351) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on GEN-2013-019115.00 (583700) 115 kV Bus a. Apply Fault at the GEN-2013-019115.00 (583700) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2013-019 (583700) 115.0 kV to G13-002-TAP (560746) 115.0 kV Transmission Circuit #1 b.2. GEN-2013-019 (583700) 115.0 kV to G13-019XFMR1 (583701) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on ORIENT 3 345.00 (635570) 345 kV Bus a. Apply Fault at the ORIENT 3 345.00 (635570) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORIENT 3 (635570) 345.0 kV to MADISON3 (635635) 345.0 kV Transmission Circuit #1 b.2. ORIENT 3 (635570) 345.0 kV to S HILLS 3 (635568) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on G18-125-TAP 345.00 (763410) 345 kV Bus a. Apply Fault at the G18-125-TAP 345.00 (763410) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on G18-131-TAP 345.00 (763443) 345 kV Bus a. Apply Fault at the G18-131-TAP 345.00 (763443) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-131-TAP (763443) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 b.2. G18-131-TAP (763443) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on G19-069-TAP 345.00 (763982) 345 kV Bus a. Apply Fault at the G19-069-TAP 345.00 (763982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-069-TAP (763982) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. G19-069-TAP (763982) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on STEINER7 115.00 (640361) 115 kV Bus a. Apply Fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEINER7 (640361) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.2. STEINER7 (640361) 115.0 kV to HUMBOLT7 (640235) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on GEN-2017-210345.00 (761208) 345 kV Bus a. Apply Fault at the GEN-2017-210345.00 (761208) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-210 (761208) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-210 (761208) 345.0 kV to G17-210-XFMR (761209) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply Fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GRPRAR1-LNX3 (652832) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on GEN-2017-144345.00 (760767) 345 kV Bus a. Apply Fault at the GEN-2017-144345.00 (760767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-144 (760767) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-144 (760767) 345.0 kV to G17-144XFMR2 (760771) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on UPSTREAM.W 7115.00 (643254) 115 kV Bus a. Apply Fault at the UPSTREAM.W 7115.00 (643254) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UPSTREAM.W 7 (643254) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. UPSTREAM.W 7 (643254) 115.0 kV to UPSTRM.COL19 (643255) 34.5 kV to UPSTRM.T1 9 (643257) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on RTLSNAKE.W 4230.00 (640561) 230 kV Bus a. Apply Fault at the RTLSNAKE.W 4230.00 (640561) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RTLSNAKE.W 4 (640561) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. RTLSNAKE.W 4 (640561) 230.0 kV to RTLSNAK.C1 9 (643263) 34.5 kV to RTLSNAK.T1 9 (643264) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on HAYSTACK.WD3345.00 (640598) 345 kV Bus a. Apply Fault at the HAYSTACK.WD3345.00 (640598) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYSTACK.WD3 (640598) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 b.2. HAYSTACK.WD3 (640598) 345.0 kV to HAYSTCK.C2 9 (643293) 34.5 kV to HAYSTCK.T2 9 (643298) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on PLUMBCR.W 3345.00 (643271) 345 kV Bus a. Apply Fault at the PLUMBCR.W 3345.00 (643271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLUMBCR.W 3 (643271) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 b.2. PLUMBCR.W 3 (643271) 345.0 kV to PLUMBCR.COL9 (643272) 34.5 kV to PLUMBCR T1 9 (643273) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on GEN-2017-201345.00 (760788) 345 kV Bus a. Apply Fault at the GEN-2017-201345.00 (760788) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-201 (760788) 345.0 kV to G17-201XFMR1 (760789) 34.5 kV Two Winding #1 b.2. GEN-2017-201 (760788) 345.0 kV to SHOLES.W 3 (640589) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on GEN-2017-182345.00 (761313) 345 kV Bus a. Apply Fault at the GEN-2017-182345.00 (761313) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-182 (761313) 345.0 kV to GEN-2017-181 (761292) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-182 (761313) 345.0 kV to G17-182XFMR1 (761314) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on GEN-2017-105161.00 (762070) 161 kV Bus a. Apply Fault at the GEN-2017-105161.00 (762070) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-105 (762070) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. GEN-2017-105 (762070) 161.0 kV to G17-105XFM1 (762071) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-043 (762780) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-043 (762780) 345.0 kV to G18-043-XFM1 (762781) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on G19-039-TAP 115.00 (763718) 115 kV Bus a. Apply Fault at the G19-039-TAP 115.00 (763718) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-039-TAP (763718) 115.0 kV to RISNGCY7 (640328) 115.0 kV Transmission Circuit #1 b.2. G19-039-TAP (763718) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. IATAN5 (541350) 161.0 kV to IATAN 7 (542982) 345.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_363 | Single Phase Fault with Stuck Breaker on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply Fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SILVRCK7 (640345) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. SILVRCK7 (640345) 115.0 kV to CENCITY7 (640107) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply Fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply Fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on ANTELOPE 3 345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3 345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on ANTELOPE 7 115.00 (640521) 115 kV Bus a. Apply Fault at the ANTELOPE 7 115.00 (640521) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3 345.00 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3 345.00 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on S1258 5 161.00 (646258) 161 kV Bus a. Apply Fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1280 5 (646280) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply Fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on CRESTON7 115.00 (640151) 115 kV Bus a. Apply Fault at the CRESTON7 115.00 (640151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESTON7 (640151) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on G18-125-TAP 345.00 (763410) 345 kV Bus a. Apply Fault at the G18-125-TAP 345.00 (763410) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_NPPD_FAULT_001 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_NPPD_FAULT_002 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_NPPD_FAULT_003 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.3. COOPER1G (640009) 22.0 kV to Generator #1 b.4. COOPER1G (640009) 22.0 kV to Load #S1 b.5. COOPER1G (640009) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_NPPD_FAULT_004 | Single Phase Fault with Stuck Breaker on TWIN CH4 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 (640386) 230 kV Bus b. Clear Fault after 14.5 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 b.3. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.4. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_NPPD_FAULT_005 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_NPPD_FAULT_006 | Single Phase Fault with Stuck Breaker on COLMB.E3 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 (640125) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_NPPD_FAULT_007 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_NPPD_FAULT_008 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_NPPD_FAULT_009 | Single Phase Fault with Stuck Breaker on COLMBUS4 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 (640133) 230 kV Bus b. Clear Fault after 8.5 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to COLMB.W4 (640131) 230.0 kV Transmission Circuit #1 b.3. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.4. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.5. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_TSGT_FAULT_001 | Single Phase Fault with Stuck Breaker on SIDNEY (MBPP) (659210) 230 kV Bus a. Apply Fault at the SIDNEY (MBPP) (659210) 230 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 b.2. SIDNEY___TS4 (659134) 230.0 kV to remove bus # b.3. SIDNEY__-MB4 (659210) 230.0 kV to remove bus # b.4. SIDNEY__-TS8 (659803) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LES_FAULT_001 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LES_FAULT_002 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LES_FAULT_003 | Single Phase Fault with Stuck Breaker on Rokeby (650290) 115 kV Bus a. Apply Fault at the Rokeby (650290) 115 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. ROKEBY 7 (650290) 115.0 kV to 27&PLR 7 (650229) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LES_FAULT_004 | Single Phase Fault with Stuck Breaker on Rokeby (650290) 115 kV Bus a. Apply Fault at the Rokeby (650290) 115 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. ROKEBY 7 (650290) 115.0 kV to ROKEBY 1G (650091) 13.8 kV Two Winding #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 3G (650093) 13.8 kV Two Winding #1 b.3. ROKEBY 1G (650091) 13.8 kV to Generator #1 b.4. ROKEBY 1G (650091) 13.8 kV to Load #S1 b.5. ROKEBY 1G (650091) 13.8 kV to remove bus # b.7. ROKEBY 3G (650093) 13.8 kV to Generator #3 b.8. ROKEBY 3G (650093) 13.8 kV to Load #S1 b.9. ROKEBY 3G (650093) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LES_FAULT_005 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LES_FAULT_006 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_LES_FAULT_007 | Single Phase Fault with Stuck Breaker on Rokeby (650290) 115 kV Bus a. Apply Fault at the Rokeby (650290) 115 kV Bus b. Clear Fault after 25 cycles and trip the following elements: b.1. ROKEBY 1G (650091) 13.8 kV to Generator #1 b.2. ROKEBY 3G (650093) 13.8 kV to Generator #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_OPPD_FAULT_001 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Transfer | GROUP2_P4_OPPD_FAULT_002 | Single Phase Fault with Stuck Breaker on S1244 5 (646244) 161 kV Bus a. Apply Fault at the S1244 5 (646244) 161 kV Bus b. Clear Fault after 25.5 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1244 5 (646244) 161.0 kV to Load #O0 b.4. S1244 5 (646244) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_001 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_002 | 3 Phase fault on W LINCOLN 7 115.00 (650208) 115 kV Bus a. Apply fault at the W LINCOLN 7 115.00 (650208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_003 | 3 Phase fault on NW70FAIRFD7 115.00 (650210) 115 kV Bus a. Apply fault at the NW70FAIRFD7 115.00 (650210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_004 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_005 | 3 Phase fault on 8&N 7 115.00 (650217) 115 kV Bus a. Apply fault at the 8&N 7 115.00 (650217) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_006 | 3 Phase fault on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.3. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_007 | 3 Phase fault on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_008 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_009 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_010 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_011 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_012 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_013 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_014 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_015 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_016 | 3 Phase fault on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.2. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_017 | 3 Phase fault on 93&O 7 115.00 (650273) 115 kV Bus a. Apply fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_018 | 3 Phase fault on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_019 | 3 Phase fault on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_020 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_021 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_022 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_023 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_024 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_025 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_026 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_027 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_028 | 3 Phase fault on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAVINS 7 (652511) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_029 | 3 Phase fault on COOPER1G 22.000 (640009) 22 kV Bus a. Apply fault at the COOPER1G 22.000 (640009) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER1G (640009) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_030 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_031 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_032 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_033 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_034 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_035 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_036 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_039 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_040 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_041 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_042 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_043 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_044 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_045 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_046 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_047 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_048 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_049 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_050 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_051 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_052 | 3 Phase fault on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_053 | 3 Phase fault on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.2. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_054 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_055 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_056 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_057 | 3 Phase fault on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_058 | 3 Phase fault on 40&BENNET 7 115.00 (650247) 115 kV Bus a. Apply fault at the 40&BENNET 7 115.00 (650247) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_059 | 3 Phase fault on NW56&MORTN7 115.00 (650207) 115 kV Bus a. Apply fault at the NW56&MORTN7 115.00 (650207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW70FAIRFD7 (650210) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_060 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.6. 2&N 7 (650230) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_061 | 3 Phase fault on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.2. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.6. 40&ROKEBY 7 (650250) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_062 | 3 Phase fault on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.6. 70&CALVERT7 (650270) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_063 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_064 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_065 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_066 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_067 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power Oscillations are oberserved at the Grand Prairie Wind Farm (645065, 645066, 645067 and 645068) following the fault and the units are tripped due to internal protection before reaching the 10 second post-fault time mark. The issue is resolved when the critical clearing time is reduced to 3 cycles. The issue is also observed in the PQ case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_068 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_069 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_070 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_071 | 3 Phase fault on SUB-H G 115.00 (642066) 115 kV Bus a. Apply fault at the SUB-H G 115.00 (642066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-H G (642066) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_072 | 3 Phase fault on SUB-C 7 115.00 (642070) 115 kV Bus a. Apply fault at the SUB-C 7 115.00 (642070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-C 7 (642070) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_073 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_074 | 3 Phase fault on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_075 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_076 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.2. STOCKVL7 (640365) 115.0 kV to STOCKVL8 (640366) 69.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 b.4. STOCKVLLET19 (643146) 13.8 kV to STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_077 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_078 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_079 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_080 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_081 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_082 | 3 Phase fault on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to FAIRBRYG (640170) 34.5 kV to FAIRBURY T19 (643056) 13.8 kV Three Winding #1 b.4. FAIRBURY T19 (643056) 13.8 kV to FAIRBRYG (640170) 34.5 kV to FAIRBRY7 (640169) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_083 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_084 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_085 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_086 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_087 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_088 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_089 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_090 | 3 Phase fault on WINSLOW7 115.00 (640409) 115 kV Bus a. Apply fault at the WINSLOW7 115.00 (640409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_091 | 3 Phase fault on STANTON7 115.00 (640357) 115 kV Bus a. Apply fault at the STANTON7 115.00 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_092 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_093 | 3 Phase fault on PETRSBG7 115.00 (640318) 115 kV Bus a. Apply fault at the PETRSBG7 115.00 (640318) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_094 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_095 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_096 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_097 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_098 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. COLMBS19 (640135) 13.2 kV to KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_099 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_100 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_101 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_102 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_103 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_104 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_105 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_106 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_107 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_108 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_109 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_110 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_111 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_112 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_113 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_114 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_115 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_116 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_117 | 3 Phase fault on HASTING4 230.00 (640214) 230 kV Bus a. Apply fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_118 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_119 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_120 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_121 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_122 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_123 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_124 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_125 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_126 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_127 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 b.2. STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_128 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_129 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_130 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_131 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_132 | 3 Phase fault on CREITON8 69.000 (640150) 69 kV Bus a. Apply fault at the CREITON8 69.000 (640150) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_133 | 3 Phase fault on GENOA 7 115.00 (640181) 115 kV Bus a. Apply fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENOA 7 (640181) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_134 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_135 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_136 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_137 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_138 | 3 Phase fault on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_139 | 3 Phase fault on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHUYLR7 (640336) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_140 | 3 Phase fault on SILVRCK8 69.000 (640346) 69 kV Bus a. Apply fault at the SILVRCK8 69.000 (640346) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_141 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_142 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_143 | 3 Phase fault on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETERSBRG.N7 (640444) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_144 | 3 Phase fault on COOPER 869.000 (640446) 69 kV Bus a. Apply fault at the COOPER 869.000 (640446) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_145 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_146 | 3 Phase fault on HOSKINS4 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS4 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_147 | 3 Phase fault on HOSKINS4 230.00 (640227) 345 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 345 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_148 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_149 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_150 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_151 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_152 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_153 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_154 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_155 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_156 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_157 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_158 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_159 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_160 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_161 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_162 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_163 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_164 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_165 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_166 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_167 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_168 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_169 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_170 | 3 Phase fault on S1398 5 161.00 (646398) 161 kV Bus a. Apply fault at the S1398 5 161.00 (646398) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_171 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_172 | 3 Phase fault on NCU903 8 69.000 (647401) 69 kV Bus a. Apply fault at the NCU903 8 69.000 (647401) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCU903 8 (647401) 69.0 kV to S962 8 (647962) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_173 | 3 Phase fault on S977 8 69.000 (647977) 69 kV Bus a. Apply fault at the S977 8 69.000 (647977) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCU903 8 (647401) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.2. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_174 | 3 Phase fault on S965 8 69.000 (647965) 69 kV Bus a. Apply fault at the S965 8 69.000 (647965) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_175 | 3 Phase fault on S967 8 69.000 (647967) 69 kV Bus a. Apply fault at the S967 8 69.000 (647967) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_176 | 3 Phase fault on S969 8 69.000 (647969) 69 kV Bus a. Apply fault at the S969 8 69.000 (647969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.2. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.3. S968 8 (647968) 69.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_177 | 3 Phase fault on S973 8 69.000 (647973) 69 kV Bus a. Apply fault at the S973 8 69.000 (647973) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.2. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_178 | 3 Phase fault on FREM D 8 69.000 (647424) 69 kV Bus a. Apply fault at the FREM D 8 69.000 (647424) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM D 8 (647424) 69.0 kV to FREM E 8 (647425) 69.0 kV Transmission Circuit #1 b.2. FREM D 8 (647424) 69.0 kV to S976 8 (647976) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_179 | 3 Phase fault on HYDCAP 8 69.000 (647102) 69 kV Bus a. Apply fault at the HYDCAP 8 69.000 (647102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_180 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_181 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_182 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_183 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_184 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_185 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_186 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_187 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_188 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_189 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_190 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_191 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_192 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_193 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-LR-MB3 (659426) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_194 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV Switched Shunt Device #//1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_195 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_196 | 3 Phase fault on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAVINS 7 (652511) 115.0 kV to SPIRIT_M-BE7 (659121) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_197 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_198 | 3 Phase fault on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_199 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_200 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_201 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_202 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_203 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_204 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_205 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_206 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_207 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_208 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_209 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_210 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_211 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_212 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_213 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_214 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_215 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_216 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_217 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_218 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_219 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_220 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_221 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_222 | 3 Phase fault on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_223 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_224 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_225 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_226 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_227 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_228 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_229 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_230 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_231 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_232 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_233 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_234 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_235 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_236 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_237 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_238 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_239 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_240 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_241 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_242 | 3 Phase fault on BEAT. S7 115.00 (640074) 115 kV Bus a. Apply fault at the BEAT. S7 115.00 (640074) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_243 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_244 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_245 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_246 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_247 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_248 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_249 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_250 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_251 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_252 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_253 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_254 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_255 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_256 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_257 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_258 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_259 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_260 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_261 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_262 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_263 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_264 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_265 | 3 Phase fault on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_266 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_267 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_268 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_269 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_270 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_271 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_272 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_273 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_274 | 3 Phase fault on COOPER_ESST869.000 (640141) 69 kV Bus a. Apply fault at the COOPER_ESST869.000 (640141) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_ESST8 (640141) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_275 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_276 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_277 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_278 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_279 | 3 Phase fault on FRIEND 7 115.00 (640174) 115 kV Bus a. Apply fault at the FRIEND 7 115.00 (640174) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_280 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_281 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_282 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_283 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_284 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_285 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_286 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_287 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_288 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_289 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_290 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_291 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_292 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_293 | 3 Phase fault on HARBINE7 115.00 (640208) 115 kV Bus a. Apply fault at the HARBINE7 115.00 (640208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_294 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_295 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_296 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_297 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_298 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_299 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_300 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_301 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_302 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_303 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_304 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_305 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_306 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_307 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_308 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_309 | 3 Phase fault on MALONEY7 115.00 (640265) 115 kV Bus a. Apply fault at the MALONEY7 115.00 (640265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_310 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_311 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_312 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_313 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_314 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_315 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_316 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_317 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_318 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_319 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Post fault steady state voltages at STERLNG7 (640362), FIRTH 7 (640171), GEN-2013-019 (583700), GEN-2019-041 (763725), G13-002-TAP (560746), and MONOLITH 7 (640591) do not recover above 0.9 p.u. No CQ units meet the PTDF criteria to be contingent on the upgrade. Issue also observed in the base case. Stable response observed after the upgrade is in-service. | Multi - Sheldon - Monolith 115 kV
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_320 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_321 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_322 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_323 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_324 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_325 | 3 Phase fault on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_326 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_327 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_328 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_329 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_330 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_331 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_332 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_333 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_334 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_335 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_336 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_337 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_338 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_339 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_340 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 3 (640520) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_341 | 3 Phase fault on BOBCAT.C 3345.00 (640529) 345 kV Bus a. Apply fault at the BOBCAT.C 3345.00 (640529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT.C 3 (640529) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_342 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_343 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_344 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_345 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_346 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | The Laramie generating site (659118) loses synchronism after the fault. The issue is resolved when the critical clearing time is reduced to 5 cycles. The issue is also observed in the PQ case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_347 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_348 | 3 Phase fault on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_349 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_350 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_351 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_352 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR8 (640073) 69.0 kV to BATTLCR7 (640072) 115.0 kV to BATTLECRKT19 (643011) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_353 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_354 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_355 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_356 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 8 (640085) 69.0 kV to BLMFLD 7 (640084) 115.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_357 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_358 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_359 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_360 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 8 (640273) 69.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_361 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT8 (640288) 69.0 kV to N.PLATT7 (640287) 115.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_362 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_363 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_364 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_365 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT19 (643137) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_366 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT29 (643138) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_367 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 8 (640360) 69.0 kV to STAPLETON 7 (640359) 115.0 kV to STAPLETONT19 (643175) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_368 | 3 Phase fault on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RISNGCY8 (640417) 69.0 kV to RISNGCY7 (640328) 115.0 kV to RISINGCTYT29 (643127) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_369 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 8 (640443) 69.0 kV to YORK 7 (640411) 115.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_370 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_371 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_372 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAMORA 8 (640468) 69.0 kV to TAMORA 7 (640375) 115.0 kV to TAMORA T2 9 (643181) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_373 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_374 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_375 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_376 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S966 8 (647966) 69.0 kV to STEINER7 (640361) 115.0 kV to STEINER T1 9 (643143) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_377 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_378 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_379 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_380 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_381 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_001 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_002 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_004 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_005 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_006 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_007 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_008 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_009 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_010 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_011 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_012 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_015 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_017 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_018 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_020 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_021 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_022 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_023 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_024 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_025 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_026 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_027 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_028 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_029 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_030 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_031 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_032 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_033 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_036 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_037 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to None Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_041 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_042 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_043 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_044 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_045 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_046 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_047 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_048 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_049 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_051 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1 (541171), OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on MADISON3 345.00 (635635) 345 kV Bus a. Apply Fault at the MADISON3 345.00 (635635) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORIENT 3 (635570) 345.0 kV to MADISON3 (635635) 345.0 kV Transmission Circuit #1 b.2. BOONVIL3 (635630) 345.0 kV to MADISON3 (635635) 345.0 kV Transmission Circuit #1 b.3. MADISON3 (635635) 345.0 kV to NORWLK3 (635640) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.2. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply Fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 b.2. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on SALIX 5 161.00 (635235) 161 kV Bus a. Apply Fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.3. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on MONONA 5 161.00 (635300) 161 kV Bus a. Apply Fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.4. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.4. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply Fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 b.2. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.3. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.4. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.7. S1366 5 (646366) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. HOSK.T89 (640230) 34.5 kV to HOSKINS4 (640227) 230.0 kV Two Winding #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply Fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.3. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT19 (643039) 13.8 kV Three Winding #1 b.4. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT29 (643040) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.3. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.4. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.5. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.3. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.4. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.4. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.5. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T1 9 (643004) 13.8 kV Three Winding #1 b.6. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T2 9 (643005) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.4. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.4. BELDEN 7 (640080) 115.0 kV to BELDEN 8 (640081) 69.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 b.2. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 b.4. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CENCITY7 115.00 (640107) 115 kV Bus a. Apply Fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.3. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT19 (643032) 13.8 kV Three Winding #1 b.4. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT29 (643033) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply Fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 b.2. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. COL.SE 7 (640124) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.3. CREITON7 (640149) 115.0 kV to CREITON8 (640150) 69.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on CRESTON7 115.00 (640151) 115 kV Bus a. Apply Fault at the CRESTON7 115.00 (640151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.2. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.3. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T1 9 (643046) 4.2 kV Three Winding #1 b.4. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T2 9 (643047) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on CRETE__7 115.00 (640153) 115 kV Bus a. Apply Fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.3. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T1 9 (643048) 13.8 kV Three Winding #1 b.4. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T2 9 (643049) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FREMONT7 115.00 (640173) 115 kV Bus a. Apply Fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.3. FREMONT7 (640173) 115.0 kV to S976 8 (647976) 69.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 b.4. FREMONT7 (640173) 115.0 kV to S976 8 (647976) 69.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply Fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.2. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.3. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.4. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 b.5. GENEVA 7 (640178) 115.0 kV to GENEVA 8 (640179) 69.0 kV to GENEVA T2 9 (643062) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T1 9 (643064) 13.8 kV Three Winding #1 b.4. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T2 9 (643065) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HARBINE7 115.00 (640208) 115 kV Bus a. Apply Fault at the HARBINE7 115.00 (640208) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.3. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to KINGSLY7 (640255) 115.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.3. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to MCCOOK G (640017) 13.8 kV Two Winding #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.4. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.5. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 b.6. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply Fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.4. MCCOOL 7 (640272) 115.0 kV to MCCOOL 8 (640273) 69.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on MINDEN 7 115.00 (640275) 115 kV Bus a. Apply Fault at the MINDEN 7 115.00 (640275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. MINDEN 7 (640275) 115.0 kV to MINDEN 9 (640276) 34.5 kV to MINDEN T1 9 (643102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.3. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.4. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.5. NELIGH 7 (640293) 115.0 kV to NELIGH 8 (640294) 69.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 b.6. NELIGH 7 (640293) 115.0 kV to NELIGH 9 (640295) 34.5 kV to NELIGH T1 9 (643109) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T1 9 (643112) 13.8 kV Three Winding #1 b.5. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T2 9 (643113) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply Fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT19 (643110) 13.8 kV Three Winding #1 b.5. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT29 (643111) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.4. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.5. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply Fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.3. RISNGCY7 (640328) 115.0 kV to RISNGCY9 (640329) 34.5 kV to RISINGCTYT19 (643126) 13.8 kV Three Winding #1 b.4. RISNGCY7 (640328) 115.0 kV to RISNGCY8 (640417) 69.0 kV to RISINGCTYT29 (643127) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply Fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.3. SCHUYLR7 (640336) 115.0 kV to SCHUYLR9 (640337) 34.5 kV to SCHUYLER T19 (643131) 13.8 kV Three Winding #1 b.4. SCHUYLR7 (640336) 115.0 kV to SCHUYLR9 (640337) 34.5 kV to SCHUYLER T29 (643132) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SEWARD 7 115.00 (640340) 115 kV Bus a. Apply Fault at the SEWARD 7 115.00 (640340) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.3. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 b.4. SEWARD 7 (640340) 115.0 kV to SEWARD 9 (640341) 34.5 kV to SEWARD T1 9 (643134) 13.8 kV Three Winding #1 b.5. SEWARD 7 (640340) 115.0 kV to SEWARD 9 (640341) 34.5 kV to SEWARD T2 9 (643135) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply Fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.2. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.3. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T19 (643139) 13.8 kV Three Winding #1 b.4. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T29 (643169) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on STNTN.N7 115.00 (640363) 115 kV Bus a. Apply Fault at the STNTN.N7 115.00 (640363) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. STNTN.N7 (640363) 115.0 kV to STNTN.N9 (640364) 34.5 kV to STANTN.N T19 (643145) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.2. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.3. THEDFRD7 (640381) 115.0 kV to THEDFRD9 (640382) 34.5 kV to THEDFORD T19 (643153) 13.8 kV Three Winding #1 b.4. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WAHOO 7 115.00 (640402) 115 kV Bus a. Apply Fault at the WAHOO 7 115.00 (640402) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAVEY 7 (640155) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 b.3. WAHOO 29 (648402) 13.8 kV to WAHOO 7 (640402) 115.0 kV Two Winding #1 b.4. WAHOO 7 (640402) 115.0 kV to WAHOO G (640403) 34.5 kV to WAHOO T1 9 (643163) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on YORK 7 115.00 (640411) 115 kV Bus a. Apply Fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.3. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.4. YORK 7 (640411) 115.0 kV to YORK 9 (640412) 34.5 kV to YORK T1 9 (643166) 13.8 kV Three Winding #1 b.5. YORK 7 (640411) 115.0 kV to YORK 8 (640443) 69.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on YORK SW7 115.00 (640413) 115 kV Bus a. Apply Fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.2. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. YORK SW7 (640413) 115.0 kV to YORK SW9 (640414) 34.5 kV to YORK.SW T1 9 (643168) 13.8 kV Three Winding #1 b.4. YORK SW7 (640413) 115.0 kV to YORK.SW T2 8 (640447) 69.0 kV to YORK.SW T2 9 (643176) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.2. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to Load #NW b.2. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.3. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.4. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to Load #NW b.2. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.3. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.4. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS9 (640137) 34.5 kV to Load #N0 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.5. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T69 (643042) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply Fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. E.COL. 4 (640126) 230.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.4. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT19 (643037) 13.8 kV Three Winding #1 b.5. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT29 (643038) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.3. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.5. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS9 (640229) 34.5 kV to Load #N2 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS9 (640229) 34.5 kV to Load #N2 b.2. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.4. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEARNEY9 (640251) 34.5 kV to Load #N0 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 b.8. KEARNEY7 (640250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.3. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 b.5. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to NORTHPLT T79 (643107) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply Fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.2. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z b.3. OGALALA9 (640303) 34.5 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T29 (643116) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 b.2. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on STEELEC7 115.00 (640426) 115 kV Bus a. Apply Fault at the STEELEC7 115.00 (640426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.2. STEELEC9 (640427) 4.2 kV to STEELEC7 (640426) 115.0 kV Two Winding #1 b.3. STEELEC7 (640426) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.2. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.3. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.4. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.6. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 b.7. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply Fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.3. ELKRDG.PLT D (640419) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.4. CROFTN.PLT D (640423) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.5. BLMFLD 7 (640084) 115.0 kV to BLMFLD 8 (640085) 69.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS9 (640137) 34.5 kV to Load #N0 b.2. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. COLMBUS7 (640136) 115.0 kV to COLMBS1G (640006) 13.8 kV Two Winding #1 b.4. COLMBUS7 (640136) 115.0 kV to COLMBS2G (640007) 13.8 kV Two Winding #1 b.5. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.6. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.7. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.8. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.9. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.12. COLMBUS7 (640136) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.5. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.6. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.7. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.8. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T69 (643042) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on COL.COG7 115.00 (640119) 115 kV Bus a. Apply Fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #1 b.2. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply Fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.4. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 b.5. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.6. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT19 (643037) 13.8 kV Three Winding #1 b.7. COLMB.E7 (640127) 115.0 kV to COLMB.E9 (640128) 34.5 kV to COLMB.ESTT29 (643038) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.4. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.5. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.6. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.7. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.8. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG9 (640225) 34.5 kV to Load #N0 b.2. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.3. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.5. HOLDREG7 (640224) 115.0 kV to HOLDREGE 8 (640448) 69.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 b.10. HOLDREG7 (640224) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.8. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.6. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 b.3. LAREDO.PLT 9 (640433) 34.5 kV to PETERSBRG.N7 (640444) 115.0 kV Two Winding #1 b.4. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on STEELEC7 115.00 (640426) 115 kV Bus a. Apply Fault at the STEELEC7 115.00 (640426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOB HL3 (533332) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.2. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.3. STEELEC7 (640426) 115.0 kV to S.FLATS.PLT7 (640558) 115.0 kV Transmission Circuit #1 b.4. STEELEC9 (640427) 4.2 kV to STEELEC7 (640426) 115.0 kV Two Winding #1 b.5. STEELEC_KXL9 (640440) 6.9 kV to STEELEC7 (640426) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.3. N.PLATTG (640018) 13.8 kV to N.PLATT9 (640289) 34.5 kV to N.PLATT7 (640287) 115.0 kV Three Winding #1 b.4. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 b.6. N.PLATT7 (640287) 115.0 kV to N.PLATT8 (640288) 69.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 b.7. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to N.PLATTG (640018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549) and OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.2. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to GEN-2019-009 (763505) 161.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.6. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on FLTWTR1W 0.6900 (645061) 0.689999998 kV Bus a. Apply Fault at the FLTWTR1W 0.6900 (645061) 0.689999998 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. S1399 5 (646399) 161.0 kV to FLTWTRX9 (648500) 34.5 kV to FLTWTRY9 (648501) 13.8 kV Three Winding #1 b.6. FLTWTR1W (645061) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on KELLY 5 161.00 (532913) 161 kV Bus a. Apply Fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.4. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. HUMBOLT5 (640234) 161.0 kV to HUMBOLT7 (640235) 115.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.3. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to HUMBOLT7 (640235) 115.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on S1258 5 161.00 (646258) 161 kV Bus a. Apply Fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on S1258 5 161.00 (646258) 161 kV Bus a. Apply Fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.4. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.5. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply Fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 b.2. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.3. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.4. GRANTNB_-TS7 (659800) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.5. OGALALA_-TS7 (659801) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.6. OGALALA_-TS7 (659801) 115.0 kV to MCONGHY_-TS7 (659824) 115.0 kV Transmission Circuit #1 b.7. ELSIETP_-TS7 (659807) 115.0 kV to PAXTON__-TS7 (659808) 115.0 kV Transmission Circuit #1 b.8. ELSIETP_-TS7 (659807) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.9. ELSIETP_-TS7 (659807) 115.0 kV to ELSIE___-TS7 (659822) 115.0 kV Transmission Circuit #1 b.10. MCONGHY_-TS7 (659824) 115.0 kV to ARTHUR__-TS7 (659825) 115.0 kV Transmission Circuit #1 b.11. BRULE 7 (640091) 115.0 kV to BRULE 9 (640092) 34.5 kV to BRULE T1 9 (643025) 13.8 kV Three Winding #1 b.12. OGALALA9 (640303) 34.5 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T29 (643116) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply Fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply Fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on 8&N 7 115.00 (650217) 115 kV Bus a. Apply Fault at the 8&N 7 115.00 (650217) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8&J 9 (650100) 34.5 kV to 171TERTIARY (650517) 34.5 kV Transmission Circuit #1 b.2. 8&N 7 (650217) 115.0 kV to 17&HOLDRGE7 (650219) 115.0 kV Transmission Circuit #1 b.3. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. 8&N 7 (650217) 115.0 kV to 8&N A9 (650317) 13.2 kV to 171TERTIARY (650517) 34.5 kV Three Winding #1 b.5. 8&N 7 (650217) 115.0 kV to 8&N B9 (650417) 13.2 kV to 172TERTIARY (650617) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply Fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.4. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply Fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.3. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.4. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on 3&VANDORN 7 115.00 (650218) 115 kV Bus a. Apply Fault at the 3&VANDORN 7 115.00 (650218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 3&VANDORN 7 (650218) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. 3&VANDORN 7 (650218) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.3. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 3&VANDORN 7 (650218) 115.0 kV to 3VANDORN 9 (650318) 13.2 kV to 181TERTIARY (650518) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply Fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&Q 7 (650260) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply Fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 30&A 7 (650252) 115.0 kV to 56&EVERETT7 (650256) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on 40&GERTIE 7 115.00 (650258) 115 kV Bus a. Apply Fault at the 40&GERTIE 7 115.00 (650258) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.5. 40&GERTIE 7 (650258) 115.0 kV to 40&GE A9 (650358) 13.2 kV to 581TERTIARY (650558) 7.2 kV Three Winding #1 b.6. 40&GERTIE 7 (650258) 115.0 kV to 40&GE B9 (650458) 13.2 kV to 582TERTIARY (650658) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on 56&ELK TAP7 115.00 (650257) 115 kV Bus a. Apply Fault at the 56&ELK TAP7 115.00 (650257) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.2. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.2. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.3. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.4. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.5. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.6. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.9. 70&CALVERT7 (650270) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.4. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.5. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.6. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 b.11. 70&CALVERT7 (650270) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 2G (650092) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 3G (650093) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 2G (650092) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 1G (650091) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.8. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.9. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply Fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.3. 27&PLR 7 (650229) 115.0 kV to 27&PLR A9 (650329) 12.5 kV to 291TERTIARY (650529) 7.2 kV Three Winding #1 b.4. 27&PLR 7 (650229) 115.0 kV to 27&PLR B9 (650429) 12.5 kV to 292TERTIARY (650629) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.2. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.5. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.6. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on 40&BENNET 7 115.00 (650247) 115 kV Bus a. Apply Fault at the 40&BENNET 7 115.00 (650247) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on 56&PLR 7 115.00 (650255) 115 kV Bus a. Apply Fault at the 56&PLR 7 115.00 (650255) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on NW12&ARBOR7 115.00 (650226) 115 kV Bus a. Apply Fault at the NW12&ARBOR7 115.00 (650226) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW70FAIRFD7 (650210) 115.0 kV Transmission Circuit #1 b.2. NW56&MORTN7 (650207) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.3. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.4. 19&ALVO 7 (650215) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.5. NW70FAIRFD7 (650210) 115.0 kV to NW70FAIRFD9 (650310) 12.5 kV to 101TERTIARY (650510) 7.2 kV Three Winding #1 b.6. NW12&ARBOR7 (650226) 115.0 kV to NW12&AR 9 (650326) 12.5 kV to 261TERTIARY (650526) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on NW5&BENTON7 115.00 (650212) 115 kV Bus a. Apply Fault at the NW5&BENTON7 115.00 (650212) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4&MORTON 7 (650205) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.2. W LINCOLN 7 (650208) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.3. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. W LINCOLN 7 (650208) 115.0 kV to WLINCOLN 9 (650308) 13.2 kV to 084TERTIARY (650508) 7.2 kV Three Winding #1 b.5. NW5&BENTON7 (650212) 115.0 kV to NW5BENTN 9 (650312) 12.5 kV to 121TERTIARY (650512) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.5. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.7. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. 8&N 7 (650217) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.7. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.4. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.7. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 b.2. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.3. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.7. 40&ROKEBY 7 (650250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.4. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.7. 70&CALVERT7 (650270) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.2. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.7. 40&ROKEBY 7 (650250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on 40&ROKEBY 7 115.00 (650250) 115 kV Bus a. Apply Fault at the 40&ROKEBY 7 115.00 (650250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 40&ROKEBY 7 (650250) 115.0 kV to 56&PLR 7 (650255) 115.0 kV Transmission Circuit #1 b.2. 56&PLR 7 (650255) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 56&PLR 7 (650255) 115.0 kV to 56&PLR 9 (650355) 12.5 kV to 551TERTIARY (650555) 7.2 kV Three Winding #1 b.7. 40&ROKEBY 7 (650250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLM1G (640010) 23.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 8 (640446) 69.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. NCU903 8 (647401) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 b.4. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER_602 8 (640143) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #z1 b.2. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on S967 8 69.000 (647967) 69 kV Bus a. Apply Fault at the S967 8 69.000 (647967) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.2. TECUMSH8 (647400) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.3. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on S968 8 69.000 (647968) 69 kV Bus a. Apply Fault at the S968 8 69.000 (647968) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECUMSH8 (647400) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.2. S967 8 (647967) 69.0 kV to S968 8 (647968) 69.0 kV Transmission Circuit #1 b.3. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.4. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on HYDCAP 8 69.000 (647102) 69 kV Bus a. Apply Fault at the HYDCAP 8 69.000 (647102) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.4. NC SYRA8 (647402) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.5. NC SYRA8 (647402) 69.0 kV to S971 8 (647971) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on S974 8 69.000 (647974) 69 kV Bus a. Apply Fault at the S974 8 69.000 (647974) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.2. S968 8 (647968) 69.0 kV to S969 8 (647969) 69.0 kV Transmission Circuit #1 b.3. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.4. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.5. S968 8 (647968) 69.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on STERLNG7 115.00 (640362) 115 kV Bus a. Apply Fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDCAP 8 (647102) 69.0 kV to ENRON 8 (647103) 69.0 kV Transmission Circuit #1 b.2. HYDCAP 8 (647102) 69.0 kV to S970 8 (647970) 69.0 kV Transmission Circuit #1 b.3. HYDCAP 8 (647102) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.4. S969 8 (647969) 69.0 kV to S974 8 (647974) 69.0 kV Transmission Circuit #1 b.5. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.2. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.3. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 b.5. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on S993 8 69.000 (647993) 69 kV Bus a. Apply Fault at the S993 8 69.000 (647993) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. MGLN TP8 (647112) 69.0 kV to S964 8 (647964) 69.0 kV Transmission Circuit #1 b.5. MGLN TP8 (647112) 69.0 kV to S993 8 (647993) 69.0 kV Transmission Circuit #1 b.6. S964 8 (647964) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.7. S993 9 (649993) 13.8 kV to S993 8 (647993) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on AUBRNT 8 69.000 (647101) 69 kV Bus a. Apply Fault at the AUBRNT 8 69.000 (647101) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 8 (640062) 69.0 kV to AUBRNT 8 (647101) 69.0 kV Transmission Circuit #1 b.2. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 b.4. S965 8 (647965) 69.0 kV to S975 8 (647975) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.8. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.4. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.5. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.7. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z b.3. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.4. SIDNEY__-MB9 (659168) 13.8 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Three Winding #1 b.5. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.2. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.3. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 b.4. SIDNEY__-MB9 (659168) 13.8 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Three Winding #1 b.5. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 b.2. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on EAST 5 161.00 (541254) 161 kV Bus a. Apply Fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST 5 (541254) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 b.2. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on IND PRK5 161.00 (541256) 161 kV Bus a. Apply Fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 b.2. IND PRK5 (541256) 161.0 kV to LAKE RD5 (541255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on G13-002-TAP 115.00 (560746) 115 kV Bus a. Apply Fault at the G13-002-TAP 115.00 (560746) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G13-002-TAP (560746) 115.0 kV to GEN-2013-019 (583700) 115.0 kV Transmission Circuit #1 b.2. G13-002-TAP (560746) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply Fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-023 (584650) 345.0 kV to G15-023XFMR2 (584654) 34.5 kV to G15-023-TER2 (584659) 13.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on GEN-2015-088345.00 (585241) 345 kV Bus a. Apply Fault at the GEN-2015-088345.00 (585241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-088 (585241) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-088 (585241) 345.0 kV to G15-088-XF-2 (585249) 34.5 kV to G15-088-TR-1 (906007) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply Fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-074 (587680) 345.0 kV to G16-074XFMR1 (587681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply Fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 b.2. WESTBORO 3 (635018) 345.0 kV to ATCHSN 3 (635017) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RLHILLS3 (635100) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on S HILLS 3 345.00 (635568) 345 kV Bus a. Apply Fault at the S HILLS 3 345.00 (635568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HILLS 3 (635568) 345.0 kV to BOONVIL3 (635630) 345.0 kV Transmission Circuit #1 b.2. S HILLS 3 (635568) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply Fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply Fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #2 b.2. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on CLATONA7 115.00 (640111) 115 kV Bus a. Apply Fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLATONA7 (640111) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply Fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. CO.LINE7 (640115) 115.0 kV to BATTLCR7 (640072) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply Fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. SHELCRK3 (640342) 345.0 kV to COLMB.E3 (640125) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 7 (640521) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on TOBIAS 3345.00 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3345.00 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. TOBIAS 3 (640525) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to RTLSNAKE.W 4 (640561) 230.0 kV Transmission Circuit #1 b.2. WAKEFIELD 4 (640560) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3345.00 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3345.00 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to HAYSTACK.WD3 (640598) 345.0 kV Transmission Circuit #1 b.2. TURTLE.CRK 3 (640588) 345.0 kV to PLUMBCR.W 3 (643271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on GEN-2017-181345.00 (761292) 345 kV Bus a. Apply Fault at the GEN-2017-181345.00 (761292) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-181 (761292) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-181 (761292) 345.0 kV to GEN-2017-182 (761313) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on GEN-2017-183345.00 (761376) 345 kV Bus a. Apply Fault at the GEN-2017-183345.00 (761376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-183 (761376) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-183 (761376) 345.0 kV to G17-184XFMR2 (761401) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on G17-105TAP 161.00 (762069) 161 kV Bus a. Apply Fault at the G17-105TAP 161.00 (762069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to RAUN 5 (635201) 161.0 kV Transmission Circuit #1 b.2. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply Fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-065-TAP (763031) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 b.2. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply Fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT19 (643137) 13.8 kV Three Winding #1 b.2. SILVRCK8 (640346) 69.0 kV to SILVRCK7 (640345) 115.0 kV to SILVERCRKT29 (643138) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on CENCITY7 115.00 (640107) 115 kV Bus a. Apply Fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV to BLMFLD 7 (640084) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. GENOA 7 (640181) 115.0 kV to ALBION 7 (640054) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.2. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. NORFOLK7 (640298) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on SCHUYLR7 115.00 (640336) 115 kV Bus a. Apply Fault at the SCHUYLR7 115.00 (640336) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCHUYLR7 (640336) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. SCHUYLR7 (640336) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER_ESST8 (640141) 69.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #z b.2. GR ISLD-LNX3 (653871) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. SD.LS-KS-MB3 (659425) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to None Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to J748POI (87487) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on COOK 5 161.00 (541257) 161 kV Bus a. Apply Fault at the COOK 5 161.00 (541257) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOK 5 (541257) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. COOK 5 (541257) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on WOODBIN5 161.00 (541258) 161 kV Bus a. Apply Fault at the WOODBIN5 161.00 (541258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODBIN5 (541258) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. WOODBIN5 (541258) 161.0 kV to EAST 5 (541254) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on AVENUECTY 5 161.00 (541394) 161 kV Bus a. Apply Fault at the AVENUECTY 5 161.00 (541394) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVENUECTY 5 (541394) 161.0 kV to MIDWAY_5 (541369) 161.0 kV Transmission Circuit #1 b.2. AVENUECTY 5 (541394) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to EASTOWN7 (541400) 345.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 b.2. EASTOWN5 (541401) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on GEN-2016-050345.00 (587350) 345 kV Bus a. Apply Fault at the GEN-2016-050345.00 (587350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-050 (587350) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-050 (587350) 345.0 kV to G16-050XFMR1 (587351) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on GEN-2013-019115.00 (583700) 115 kV Bus a. Apply Fault at the GEN-2013-019115.00 (583700) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2013-019 (583700) 115.0 kV to G13-002-TAP (560746) 115.0 kV Transmission Circuit #1 b.2. GEN-2013-019 (583700) 115.0 kV to G13-019XFMR1 (583701) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on ORIENT 3 345.00 (635570) 345 kV Bus a. Apply Fault at the ORIENT 3 345.00 (635570) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORIENT 3 (635570) 345.0 kV to MADISON3 (635635) 345.0 kV Transmission Circuit #1 b.2. ORIENT 3 (635570) 345.0 kV to S HILLS 3 (635568) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on G18-125-TAP 345.00 (763410) 345 kV Bus a. Apply Fault at the G18-125-TAP 345.00 (763410) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on G18-131-TAP 345.00 (763443) 345 kV Bus a. Apply Fault at the G18-131-TAP 345.00 (763443) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-131-TAP (763443) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 b.2. G18-131-TAP (763443) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on G19-069-TAP 345.00 (763982) 345 kV Bus a. Apply Fault at the G19-069-TAP 345.00 (763982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-069-TAP (763982) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. G19-069-TAP (763982) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on STEINER7 115.00 (640361) 115 kV Bus a. Apply Fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEINER7 (640361) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.2. STEINER7 (640361) 115.0 kV to HUMBOLT7 (640235) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on GEN-2017-210345.00 (761208) 345 kV Bus a. Apply Fault at the GEN-2017-210345.00 (761208) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-210 (761208) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-210 (761208) 345.0 kV to G17-210-XFMR (761209) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply Fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GRPRAR1-LNX3 (652832) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on GEN-2017-144345.00 (760767) 345 kV Bus a. Apply Fault at the GEN-2017-144345.00 (760767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-144 (760767) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-144 (760767) 345.0 kV to G17-144XFMR2 (760771) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on UPSTREAM.W 7115.00 (643254) 115 kV Bus a. Apply Fault at the UPSTREAM.W 7115.00 (643254) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UPSTREAM.W 7 (643254) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. UPSTREAM.W 7 (643254) 115.0 kV to UPSTRM.COL19 (643255) 34.5 kV to UPSTRM.T1 9 (643257) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on RTLSNAKE.W 4230.00 (640561) 230 kV Bus a. Apply Fault at the RTLSNAKE.W 4230.00 (640561) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RTLSNAKE.W 4 (640561) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. RTLSNAKE.W 4 (640561) 230.0 kV to RTLSNAK.C1 9 (643263) 34.5 kV to RTLSNAK.T1 9 (643264) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on HAYSTACK.WD3345.00 (640598) 345 kV Bus a. Apply Fault at the HAYSTACK.WD3345.00 (640598) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYSTACK.WD3 (640598) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 b.2. HAYSTACK.WD3 (640598) 345.0 kV to HAYSTCK.C2 9 (643293) 34.5 kV to HAYSTCK.T2 9 (643298) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on PLUMBCR.W 3345.00 (643271) 345 kV Bus a. Apply Fault at the PLUMBCR.W 3345.00 (643271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLUMBCR.W 3 (643271) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 b.2. PLUMBCR.W 3 (643271) 345.0 kV to PLUMBCR.COL9 (643272) 34.5 kV to PLUMBCR T1 9 (643273) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on GEN-2017-201345.00 (760788) 345 kV Bus a. Apply Fault at the GEN-2017-201345.00 (760788) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-201 (760788) 345.0 kV to G17-201XFMR1 (760789) 34.5 kV Two Winding #1 b.2. GEN-2017-201 (760788) 345.0 kV to SHOLES.W 3 (640589) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on GEN-2017-182345.00 (761313) 345 kV Bus a. Apply Fault at the GEN-2017-182345.00 (761313) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-182 (761313) 345.0 kV to GEN-2017-181 (761292) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-182 (761313) 345.0 kV to G17-182XFMR1 (761314) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on GEN-2017-105161.00 (762070) 161 kV Bus a. Apply Fault at the GEN-2017-105161.00 (762070) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-105 (762070) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. GEN-2017-105 (762070) 161.0 kV to G17-105XFM1 (762071) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-043 (762780) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-043 (762780) 345.0 kV to G18-043-XFM1 (762781) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on G19-039-TAP 115.00 (763718) 115 kV Bus a. Apply Fault at the G19-039-TAP 115.00 (763718) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-039-TAP (763718) 115.0 kV to RISNGCY7 (640328) 115.0 kV Transmission Circuit #1 b.2. G19-039-TAP (763718) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. IATAN5 (541350) 161.0 kV to IATAN 7 (542982) 345.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_363 | Single Phase Fault with Stuck Breaker on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply Fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SILVRCK7 (640345) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. SILVRCK7 (640345) 115.0 kV to CENCITY7 (640107) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on RISNGCY7 115.00 (640328) 115 kV Bus a. Apply Fault at the RISNGCY7 115.00 (640328) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RISNGCY7 (640328) 115.0 kV to G19-039-TAP (763718) 115.0 kV Transmission Circuit #1 b.2. RISNGCY7 (640328) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply Fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on ANTELOPE 3 345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3 345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on ANTELOPE 7 115.00 (640521) 115 kV Bus a. Apply Fault at the ANTELOPE 7 115.00 (640521) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3 345.00 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3 345.00 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on S1258 5 161.00 (646258) 161 kV Bus a. Apply Fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1280 5 (646280) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply Fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on CRESTON7 115.00 (640151) 115 kV Bus a. Apply Fault at the CRESTON7 115.00 (640151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESTON7 (640151) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on G18-125-TAP 345.00 (763410) 345 kV Bus a. Apply Fault at the G18-125-TAP 345.00 (763410) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_NPPD_FAULT_001 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_NPPD_FAULT_002 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_NPPD_FAULT_003 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.3. COOPER1G (640009) 22.0 kV to Generator #1 b.4. COOPER1G (640009) 22.0 kV to Load #S1 b.5. COOPER1G (640009) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_NPPD_FAULT_004 | Single Phase Fault with Stuck Breaker on TWIN CH4 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 (640386) 230 kV Bus b. Clear Fault after 14.5 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 b.3. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.4. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_NPPD_FAULT_005 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_NPPD_FAULT_006 | Single Phase Fault with Stuck Breaker on COLMB.E3 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 (640125) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_NPPD_FAULT_007 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_NPPD_FAULT_008 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_NPPD_FAULT_009 | Single Phase Fault with Stuck Breaker on COLMBUS4 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 (640133) 230 kV Bus b. Clear Fault after 8.5 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to COLMB.W4 (640131) 230.0 kV Transmission Circuit #1 b.3. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.4. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.5. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_TSGT_FAULT_001 | Single Phase Fault with Stuck Breaker on SIDNEY (MBPP) (659210) 230 kV Bus a. Apply Fault at the SIDNEY (MBPP) (659210) 230 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 b.2. SIDNEY___TS4 (659134) 230.0 kV to remove bus # b.3. SIDNEY__-MB4 (659210) 230.0 kV to remove bus # b.4. SIDNEY__-TS8 (659803) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LES_FAULT_001 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LES_FAULT_002 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LES_FAULT_003 | Single Phase Fault with Stuck Breaker on Rokeby (650290) 115 kV Bus a. Apply Fault at the Rokeby (650290) 115 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. ROKEBY 7 (650290) 115.0 kV to 27&PLR 7 (650229) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LES_FAULT_004 | Single Phase Fault with Stuck Breaker on Rokeby (650290) 115 kV Bus a. Apply Fault at the Rokeby (650290) 115 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. ROKEBY 7 (650290) 115.0 kV to ROKEBY 1G (650091) 13.8 kV Two Winding #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 3G (650093) 13.8 kV Two Winding #1 b.3. ROKEBY 1G (650091) 13.8 kV to Generator #1 b.4. ROKEBY 1G (650091) 13.8 kV to Load #S1 b.5. ROKEBY 1G (650091) 13.8 kV to remove bus # b.7. ROKEBY 3G (650093) 13.8 kV to Generator #3 b.8. ROKEBY 3G (650093) 13.8 kV to Load #S1 b.9. ROKEBY 3G (650093) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LES_FAULT_005 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LES_FAULT_006 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 3 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_LES_FAULT_007 | Single Phase Fault with Stuck Breaker on Rokeby (650290) 115 kV Bus a. Apply Fault at the Rokeby (650290) 115 kV Bus b. Clear Fault after 25 cycles and trip the following elements: b.1. ROKEBY 1G (650091) 13.8 kV to Generator #1 b.2. ROKEBY 3G (650093) 13.8 kV to Generator #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_OPPD_FAULT_001 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Transfer | GROUP2_P4_OPPD_FAULT_002 | Single Phase Fault with Stuck Breaker on S1244 5 (646244) 161 kV Bus a. Apply Fault at the S1244 5 (646244) 161 kV Bus b. Clear Fault after 25.5 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1244 5 (646244) 161.0 kV to Load #O0 b.4. S1244 5 (646244) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_033 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_051 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_066 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_191 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_208 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_209 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_223 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_225 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_230 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_231 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_294 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_REGIONAL_FAULT_033 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_033 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_051 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_066 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_191 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_208 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_209 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_223 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_225 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_230 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_231 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. None to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_294 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_REGIONAL_FAULT_003 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_REGIONAL_FAULT_019 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_REGIONAL_FAULT_033 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_REGIONAL_FAULT_040 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to non-convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_067 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power Oscillations are oberserved at the Grand Prairie Wind Farm (645065, 645066, 645067 and 645068) following the fault and the units are tripped due to internal protection before reaching the 10 second post-fault time mark. The issue is resolved when the critical clearing time is reduced to 3 cycles. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_346 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | The Laramie generating site (659118) loses synchronism after the fault. The issue is resolved when the critical clearing time is reduced to 4 cycles. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_067 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Power Oscillations are oberserved at the Grand Prairie Wind Farm (645065, 645066, 645067 and 645068) following the fault and the units are tripped due to internal protection before reaching the 10 second post-fault time mark. The issue is resolved when the critical clearing time is reduced to 3 cycles. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_346 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes | The Laramie generating site (659118) loses synchronism after the fault. The issue is resolved when the critical clearing time is reduced to 4 cycles. | No mitigation required.
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25S | Base | GROUP2_P1_LOCAL_FAULT_319 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Post fault steady state voltages at STERLNG7 (640362), FIRTH 7 (640171), GEN-2013-019 (583700), GEN-2019-041 (763725), G13-002-TAP (560746), and MONOLITH 7 (640591) do not recover above 0.9 p.u. Stable response observed after the upgrade is in-service. | Multi - Sheldon - Monolith 115 kV
02 NEBRASKA | DISIS-2018-002 / DISIS-2019-001-CF | 25W | Base | GROUP2_P1_LOCAL_FAULT_319 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Post fault steady state voltages at STERLNG7 (640362), FIRTH 7 (640171), GEN-2013-019 (583700), GEN-2019-041 (763725), G13-002-TAP (560746), and MONOLITH 7 (640591) do not recover above 0.9 p.u. Stable response observed after the upgrade is in-service. | Multi - Sheldon - Monolith 115 kV
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512753_TONNEC2-512745_SSLINC2_Ckt1 | 3 Phase fault on TONNEC2 (512753) 69.0 kV a. Apply fault on TONNEC2 (512753) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONNEC2 (512753) 69.0 bus to TONECESTR2 (512756) 69.0 bus CKT 1 b. 2. Trip branch from TONECESTR2 (512756) 69.0 bus to ARKLIN2 (512728) 69.0 bus CKT 1 b. 3. Trip branch from ARKLIN2 (512728) 69.0 bus to SSNEWN2 (512747) 69.0 bus CKT 1 b. 4. Trip branch from SSNEWN2 (512747) 69.0 bus to SSNORT2 (512746) 69.0 bus CKT 1 b. 5. Drop load from bus SSNORT2 (512746) 69.0 kV bus b. 6. Drop load from bus SSLINC2 (512745) 69.0 kV bus b. 7. Trip branch from SSNORT2 (512746) 69.0 bus to SSLINC2 (512745) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONNEC2 (512753) 69.0 bus to TONECESTR2 (512756) 69.0 bus CKT 1 c. 2. Reclose branch from TONECESTR2 (512756) 69.0 bus to ARKLIN2 (512728) 69.0 bus CKT 1 c. 3. Reclose branch from ARKLIN2 (512728) 69.0 bus to SSNEWN2 (512747) 69.0 bus CKT 1 c. 4. Reclose branch from SSNEWN2 (512747) 69.0 bus to SSNORT2 (512746) 69.0 bus CKT 1 c. 5. Reclose branch from SSNORT2 (512746) 69.0 bus to SSLINC2 (512745) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONNEC2 (512753) 69.0 bus to TONECESTR2 (512756) 69.0 bus CKT 1 d. 2. Trip branch from TONECESTR2 (512756) 69.0 bus to ARKLIN2 (512728) 69.0 bus CKT 1 d. 3. Trip branch from ARKLIN2 (512728) 69.0 bus to SSNEWN2 (512747) 69.0 bus CKT 1 d. 4. Trip branch from SSNEWN2 (512747) 69.0 bus to SSNORT2 (512746) 69.0 bus CKT 1 d. 5. Trip branch from SSNORT2 (512746) 69.0 bus to SSLINC2 (512745) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512753_TONNEC2-512751_TONECE5_3Winding | 3 Phase fault on TONNEC2 (512753) 69.0 kV a. Apply fault on TONNEC2 (512753) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONNEC1 (512754) to trip transformer at TONNEC1 13.200 (512754) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512751_TONECE5-512643_SILMCTY5_Ckt1 | 3 Phase fault on TONECE5 (512751) 161.0 kV a. Apply fault on TONECE5 (512751) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512751_TONECE5-512750_TONECE7_3Winding | 3 Phase fault on TONECE5 (512751) 161.0 kV a. Apply fault on TONECE5 (512751) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONECE1 (512752) to trip transformer at TONECE1 13.200 (512752) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512751_TONECE5-512753_TONNEC2_3Winding | 3 Phase fault on TONECE5 (512751) 161.0 kV a. Apply fault on TONECE5 (512751) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONNEC1 (512754) to trip transformer at TONNEC1 13.200 (512754) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512750_TONECE7-512650_GRDA1_Ckt1 | 3 Phase fault on TONECE7 (512750) 345.0 kV a. Apply fault on TONECE7 (512750) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512750_TONECE7-506935_FLINTCR7_Ckt1 | 3 Phase fault on TONECE7 (512750) 345.0 kV a. Apply fault on TONECE7 (512750) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512750_TONECE7-512751_TONECE5_3Winding | 3 Phase fault on TONECE7 (512750) 345.0 kV a. Apply fault on TONECE7 (512750) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TONECE1 (512752) to trip transformer at TONECE1 13.200 (512752) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506935_FLINTCR7-506929_ECNTRTN5_3Winding | 3 Phase fault on FLINTCR7 (506935) 345.0 kV a. Apply fault on FLINTCR7 (506935) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345.0 bus to SHIPERD7 (506979) 345.0 bus CKT 1 b. 2. Disconnect bus at SHIPERD1 (506981) to trip transformer at SHIPERD1 13.8 kV bus b. 3. Trip branch from SHIPERD5 (506980) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 b. 4. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 5. Trip branch from CENTRTN5 (506952) 161.0 bus to ECNTRTN5 (506929) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR7 (506935) 345.0 bus to SHIPERD7 (506979) 345.0 bus CKT 1 c. 2. Reclose branch from SHIPERD5 (506980) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 c. 3. Reclose branch from CENTRTN5 (506952) 161.0 bus to ECNTRTN5 (506929) 161.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR7 (506935) 345.0 bus to SHIPERD7 (506979) 345.0 bus CKT 1 d. 2. Trip branch from SHIPERD5 (506980) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 d. 3. Trip branch from CENTRTN5 (506952) 161.0 bus to ECNTRTN5 (506929) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506935_FLINTCR7-549984_BROOKLINE_Ckt1 | 3 Phase fault on FLINTCR7 (506935) 345.0 kV a. Apply fault on FLINTCR7 (506935) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506935_FLINTCR7-506934_FLINTCR5_3Winding | 3 Phase fault on FLINTCR7 (506935) 345.0 kV a. Apply fault on FLINTCR7 (506935) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at FLINT2-1 (506920) to trip transformer at FLINT2-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512643_SILMCTY5-506948_SILOAM_Ckt1 | 3 Phase fault on SILMCTY5 (512643) 161.0 kV a. Apply fault on SILMCTY5 (512643) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512643_SILMCTY5-512714_KANSATP5_Ckt1 | 3 Phase fault on SILMCTY5 (512643) 161.0 kV a. Apply fault on SILMCTY5 (512643) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 b. 2. Drop load from bus SILSPWW5 (512642) 161.0 kV bus b. 3. Trip branch from SILSPWW5 (512642) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY5 (512643) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 c. 2. Reclose branch from SILSPWW5 (512642) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY5 (512643) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 d. 2. Trip branch from SILSPWW5 (512642) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512643_SILMCTY5-512820_SILMCTY2_3Winding | 3 Phase fault on SILMCTY5 (512643) 161.0 kV a. Apply fault on SILMCTY5 (512643) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SLMCTY2 (512850) to trip transformer at SLMCTY2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512650_GRDA1-300740_7SPORTSMAN_Ckt1 | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512650_GRDA1-512865_GREC_Ckt1 | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512650_GRDA1-512656_GRDA1_3Winding | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at GRDA1 (512821) to trip transformer at GRDA1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_549984_BROOKLINE-300045_7MORGAN_Ckt1 | 3 Phase fault on BROOKLINE (549984) 345.0 kV a. Apply fault on BROOKLINE (549984) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_549984_BROOKLINE-549969_BROOKLINE_3Winding | 3 Phase fault on BROOKLINE (549984) 345.0 kV a. Apply fault on BROOKLINE (549984) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at BRKLNE (549989) to trip transformer at BRKLNE XF2 113.200 (549989) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506934_FLINTCR5-506990_GREENHOUSE_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 b. 2. Drop load from bus GENTRY (504201) 161.0 kV bus b. 3. Trip branch from GENTRY (504201) 161.0 bus to BEN279_5 (506960) 161.0 bus CKT 1 b. 4. Drop load from bus BEN279_5 (506960) 161.0 kV bus b. 5. Drop load from bus GREENHOUSE (506990) 161.0 kV bus b. 6. Trip branch from BEN279_5 (506960) 161.0 bus to GREENHOUSE (506990) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 c. 2. Reclose branch from GENTRY (504201) 161.0 bus to BEN279_5 (506960) 161.0 bus CKT 1 c. 3. Reclose branch from BEN279_5 (506960) 161.0 bus to GREENHOUSE (506990) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 d. 2. Trip branch from GENTRY (504201) 161.0 bus to BEN279_5 (506960) 161.0 bus CKT 1 d. 3. Trip branch from BEN279_5 (506960) 161.0 bus to GREENHOUSE (506990) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506934_FLINTCR5-506957_TONTITN5_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506934_FLINTCR5-547484_DEC392_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to DEC392 (547484) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 kV bus to DEC392 (547484) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to DEC392 (547484) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506934_FLINTCR5-504202_SILOAMSP_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SILOAMSP (504202) 161.0 kV bus b. 2. Trip branch from FLINTCR5 (506934) 161.0 bus to SILOAMSP (504202) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 bus to SILOAMSP (504202) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to SILOAMSP (504202) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506934_FLINTCR5-506935_FLINTCR7_3Winding | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at FLINT2-1 (506920) to trip transformer at FLINT2-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506934_FLINTCR5-506948_SILOAM_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506948_SILOAM-506944_CHAMSPR5_Ckt1 | 3 Phase fault on SILOAM (506948) 161.0 kV a. Apply fault on SILOAM (506948) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506948_SILOAM-506936_GREENLD2_3Winding | 3 Phase fault on SILOAM (506948) 161.0 kV a. Apply fault on SILOAM (506948) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SILOAM-1 (506917) to trip transformer at SILOAM-1 13.200 (506917) 13.2 kV bus b. 2. Drop switching device from bus SILOAM (506973) 69.0 kV bus b. 3. Trip branch from SILOAM (506973) 69.0 bus to LINCOLN2 (506972) 69.0 bus CKT 1 b. 4. Drop load from bus LINCOLN2 (506972) 69.0 kV bus b. 5. Trip branch from LINCOLN2 (506972) 69.0 bus to PRGROVE2 (506941) 69.0 bus CKT 1 b. 6. Drop load from bus PRGROVE2 (506941) 69.0 kV bus b. 7. Trip branch from PRGROVE2 (506941) 69.0 bus to GREENLD2 (506936) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILOAM (506973) 69.0 bus to LINCOLN2 (506972) 69.0 bus CKT 1 c. 2. Reclose branch from LINCOLN2 (506972) 69.0 bus to PRGROVE2 (506941) 69.0 bus CKT 1 c. 3. Reclose branch from PRGROVE2 (506941) 69.0 bus to GREENLD2 (506936) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILOAM (506973) 69.0 bus to LINCOLN2 (506972) 69.0 bus CKT 1 d. 2. Trip branch from LINCOLN2 (506972) 69.0 bus to PRGROVE2 (506941) 69.0 bus CKT 1 d. 3. Trip branch from PRGROVE2 (506941) 69.0 bus to GREENLD2 (506936) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512820_SILMCTY2-512730_SSSWES2_Ckt1 | 3 Phase fault on SILMCTY2 (512820) 69.0 kV a. Apply fault on SILMCTY2 (512820) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SSSWES2 (512730) 69.0 kV bus b. 2. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWES2 (512730) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY2 (512820) 69.0 bus to SSSWES2 (512730) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWES2 (512730) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512820_SILMCTY2-512643_SILMCTY5_3Winding | 3 Phase fault on SILMCTY2 (512820) 69.0 kV a. Apply fault on SILMCTY2 (512820) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SLMCTY2 (512850) to trip transformer at SLMCTY2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512820_SILMCTY2-512744_SSMOSS2_Ckt1 | 3 Phase fault on SILMCTY2 (512820) 69.0 kV a. Apply fault on SILMCTY2 (512820) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWTP2 (512737) 69.0 bus CKT 1 b. 2. Drop load from bus SSMOSS2 (512744) 69.0 kV bus b. 3. Trip branch from SSSWTP2 (512737) 69.0 bus to SSMOSS2 (512744) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY2 (512820) 69.0 bus to SSSWTP2 (512737) 69.0 bus CKT 1 c. 2. Reclose branch from SSSWTP2 (512737) 69.0 bus to SSMOSS2 (512744) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWTP2 (512737) 69.0 bus CKT 1 d. 2. Trip branch from SSSWTP2 (512737) 69.0 bus to SSMOSS2 (512744) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_300740_7SPORTSMAN-300741_5SPORTSMAN_Ckt1 | 3 Phase fault on 7SPORTSMAN (300740) 345.0 kV a. Apply fault on 7SPORTSMAN (300740) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_300740_7SPORTSMAN-300741_5SPORTSMAN_Ckt2 | 3 Phase fault on 7SPORTSMAN (300740) 345.0 kV a. Apply fault on 7SPORTSMAN (300740) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_300740_7SPORTSMAN-300739_7BLACKBERRY_Ckt1 | 3 Phase fault on 7SPORTSMAN (300740) 345.0 kV a. Apply fault on 7SPORTSMAN (300740) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SPORTSMAN (300740) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512865_GREC-513596_IGLOOV_Ckt1 | 3 Phase fault on GREC (512865) 345.0 kV a. Apply fault on GREC (512865) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512656_GRDA1-512742_WMAIN_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus WMAIN (512742) 161.0 kV bus b. 2. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512656_GRDA1-512650_GRDA1_3Winding | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at GRDA1 (512821) to trip transformer at GRDA1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_300045_7MORGAN-300949_7JASPER_Ckt1 | 3 Phase fault on 7MORGAN (300045) 345.0 kV a. Apply fault on 7MORGAN (300045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_549969_BROOKLINE-505492_SPRGFLD5_Ckt1 | 3 Phase fault on BROOKLINE (549969) 161.0 kV a. Apply fault on BROOKLINE (549969) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_549969_BROOKLINE-549955_JUNCTION_Ckt1 | 3 Phase fault on BROOKLINE (549969) 161.0 kV a. Apply fault on BROOKLINE (549969) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506957_TONTITN5-504010_ELMSPRGS_Ckt1 | 3 Phase fault on TONTITN5 (506957) 161.0 kV a. Apply fault on TONTITN5 (506957) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506957_TONTITN5-506945_CHAMSPR7_3Winding | 3 Phase fault on TONTITN5 (506957) 161.0 kV a. Apply fault on TONTITN5 (506957) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONTITN1 (506958) to trip transformer at TONTITN1 13.8 kV bus b. 2. Trip branch from TONTITN7 (506959) 345.0 bus to CHAMSPR7 (506945) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONTITN7 (506959) 345.0 bus to CHAMSPR7 (506945) 345.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONTITN7 (506959) 345.0 bus to CHAMSPR7 (506945) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506944_CHAMSPR5-506992_WEDINGTON_Ckt1 | 3 Phase fault on CHAMSPR5 (506944) 161.0 kV a. Apply fault on CHAMSPR5 (506944) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506944_CHAMSPR5-506945_CHAMSPR7_3Winding | 3 Phase fault on CHAMSPR5 (506944) 161.0 kV a. Apply fault on CHAMSPR5 (506944) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CHAMSPR1 (506919) to trip transformer at CHAMSPR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512714_KANSATP5-512635_KERR_Ckt1 | 3 Phase fault on KANSATP5 (512714) 161.0 kV a. Apply fault on KANSATP5 (512714) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 b. 2. Drop load from bus 412SUB (512637) 161.0 kV bus b. 3. Trip branch from 412SUB (512637) 161.0 bus to KERR (512635) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KANSATP5 (512714) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 c. 2. Reclose branch from 412SUB (512637) 161.0 bus to KERR (512635) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KANSATP5 (512714) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 d. 2. Trip branch from 412SUB (512637) 161.0 bus to KERR (512635) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512714_KANSATP5-512643_SILMCTY5_Ckt1 | 3 Phase fault on KANSATP5 (512714) 161.0 kV a. Apply fault on KANSATP5 (512714) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 b. 2. Drop load from bus SILSPWW5 (512642) 161.0 kV bus b. 3. Trip branch from SILSPWW5 (512642) 161.0 bus to SILMCTY5 (512643) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KANSATP5 (512714) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 c. 2. Reclose branch from SILSPWW5 (512642) 161.0 bus to SILMCTY5 (512643) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KANSATP5 (512714) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 d. 2. Trip branch from SILSPWW5 (512642) 161.0 bus to SILMCTY5 (512643) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512714_KANSATP5-512715_KANSAS_3Winding | 3 Phase fault on KANSATP5 (512714) 161.0 kV a. Apply fault on KANSATP5 (512714) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161.0 bus to KANSAS (512716) 161.0 bus CKT 1 b. 2. Disconnect bus at KANSAS1 (512736) to trip transformer at KANSAS1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KANSATP5 (512714) 161.0 bus to KANSAS (512716) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KANSATP5 (512714) 161.0 bus to KANSAS (512716) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506929_ECNTRTN5-506935_FLINTCR7_3Winding | 3 Phase fault on ECNTRTN5 (506929) 161.0 kV a. Apply fault on ECNTRTN5 (506929) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN5 (506929) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 b. 2. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 3. Trip branch from CENTRTN5 (506952) 161.0 bus to SHIPERD5 (506980) 161.0 bus CKT 1 b. 4. Disconnect bus at SHIPERD1 (506981) to trip transformer at SHIPERD1 13.8 kV bus b. 5. Drop load from bus ECNTRTN5 (506929) 161.0 kV bus b. 6. Drop load from bus ECNTRTN5 (506929) 161.0 kV bus b. 7. Trip branch from SHIPERD7 (506979) 345.0 bus to FLINTCR7 (506935) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ECNTRTN5 (506929) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 c. 2. Reclose branch from CENTRTN5 (506952) 161.0 bus to SHIPERD5 (506980) 161.0 bus CKT 1 c. 3. Reclose branch from SHIPERD7 (506979) 345.0 bus to FLINTCR7 (506935) 345.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ECNTRTN5 (506929) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 d. 2. Trip branch from CENTRTN5 (506952) 161.0 bus to SHIPERD5 (506980) 161.0 bus CKT 1 d. 3. Trip branch from SHIPERD7 (506979) 345.0 bus to FLINTCR7 (506935) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506929_ECNTRTN5-506963_BENT_SL5_Ckt1 | 3 Phase fault on ECNTRTN5 (506929) 161.0 kV a. Apply fault on ECNTRTN5 (506929) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus BENT_SL5 (506963) 161.0 kV bus b. 2. Trip branch from ECNTRTN5 (506929) 161.0 bus to BENT_SL5 (506963) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ECNTRTN5 (506929) 161.0 bus to BENT_SL5 (506963) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ECNTRTN5 (506929) 161.0 bus to BENT_SL5 (506963) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_513596_IGLOOV-513591_HERRON_3Winding | 3 Phase fault on IGLOOV (513596) 345.0 kV a. Apply fault on IGLOOV (513596) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at IGLOTER2 (513594) to trip transformer at IGLOTER2 1 13.200 (513594) 13.2 kV bus b. 2. Trip branch from IGLOOV2 (513595) 161.0 bus to HERRON (513591) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from IGLOOV2 (513595) 161.0 bus to HERRON (513591) 161.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from IGLOOV2 (513595) 161.0 bus to HERRON (513591) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_513596_IGLOOV-509852_TNO--7_Ckt1 | 3 Phase fault on IGLOOV (513596) 345.0 kV a. Apply fault on IGLOOV (513596) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV (513596) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from IGLOOV (513596) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from IGLOOV (513596) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506945_CHAMSPR7-509745_CLARKSV7_Ckt1 | 3 Phase fault on CHAMSPR7 (506945) 345.0 kV a. Apply fault on CHAMSPR7 (506945) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506945_CHAMSPR7-506957_TONTITN5_3Winding | 3 Phase fault on CHAMSPR7 (506945) 345.0 kV a. Apply fault on CHAMSPR7 (506945) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR7 (506945) 345.0 bus to TONTITN7 (506959) 345.0 bus CKT 1 b. 2. Disconnect bus at TONTITN1 (506958) to trip transformer at TONTITN1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHAMSPR7 (506945) 345.0 bus to TONTITN7 (506959) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHAMSPR7 (506945) 345.0 bus to TONTITN7 (506959) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506945_CHAMSPR7-506944_CHAMSPR5_3Winding | 3 Phase fault on CHAMSPR7 (506945) 345.0 kV a. Apply fault on CHAMSPR7 (506945) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CHAMSPR1 (506919) to trip transformer at CHAMSPR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512751_TONECE5 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a. Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 b. 2. Disconnect TONECE1 (512752) 13.2 kV bus to trip transformer at TONECE1 13.200 (512752) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512750_TONECE7 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345.0 kV bus a. Apply single-phase fault on TONECE7 (512750) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 b. 2. Trip branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-506935_FLINTCR7 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Trip branch from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 3. Disconnect SHIPERD1 (506981) 13.8 kV bus to trip transformer at SHIPERD1 13.8 kV bus b. 4. Trip branch from SHIPERD5 (506980) 161.0 kV bus to CENTRTN5 (506952) 161.0 kV bus CKT 1 b. 5. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 6. Trip branch from CENTRTN5 (506952) 161.0 kV bus to ECNTRTN5 (506929) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512643_SILMCTY5 | Single Phase Fault with Stuck Breaker on SILMCTY5 (512643) 161.0 kV bus a. Apply single-phase fault on SILMCTY5 (512643) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 b. 2. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILSPWW5 (512642) 161.0 kV bus CKT 1 b. 3. Drop load from bus SILSPWW5 (512642) 161.0 kV bus b. 4. Trip branch from SILSPWW5 (512642) 161.0 kV bus to KANSATP5 (512714) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512650_GRDA1 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a. Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Trip branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-549984_BROOKLINE | Single Phase Fault with Stuck Breaker on BROOKLINE (549984) 345.0 kV bus a. Apply single-phase fault on BROOKLINE (549984) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 b. 2. Disconnect BRKLNE (549988) 13.2 kV bus to trip transformer at BRKLNE XF1 113.200 (549988) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-506934_FLINTCR5 | Single Phase Fault with Stuck Breaker on FLINTCR5 (506934) 161.0 kV bus a. Apply single-phase fault on FLINTCR5 (506934) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus GENTRY (504201) 161.0 kV bus b. 2. Trip branch from FLINTCR5 (506934) 161.0 kV bus to GENTRY (504201) 161.0 kV bus CKT 1 b. 3. Trip branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-506948_SILOAM | Single Phase Fault with Stuck Breaker on SILOAM (506948) 161.0 kV bus a. Apply single-phase fault on SILOAM (506948) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 b. 2. Trip branch from SILOAM (506948) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512656_GRDA1 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 b. 2. Drop load from bus WMAIN (512742) 161.0 kV bus b. 3. Trip branch from WMAIN (512742) 161.0 kV bus to NWMAID5 (512757) 161.0 kV bus CKT 1 b. 4. Drop load from bus NWMAID5 (512757) 161.0 kV bus b. 5. Trip branch from NWMAID5 (512757) 161.0 kV bus to GERALDGAY5 (512760) 161.0 kV bus CKT 1 b. 6. Drop load from bus GERALDGAY5 (512760) 161.0 kV bus b. 7. Trip branch from GERALDGAY5 (512760) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 8. Disconnect GRDA2 (512826) 13.8 kV bus to trip transformer at GRDA2 1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-300045_7MORGAN | Single Phase Fault with Stuck Breaker on 7MORGAN (300045) 345.0 kV bus a. Apply single-phase fault on 7MORGAN (300045) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 b. 2. Trip branch from 7MORGAN (300045) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-549969_BROOKLINE | Single Phase Fault with Stuck Breaker on BROOKLINE (549969) 161.0 kV bus a. Apply single-phase fault on BROOKLINE (549969) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 b. 2. Trip branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-506957_TONTITN5 | Single Phase Fault with Stuck Breaker on TONTITN5 (506957) 161.0 kV bus a. Apply single-phase fault on TONTITN5 (506957) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 b. 2. Disconnect TONTITN1 (506958) 13.8 kV bus to trip transformer at TONTITN1 13.8 kV bus b. 3. Trip branch from TONTITN7 (506959) 345.0 kV bus to CHAMSPR7 (506945) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-506944_CHAMSPR5 | Single Phase Fault with Stuck Breaker on CHAMSPR5 (506944) 161.0 kV bus a. Apply single-phase fault on CHAMSPR5 (506944) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 b. 2. Disconnect CHAMSPR1 (506919) 13.8 kV bus to trip transformer at CHAMSPR1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-514803_SOONER | Single Phase Fault with Stuck Breaker on SOONER (514803) 345.0 kV bus a. Apply single-phase fault on SOONER (514803) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 b. 2. Trip branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-506929_ECNTRTN5 | Single Phase Fault with Stuck Breaker on ECNTRTN5 (506929) 161.0 kV bus a. Apply single-phase fault on ECNTRTN5 (506929) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN5 (506929) 161.0 kV bus to CENTRTN5 (506952) 161.0 kV bus CKT 1 b. 2. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 3. Trip branch from CENTRTN5 (506952) 161.0 kV bus to SHIPERD5 (506980) 161.0 kV bus CKT 1 b. 4. Disconnect SHIPERD1 (506981) 13.8 kV bus to trip transformer at SHIPERD1 13.8 kV bus b. 5. Trip branch from SHIPERD7 (506979) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 b. 6. Drop load from bus BENT_SL5 (506963) 161.0 kV bus b. 7. Trip branch from ECNTRTN5 (506929) 161.0 kV bus to BENT_SL5 (506963) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515576_RANCHRD7-515621_OPENSKY7_Ckt1 | 3 Phase fault on RANCHRD7 (515576) 345.0 kV a. Apply fault on RANCHRD7 (515576) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515576_RANCHRD7-514803_SOONER_Ckt1 | 3 Phase fault on RANCHRD7 (515576) 345.0 kV a. Apply fault on RANCHRD7 (515576) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from RANCHRD7 (515576) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514803_SOONER-560056_G15-066T_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514803_SOONER-509755_WEKIWA-7_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514803_SOONER-516010_PINTAIL7_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to PINTAIL7 (516010) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to PINTAIL7 (516010) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to PINTAIL7 (516010) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514803_SOONER-514802_SOONER_3Winding | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SOONER (515760) to trip transformer at SOONER 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514803_SOONER-587804_G16-119-TAP_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to G16-119-TAP (587804) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to G16-119-TAP (587804) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to G16-119-TAP (587804) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515621_OPENSKY7-560053_G15-052T_Ckt1 | 3 Phase fault on OPENSKY7 (515621) 345.0 kV a. Apply fault on OPENSKY7 (515621) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509755_WEKIWA-7-509757_WEKIWA-4_3Winding | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at WEKIW1-1 (509879) to trip transformer at WEKIW1-1 34.500 (509879) 34.5 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509755_WEKIWA-7-509870_SAPLPRD7_Ckt1 | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509755_WEKIWA-7-509852_TNO--7_Ckt1 | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_560056_G15-066T-512694_CLEVLND7_Ckt1 | 3 Phase fault on G15-066T (560056) 345.0 kV a. Apply fault on G15-066T (560056) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-066T (560056) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G15-066T (560056) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G15-066T (560056) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514802_SOONER-514798_SNRPMPT4_Ckt1 | 3 Phase fault on SOONER (514802) 138.0 kV a. Apply fault on SOONER (514802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514802_SOONER-514704_MILLERT4_Ckt1 | 3 Phase fault on SOONER (514802) 138.0 kV a. Apply fault on SOONER (514802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_560053_G15-052T-532794_ROSEHIL7_Ckt1 | 3 Phase fault on G15-052T (560053) 345.0 kV a. Apply fault on G15-052T (560053) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-052T (560053) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G15-052T (560053) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G15-052T (560053) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-514802_SOONER | Single Phase Fault with Stuck Breaker on SOONER (514802) 138.0 kV bus a. Apply single-phase fault on SOONER (514802) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 b. 2. Trip branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_763113_G18-079-TAP-512734_FARML_Ckt1 | 3 Phase fault on G18-079-TAP (763113) 138.0 kV a. Apply fault on G18-079-TAP (763113) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G18-079-TAP (763113) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G18-079-TAP (763113) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_763113_G18-079-TAP-510380_DELWARE7_3Winding | 3 Phase fault on G18-079-TAP (763113) 138.0 kV a. Apply fault on G18-079-TAP (763113) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138.0 bus to DELWARE4 (510379) 138.0 bus CKT 1 b. 2. Disconnect bus at DELAWAR1 (510370) to trip transformer at DELAWAR1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G18-079-TAP (763113) 138.0 bus to DELWARE4 (510379) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G18-079-TAP (763113) 138.0 bus to DELWARE4 (510379) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512734_FARML-510378_SCOFCTY4_Ckt1 | 3 Phase fault on FARML (512734) 138.0 kV a. Apply fault on FARML (512734) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FARML (512734) 138.0 kV bus to SCOFCTY4 (510378) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FARML (512734) 138.0 kV bus to SCOFCTY4 (510378) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FARML (512734) 138.0 kV bus to SCOFCTY4 (510378) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510380_DELWARE7-510406_NES-7_Ckt1 | 3 Phase fault on DELWARE7 (510380) 345.0 kV a. Apply fault on DELWARE7 (510380) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510380_DELWARE7-532793_NEOSHO_Ckt1 | 3 Phase fault on DELWARE7 (510380) 345.0 kV a. Apply fault on DELWARE7 (510380) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510380_DELWARE7-763113_G18-079-TAP_3Winding | 3 Phase fault on DELWARE7 (510380) 345.0 kV a. Apply fault on DELWARE7 (510380) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at DELAWAR1 (510370) to trip transformer at DELAWAR1 13.8 kV bus b. 2. Trip branch from DELWARE4 (510379) 138.0 bus to G18-079-TAP (763113) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DELWARE4 (510379) 138.0 bus to G18-079-TAP (763113) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DELWARE4 (510379) 138.0 bus to G18-079-TAP (763113) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510378_SCOFCTY4-510422_COFFEYT4_Ckt1 | 3 Phase fault on SCOFCTY4 (510378) 138.0 kV a. Apply fault on SCOFCTY4 (510378) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510378_SCOFCTY4-510420_SCOFFEYV4_Ckt1 | 3 Phase fault on SCOFCTY4 (510378) 138.0 kV a. Apply fault on SCOFCTY4 (510378) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SCOFFEYV4 (510420) 138.0 kV bus b. 2. Trip branch from SCOFCTY4 (510378) 138.0 bus to SCOFFEYV4 (510420) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SCOFCTY4 (510378) 138.0 bus to SCOFFEYV4 (510420) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SCOFCTY4 (510378) 138.0 bus to SCOFFEYV4 (510420) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510406_NES-7-509852_TNO--7_Ckt1 | 3 Phase fault on N.E.S.-7 (510406) 345.0 kV a. Apply fault on N.E.S.-7 (510406) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510406_NES-7-509807_ONETA--7_Ckt1 | 3 Phase fault on N.E.S.-7 (510406) 345.0 kV a. Apply fault on N.E.S.-7 (510406) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from N.E.S.-7 (510406) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_532793_NEOSHO-532937_NEOSHO_3Winding | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532825) to trip transformer at N345 2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_532793_NEOSHO-542981_LACYGNE7_Ckt1 | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_532793_NEOSHO-533021_NEOSHO_3Winding | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532824) to trip transformer at N345 1 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_532793_NEOSHO-532777_G17-009-TAP_Ckt1 | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to G17-009-TAP (532777) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532793) 345.0 kV bus to G17-009-TAP (532777) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to G17-009-TAP (532777) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_532793_NEOSHO-300739_7BLACKBERRY_Ckt1 | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532793) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510422_COFFEYT4-533002_DEARING4_Ckt1 | 3 Phase fault on COFFEYT4 (510422) 138.0 kV a. Apply fault on COFFEYT4 (510422) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138.0 kV bus to DEARING4 (533002) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from COFFEYT4 (510422) 138.0 kV bus to DEARING4 (533002) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from COFFEYT4 (510422) 138.0 kV bus to DEARING4 (533002) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510422_COFFEYT4-510391_BV-SE--4_Ckt1 | 3 Phase fault on COFFEYT4 (510422) 138.0 kV a. Apply fault on COFFEYT4 (510422) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138.0 bus to NBVILLE4 (510386) 138.0 bus CKT 1 b. 2. Drop load from bus NBVILLE4 (510386) 138.0 kV bus b. 3. Trip branch from NBVILLE4 (510386) 138.0 bus to BV-SE--4 (510391) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from COFFEYT4 (510422) 138.0 bus to NBVILLE4 (510386) 138.0 bus CKT 1 c. 2. Reclose branch from NBVILLE4 (510386) 138.0 bus to BV-SE--4 (510391) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from COFFEYT4 (510422) 138.0 bus to NBVILLE4 (510386) 138.0 bus CKT 1 d. 2. Trip branch from NBVILLE4 (510386) 138.0 bus to BV-SE--4 (510391) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509807_ONETA--7-509836_OEC_Ckt2 | 3 Phase fault on ONETA--7 (509807) 345.0 kV a. Apply fault on ONETA--7 (509807) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509807_ONETA--7-509836_OEC_Ckt1 | 3 Phase fault on ONETA--7 (509807) 345.0 kV a. Apply fault on ONETA--7 (509807) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509852_TNO--7-509895_TNO2-4_3Winding | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TNO2-1 (509894) to trip transformer at TNO2-1 34.500 (509894) 34.5 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_542981_LACYGNE7-542968_STILWEL7_Ckt1 | 3 Phase fault on LACYGNE7 (542981) 345.0 kV a. Apply fault on LACYGNE7 (542981) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_542981_LACYGNE7-542965_WGRDNR7_Ckt1 | 3 Phase fault on LACYGNE7 (542981) 345.0 kV a. Apply fault on LACYGNE7 (542981) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_533021_NEOSHO-532793_NEOSHO_3Winding | 3 Phase fault on NEOSHO (533021) 138.0 kV a. Apply fault on NEOSHO (533021) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532824) to trip transformer at N345 1 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_533021_NEOSHO-533022_NEOSHON4_CktZ1 | 3 Phase fault on NEOSHO (533021) 138.0 kV a. Apply fault on NEOSHO (533021) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_532937_NEOSHO-532793_NEOSHO_3Winding | 3 Phase fault on NEOSHO (532937) 161.0 kV a. Apply fault on NEOSHO (532937) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532825) to trip transformer at N345 2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_532937_NEOSHO-547469_RIV4525_Ckt1 | 3 Phase fault on NEOSHO (532937) 161.0 kV a. Apply fault on NEOSHO (532937) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_533020_NEOSHOS4-532937_NEOSHO_3Winding | 3 Phase fault on NEOSHOS4 (533020) 138.0 kV a. Apply fault on NEOSHOS4 (533020) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEOSH5 (532959) to trip transformer at NEOSH5 1 13.200 (532959) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_533020_NEOSHOS4-533003_LIBERTY4_Ckt1 | 3 Phase fault on NEOSHOS4 (533020) 138.0 kV a. Apply fault on NEOSHOS4 (533020) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS4 (533020) 138.0 bus to TV1MNDV4 (533008) 138.0 bus CKT 1 b. 2. Drop load from bus TV1MNDV4 (533008) 138.0 kV bus b. 3. Trip branch from TV1MNDV4 (533008) 138.0 bus to LIBERTY4 (533003) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHOS4 (533020) 138.0 bus to TV1MNDV4 (533008) 138.0 bus CKT 1 c. 2. Reclose branch from TV1MNDV4 (533008) 138.0 bus to LIBERTY4 (533003) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHOS4 (533020) 138.0 bus to TV1MNDV4 (533008) 138.0 bus CKT 1 d. 2. Trip branch from TV1MNDV4 (533008) 138.0 bus to LIBERTY4 (533003) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_533020_NEOSHOS4-533021_NEOSHO_CktZ1 | 3 Phase fault on NEOSHOS4 (533020) 138.0 kV a. Apply fault on NEOSHOS4 (533020) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS4 (533020) 138.0 kV bus to NEOSHO (533021) 138.0 kV bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHOS4 (533020) 138.0 kV bus to NEOSHO (533021) 138.0 kV bus CKT Z1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHOS4 (533020) 138.0 kV bus to NEOSHO (533021) 138.0 kV bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_533022_NEOSHON4-588664_G17-022-TAP_Ckt1 | 3 Phase fault on NEOSHON4 (533022) 138.0 kV a. Apply fault on NEOSHON4 (533022) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHON4 (533022) 138.0 bus to NEPARSN4 (533005) 138.0 bus CKT 1 b. 2. Drop load from bus NEPARSN4 (533005) 138.0 kV bus b. 3. Drop load from bus NEPARSN4 (533005) 138.0 kV bus b. 4. Drop load from bus NEPARSN4 (533005) 138.0 kV bus b. 5. Drop switching device from bus NEPARSN4 (533005) 138.0 kV bus b. 6. Trip branch from NEPARSN4 (533005) 138.0 bus to G17-022-TAP (588664) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHON4 (533022) 138.0 bus to NEPARSN4 (533005) 138.0 bus CKT 1 c. 2. Reclose branch from NEPARSN4 (533005) 138.0 bus to G17-022-TAP (588664) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHON4 (533022) 138.0 bus to NEPARSN4 (533005) 138.0 bus CKT 1 d. 2. Trip branch from NEPARSN4 (533005) 138.0 bus to G17-022-TAP (588664) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_533022_NEOSHON4-533768_NEOSHON2_3Winding | 3 Phase fault on NEOSHON4 (533022) 138.0 kV a. Apply fault on NEOSHON4 (533022) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEC (532711) to trip transformer at NEC U3 12.000 (532711) 12.0 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-510380_DELWARE7 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-510378_SCOFCTY4 | Single Phase Fault with Stuck Breaker on SCOFCTY4 (510378) 138.0 kV bus a. Apply single-phase fault on SCOFCTY4 (510378) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 b. 2. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-510406_NES-7 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 b. 2. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-532793_NEOSHO | Single Phase Fault with Stuck Breaker on NEOSHO (532793) 345.0 kV bus a. Apply single-phase fault on NEOSHO (532793) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect N345 (532825) 13.8 kV bus to trip transformer at N345 2 1 13.8 kV bus b. 2. Trip branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-509807_ONETA--7 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 b. 2. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-509852_TNO--7 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect TNO2-1 (509894) 34.5 kV bus to trip transformer at TNO2-1 34.500 (509894) 34.5 kV bus b. 2. Trip branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-542981_LACYGNE7 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a. Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 2. Trip branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-533021_NEOSHO | Single Phase Fault with Stuck Breaker on NEOSHO (533021) 138.0 kV bus a. Apply single-phase fault on NEOSHO (533021) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect N345 (532824) 13.8 kV bus to trip transformer at N345 1 1 13.8 kV bus b. 2. Trip branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-532937_NEOSHO | Single Phase Fault with Stuck Breaker on NEOSHO (532937) 161.0 kV bus a. Apply single-phase fault on NEOSHO (532937) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect N345 (532825) 13.8 kV bus to trip transformer at N345 2 1 13.8 kV bus b. 2. Trip branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510907_PITTSB-7-514809_JOHNCO_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510907_PITTSB-7-515045_SEMINOL7_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510907_PITTSB-7-515422_C-RIVER7_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510907_PITTSB-7-510911_VALIANT7_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510911_VALIANT7-508298_LYDIA_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510911_VALIANT7-510918_VALIANT4_3Winding | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at VALN3-1 (510939) to trip transformer at VALN3-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510911_VALIANT7-521157_HUGO_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510911_VALIANT7-508072_NWTXARK7_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514809_JOHNCO-514808_JOHNCO_3Winding | 3 Phase fault on JOHNCO (514809) 345.0 kV a. Apply fault on JOHNCO (514809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at JOHNCO11 (514810) to trip transformer at JOHNCO11 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-510907_PITTSB-7 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 b. 2. Trip branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514809_JOHNCO-515136_SUNNYSD7_Ckt1 | 3 Phase fault on JOHNCO (514809) 345.0 kV a. Apply fault on JOHNCO (514809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514809_JOHNCO-516006_DMNDSPG7_Ckt1 | 3 Phase fault on JOHNCO (514809) 345.0 kV a. Apply fault on JOHNCO (514809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to DMNDSPG7 (516006) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514809) 345.0 kV bus to DMNDSPG7 (516006) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to DMNDSPG7 (516006) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515045_SEMINOL7-514934_DRAPER_Ckt1 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515045_SEMINOL7-514934_DRAPER_Ckt2 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515045_SEMINOL7-515044_SEMINOL4_Ckt3 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 bus to SEMINOL4 (515044) 345.0 bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 bus to SEMINOL4 (515044) 345.0 bus CKT 3 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 bus to SEMINOL4 (515044) 345.0 bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515045_SEMINOL7-515044_SEMINOL4_3Winding | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SEMINO11 (515756) to trip transformer at SEMINO11 14.400 (515756) 14.399999618530273 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515045_SEMINOL7-514934_DRAPER_Ckt3 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 3 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515045_SEMINOL7-588839_FIREWHL-TAP_Ckt1 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515045_SEMINOL7-514908_ARCADIA7_Ckt1 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to ARCADIA7 (514908) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to ARCADIA7 (514908) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to ARCADIA7 (514908) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515422_C-RIVER7-510951_TALAWANDA_3Winding | 3 Phase fault on C-RIVER7 (515422) 345.0 kV a. Apply fault on C-RIVER7 (515422) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at C-RIVER1 (510947) to trip transformer at C-RIVER1 13.8 kV bus b. 2. Trip branch from C-RIVER4 (510946) 138.0 bus to TALAWANDA (510951) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from C-RIVER4 (510946) 138.0 bus to TALAWANDA (510951) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from C-RIVER4 (510946) 138.0 bus to TALAWANDA (510951) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515422_C-RIVER7-588839_FIREWHL-TAP_Ckt1 | 3 Phase fault on C-RIVER7 (515422) 345.0 kV a. Apply fault on C-RIVER7 (515422) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508298_LYDIA-508359_WELSH_Ckt1 | 3 Phase fault on LYDIA (508298) 345.0 kV a. Apply fault on LYDIA (508298) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508298_LYDIA-508072_NWTXARK7_Ckt1 | 3 Phase fault on LYDIA (508298) 345.0 kV a. Apply fault on LYDIA (508298) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LYDIA (508298) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LYDIA (508298) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510918_VALIANT4-510866_V-WEYCO4_Ckt1 | 3 Phase fault on VALIANT4 (510918) 138.0 kV a. Apply fault on VALIANT4 (510918) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus V-WEYCO4 (510866) 138.0 kV bus b. 2. Drop switching device from bus V-WEYCO4 (510866) 138.0 kV bus b. 3. Trip branch from VALIANT4 (510918) 138.0 bus to V-WEYCO4 (510866) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT4 (510918) 138.0 bus to V-WEYCO4 (510866) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT4 (510918) 138.0 bus to V-WEYCO4 (510866) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510918_VALIANT4-520948_HUGO_Ckt1 | 3 Phase fault on VALIANT4 (510918) 138.0 kV a. Apply fault on VALIANT4 (510918) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515136_SUNNYSD7-511568_TERRYRD7_Ckt1 | 3 Phase fault on SUNNYSD7 (515136) 345.0 kV a. Apply fault on SUNNYSD7 (515136) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515136_SUNNYSD7-515135_SUNNYSD4_3Winding | 3 Phase fault on SUNNYSD7 (515136) 345.0 kV a. Apply fault on SUNNYSD7 (515136) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SUNYSD (515405) to trip transformer at SUNYSD 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514808_JOHNCO-514809_JOHNCO_3Winding | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at JOHNCO11 (514810) to trip transformer at JOHNCO11 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514808_JOHNCO-515120_RUSSET-4_Ckt1 | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514808_JOHNCO-515150_CANEYCK4_Ckt1 | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514808_JOHNCO-515122_SXMLCKT4_Ckt1 | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to SXMLCKT4 (515122) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514808) 138.0 kV bus to SXMLCKT4 (515122) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to SXMLCKT4 (515122) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514934_DRAPER-514933_DRAPER_3Winding | 3 Phase fault on DRAPER (514934) 345.0 kV a. Apply fault on DRAPER (514934) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at DRAPER41 (515721) to trip transformer at DRAPER41 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-510911_VALIANT7 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 2. Disconnect VALN2-1 (510938) 13.8 kV bus to trip transformer at VALN2-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-514809_JOHNCO | Single Phase Fault with Stuck Breaker on JOHNCO (514809) 345.0 kV bus a. Apply single-phase fault on JOHNCO (514809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect JOHNCO11 (514810) 13.8 kV bus to trip transformer at JOHNCO11 13.8 kV bus b. 2. Trip branch from JOHNCO (514809) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-515045_SEMINOL7 | Single Phase Fault with Stuck Breaker on SEMINOL7 (515045) 345.0 kV bus a. Apply single-phase fault on SEMINOL7 (515045) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 b. 2. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-515422_C-RIVER7 | Single Phase Fault with Stuck Breaker on C-RIVER7 (515422) 345.0 kV bus a. Apply single-phase fault on C-RIVER7 (515422) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect C-RIVER1 (510947) 13.8 kV bus to trip transformer at C-RIVER1 13.8 kV bus b. 2. Trip branch from C-RIVER4 (510946) 138.0 kV bus to TALAWANDA (510951) 138.0 kV bus CKT 1 b. 3. Trip branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-510918_VALIANT4 | Single Phase Fault with Stuck Breaker on VALIANT4 (510918) 138.0 kV bus a. Apply single-phase fault on VALIANT4 (510918) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus V-WEYCO4 (510866) 138.0 kV bus b. 2. Drop switching device from bus V-WEYCO4 (510866) 138.0 kV bus b. 3. Trip branch from VALIANT4 (510918) 138.0 kV bus to V-WEYCO4 (510866) 138.0 kV bus CKT 1 b. 4. Trip branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-515136_SUNNYSD7 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a. Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 b. 2. Disconnect SUNYSD (515405) 13.8 kV bus to trip transformer at SUNYSD 1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-514934_DRAPER | Single Phase Fault with Stuck Breaker on DRAPER (514934) 345.0 kV bus a. Apply single-phase fault on DRAPER (514934) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect DRAPER31 (515720) 13.8 kV bus to trip transformer at DRAPER31 13.8 kV bus b. 2. Disconnect DRAPER41 (515721) 13.8 kV bus to trip transformer at DRAPER41 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508298_LYDIA-510911_VALIANT7_Ckt1 | 3 Phase fault on LYDIA (508298) 345.0 kV a. Apply fault on LYDIA (508298) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508072_NWTXARK7-507454_TURK_3Winding | 3 Phase fault on NWTXARK7 (508072) 345.0 kV a. Apply fault on NWTXARK7 (508072) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345.0 bus to TURK (507455) 345.0 bus CKT 1 b. 2. Disconnect bus at TURK (507457) to trip transformer at TURK 1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWTXARK7 (508072) 345.0 bus to TURK (507455) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWTXARK7 (508072) 345.0 bus to TURK (507455) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508072_NWTXARK7-508071_NWTXARK4_3Winding | 3 Phase fault on NWTXARK7 (508072) 345.0 kV a. Apply fault on NWTXARK7 (508072) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at NWTEX2-1 (508101) to trip transformer at NWTEX2-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508072_NWTXARK7-508359_WELSH_Ckt1 | 3 Phase fault on NWTXARK7 (508072) 345.0 kV a. Apply fault on NWTXARK7 (508072) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508072_NWTXARK7-510911_VALIANT7_Ckt1 | 3 Phase fault on NWTXARK7 (508072) 345.0 kV a. Apply fault on NWTXARK7 (508072) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508359_WELSH-508832_DIANA_Ckt1 | 3 Phase fault on WELSH (508359) 345.0 kV a. Apply fault on WELSH (508359) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508359_WELSH-508832_DIANA_Ckt2 | 3 Phase fault on WELSH (508359) 345.0 kV a. Apply fault on WELSH (508359) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508359_WELSH-508841_WILKES_Ckt1 | 3 Phase fault on WELSH (508359) 345.0 kV a. Apply fault on WELSH (508359) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508359_WELSH-5917_SPPMAINBUS_Ckt1 | 3 Phase fault on WELSH (508359) 345.0 kV a. Apply fault on WELSH (508359) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to SPPMAINBUS (5917) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WELSH (508359) 345.0 kV bus to SPPMAINBUS (5917) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WELSH (508359) 345.0 kV bus to SPPMAINBUS (5917) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510911_VALIANT7-510907_PITTSB-7_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to PITTSB-7 (510907) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508071_NWTXARK4-508070_NWT-BNT4_Ckt1 | 3 Phase fault on NWTXARK4 (508071) 138.0 kV a. Apply fault on NWTXARK4 (508071) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138.0 kV bus to NWT-BNT4 (508070) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWTXARK4 (508071) 138.0 kV bus to NWT-BNT4 (508070) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWTXARK4 (508071) 138.0 kV bus to NWT-BNT4 (508070) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508071_NWTXARK4-508072_NWTXARK7_3Winding | 3 Phase fault on NWTXARK4 (508071) 138.0 kV a. Apply fault on NWTXARK4 (508071) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NWTEX1-1 (508100) to trip transformer at NWTEX1-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508298_LYDIA | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip branch from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508072_NWTXARK7 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345.0 kV bus to TURK (507455) 345.0 kV bus CKT 1 b. 2. Disconnect TURK (507457) 13.8 kV bus to trip transformer at TURK 1 13.8 kV bus b. 3. Disconnect NWTEX1-1 (508100) 13.8 kV bus to trip transformer at NWTEX1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508359_WELSH | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508071_NWTXARK4 | Single Phase Fault with Stuck Breaker on NWTXARK4 (508071) 138.0 kV bus a. Apply single-phase fault on NWTXARK4 (508071) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138.0 kV bus to NWT-BNT4 (508070) 138.0 kV bus CKT 1 b. 2. Disconnect NWTEX1-1 (508100) 13.8 kV bus to trip transformer at NWTEX1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508832_DIANA | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508809_LONGWD-508808_LONGWD_3Winding | 3 Phase fault on LONGWD (508809) 345.0 kV a. Apply fault on LONGWD (508809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at LONGW1-1 (508819) to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508809_LONGWD-508841_WILKES_Ckt1 | 3 Phase fault on LONGWD (508809) 345.0 kV a. Apply fault on LONGWD (508809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508809_LONGWD-507760_SW_Ckt1 | 3 Phase fault on LONGWD (508809) 345.0 kV a. Apply fault on LONGWD (508809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508809_LONGWD-337376_7SAREPTA%_Ckt1 | 3 Phase fault on LONGWD (508809) 345.0 kV a. Apply fault on LONGWD (508809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508809) 345.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508809) 345.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508809) 345.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337376_7SAREPTA%-337561_8EL_3Winding | 3 Phase fault on 7SAREPTA% (337376) 345.0 kV a. Apply fault on 7SAREPTA% (337376) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SAREPTA% (337376) 345.0 bus to 7EL (337562) 345.0 bus CKT 1 b. 2. Disconnect bus at 1EL (337565) to trip transformer at 1EL DORADO2 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SAREPTA% (337376) 345.0 bus to 7EL (337562) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SAREPTA% (337376) 345.0 bus to 7EL (337562) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337376_7SAREPTA%-337363_3SAREPTA!_Ckt1 | 3 Phase fault on 7SAREPTA% (337376) 345.0 kV a. Apply fault on 7SAREPTA% (337376) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SAREPTA% (337376) 345.0 bus to 3SAREPTA! (337363) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SAREPTA% (337376) 345.0 bus to 3SAREPTA! (337363) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SAREPTA% (337376) 345.0 bus to 3SAREPTA! (337363) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_507760_SW-507759_SW_3Winding | 3 Phase fault on SW (507760) 345.0 kV a. Apply fault on SW (507760) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SWSHV1-1 (507778) to trip transformer at SWSHV1-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_507760_SW-500250_DOLHILL7_Ckt1 | 3 Phase fault on SW (507760) 345.0 kV a. Apply fault on SW (507760) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SW (507760) 345.0 kV bus to DOLHILL7 (500250) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SW (507760) 345.0 kV bus to DOLHILL7 (500250) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SW (507760) 345.0 kV bus to DOLHILL7 (500250) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_507760_SW-508832_DIANA_Ckt1 | 3 Phase fault on SW (507760) 345.0 kV a. Apply fault on SW (507760) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508841_WILKES-508840_WILKES_3Winding | 3 Phase fault on WILKES (508841) 345.0 kV a. Apply fault on WILKES (508841) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at WILKES-1 (508826) to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508841_WILKES-509409_WILKE3-1_Ckt1 | 3 Phase fault on WILKES (508841) 345.0 kV a. Apply fault on WILKES (508841) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop load from bus WILKE3-1 (509409) 22.0 kV bus b. 2. Trip branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508841_WILKES-509409_WILKE3-1_Ckt2 | 3 Phase fault on WILKES (508841) 345.0 kV a. Apply fault on WILKES (508841) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop load from bus WILKE3-1 (509409) 22.0 kV bus b. 2. Trip branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WILKES (508841) 345.0 bus to WILKE3-1 (509409) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508841_WILKES-508359_WELSH_Ckt1 | 3 Phase fault on WILKES (508841) 345.0 kV a. Apply fault on WILKES (508841) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WILKES (508841) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WILKES (508841) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WILKES (508841) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508808_LONGWD-508809_LONGWD_3Winding | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LONGW1-1 (508819) to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508808_LONGWD-508806_LIEBERM4_Ckt1 | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508808) 138.0 kV bus to LIEBERM4 (508806) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508808) 138.0 kV bus to LIEBERM4 (508806) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508808) 138.0 kV bus to LIEBERM4 (508806) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508808_LONGWD-507711_ARSHILL4_Ckt1 | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508808) 138.0 bus to NORAM (507774) 138.0 bus CKT 1 b. 2. Drop load from bus NORAM (507774) 138.0 kV bus b. 3. Trip branch from NORAM (507774) 138.0 bus to RAINES (507749) 138.0 bus CKT 1 b. 4. Drop load from bus RAINES (507749) 138.0 kV bus b. 5. Drop switching device from bus RAINES (507749) 138.0 kV bus b. 6. Trip branch from RAINES (507749) 138.0 bus to ARSHILL4 (507711) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508808) 138.0 bus to NORAM (507774) 138.0 bus CKT 1 c. 2. Reclose branch from NORAM (507774) 138.0 bus to RAINES (507749) 138.0 bus CKT 1 c. 3. Reclose branch from RAINES (507749) 138.0 bus to ARSHILL4 (507711) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508808) 138.0 bus to NORAM (507774) 138.0 bus CKT 1 d. 2. Trip branch from NORAM (507774) 138.0 bus to RAINES (507749) 138.0 bus CKT 1 d. 3. Trip branch from RAINES (507749) 138.0 bus to ARSHILL4 (507711) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508808_LONGWD-507727_FLOURNY4_Ckt1 | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508808) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 b. 2. Drop load from bus OAKPH (508816) 138.0 kV bus b. 3. Trip branch from OAKPH (508816) 138.0 bus to FLOURNY4 (507727) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508808) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 c. 2. Reclose branch from OAKPH (508816) 138.0 bus to FLOURNY4 (507727) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508808) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 d. 2. Trip branch from OAKPH (508816) 138.0 bus to FLOURNY4 (507727) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508808_LONGWD-508566_SABMINT4_Ckt1 | 3 Phase fault on LONGWD (508808) 138.0 kV a. Apply fault on LONGWD (508808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD (508808) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 b. 2. Drop load from bus SCOTTSV4 (508567) 138.0 kV bus b. 3. Trip branch from SCOTTSV4 (508567) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 b. 4. Drop load from bus SEMRSHL4 (508569) 138.0 kV bus b. 5. Trip branch from SEMRSHL4 (508569) 138.0 bus to SABMINT4 (508566) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LONGWD (508808) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 c. 2. Reclose branch from SCOTTSV4 (508567) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 c. 3. Reclose branch from SEMRSHL4 (508569) 138.0 bus to SABMINT4 (508566) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LONGWD (508808) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 d. 2. Trip branch from SCOTTSV4 (508567) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 d. 3. Trip branch from SEMRSHL4 (508569) 138.0 bus to SABMINT4 (508566) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337561_8EL-338440_8PANDA%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337561_8EL-337368_8MT_OLIVE%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8MT_OLIVE% (337368) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8MT_OLIVE% (337368) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8MT_OLIVE% (337368) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337561_8EL-337420_8STERLING%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8STERLING% (337420) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8STERLING% (337420) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8STERLING% (337420) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337561_8EL-338440_8PANDA%_Ckt2 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337561_8EL-337643_8SHERIDAN%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8SHERIDAN% (337643) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8SHERIDAN% (337643) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8SHERIDAN% (337643) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337561_8EL-337376_7SAREPTA%_3Winding | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at 1EL (337565) to trip transformer at 1EL DORADO2 13.8 kV bus b. 2. Trip branch from 7EL (337562) 345.0 bus to 7SAREPTA% (337376) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7EL (337562) 345.0 bus to 7SAREPTA% (337376) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7EL (337562) 345.0 bus to 7SAREPTA% (337376) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337561_8EL-337539_3EL_3Winding | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at 1EL (337566) to trip transformer at 1EL DORADO3 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337561_8EL-337515_8MCNEIL%_Ckt1 | 3 Phase fault on 8EL (337561) 500.0 kV a. Apply fault on 8EL (337561) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8MCNEIL% (337515) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8EL (337561) 500.0 kV bus to 8MCNEIL% (337515) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8MCNEIL% (337515) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337363_3SAREPTA!-337376_7SAREPTA%_Ckt1 | 3 Phase fault on 3SAREPTA! (337363) 115.0 kV a. Apply fault on 3SAREPTA! (337363) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 3SAREPTA! (337363) 115.0 bus to 7SAREPTA% (337376) 115.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 3SAREPTA! (337363) 115.0 bus to 7SAREPTA% (337376) 115.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 3SAREPTA! (337363) 115.0 bus to 7SAREPTA% (337376) 115.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337363_3SAREPTA!-337361_3MINDEN_LA!_Ckt1 | 3 Phase fault on 3SAREPTA! (337363) 115.0 kV a. Apply fault on 3SAREPTA! (337363) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 3MINDEN_LA! (337361) 115.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 3SAREPTA! (337363) 115.0 kV bus to 3MINDEN_LA! (337361) 115.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 3MINDEN_LA! (337361) 115.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_500250_DOLHILL7-500260_DOLHILL6_Ckt1 | 3 Phase fault on DOLHILL7 (500250) 345.0 kV a. Apply fault on DOLHILL7 (500250) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DOLHILL7 (500250) 345.0 bus to DOLHILL6 (500260) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DOLHILL7 (500250) 345.0 bus to DOLHILL6 (500260) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DOLHILL7 (500250) 345.0 bus to DOLHILL6 (500260) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508832_DIANA-508359_WELSH_Ckt1 | 3 Phase fault on DIANA (508832) 345.0 kV a. Apply fault on DIANA (508832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508832_DIANA-508359_WELSH_Ckt2 | 3 Phase fault on DIANA (508832) 345.0 kV a. Apply fault on DIANA (508832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_507759_SW-507760_SW_3Winding | 3 Phase fault on SW (507759) 138.0 kV a. Apply fault on SW (507759) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SWSHV1-1 (507778) to trip transformer at SWSHV1-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508840_WILKES-508841_WILKES_3Winding | 3 Phase fault on WILKES (508840) 138.0 kV a. Apply fault on WILKES (508840) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WILKES-1 (508826) to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508840_WILKES-508297_LSSOUTH4_Ckt1 | 3 Phase fault on WILKES (508840) 138.0 kV a. Apply fault on WILKES (508840) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES (508840) 138.0 kV bus to LSSOUTH4 (508297) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WILKES (508840) 138.0 kV bus to LSSOUTH4 (508297) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WILKES (508840) 138.0 kV bus to LSSOUTH4 (508297) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508806_LIEBERM4-588404_G16-167-TAP_Ckt1 | 3 Phase fault on LIEBERM4 (508806) 138.0 kV a. Apply fault on LIEBERM4 (508806) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LIEBERM4 (508806) 138.0 kV bus to G16-167-TAP (588404) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LIEBERM4 (508806) 138.0 kV bus to G16-167-TAP (588404) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LIEBERM4 (508806) 138.0 kV bus to G16-167-TAP (588404) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_507727_FLOURNY4-507726_FLOURNY2_3Winding | 3 Phase fault on FLOURNY4 (507727) 138.0 kV a. Apply fault on FLOURNY4 (507727) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at FLOURNY1 (507740) to trip transformer at FLOURNY1 12.470 (507740) 12.470000267028809 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_507727_FLOURNY4-508808_LONGWD_Ckt1 | 3 Phase fault on FLOURNY4 (507727) 138.0 kV a. Apply fault on FLOURNY4 (507727) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY4 (507727) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 b. 2. Drop load from bus OAKPH (508816) 138.0 kV bus b. 3. Trip branch from OAKPH (508816) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLOURNY4 (507727) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 c. 2. Reclose branch from OAKPH (508816) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLOURNY4 (507727) 138.0 bus to OAKPH (508816) 138.0 bus CKT 1 d. 2. Trip branch from OAKPH (508816) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_507727_FLOURNY4-507732_GENMOTR4_Ckt1 | 3 Phase fault on FLOURNY4 (507727) 138.0 kV a. Apply fault on FLOURNY4 (507727) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus GENMOTR4 (507732) 138.0 kV bus b. 2. Trip branch from FLOURNY4 (507727) 138.0 bus to GENMOTR4 (507732) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLOURNY4 (507727) 138.0 bus to GENMOTR4 (507732) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLOURNY4 (507727) 138.0 bus to GENMOTR4 (507732) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337368_8MT_OLIVE%-509366_LAYFLD8_Ckt1 | 3 Phase fault on 8MT_OLIVE% (337368) 500.0 kV a. Apply fault on 8MT_OLIVE% (337368) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8MT_OLIVE% (337368) 500.0 kV bus to LAYFLD8 (509366) 500.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8MT_OLIVE% (337368) 500.0 kV bus to LAYFLD8 (509366) 500.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8MT_OLIVE% (337368) 500.0 kV bus to LAYFLD8 (509366) 500.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337368_8MT_OLIVE%-337369_6MT_OLIVE%_Ckt1 | 3 Phase fault on 8MT_OLIVE% (337368) 500.0 kV a. Apply fault on 8MT_OLIVE% (337368) 500.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 8MT_OLIVE% (337368) 500.0 bus to 6MT_OLIVE% (337369) 500.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 8MT_OLIVE% (337368) 500.0 bus to 6MT_OLIVE% (337369) 500.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 8MT_OLIVE% (337368) 500.0 bus to 6MT_OLIVE% (337369) 500.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_337539_3EL-337561_8EL_3Winding | 3 Phase fault on 3EL (337539) 115.0 kV a. Apply fault on 3EL (337539) 115.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at 1EL (337566) to trip transformer at 1EL DORADO3 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_507711_ARSHILL4-507789_STLGENS4_Ckt1 | 3 Phase fault on ARSHILL4 (507711) 138.0 kV a. Apply fault on ARSHILL4 (507711) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to STLGENS4 (507789) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ARSHILL4 (507711) 138.0 kV bus to STLGENS4 (507789) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to STLGENS4 (507789) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_507711_ARSHILL4-507731_FTHUMBG4_Ckt1 | 3 Phase fault on ARSHILL4 (507711) 138.0 kV a. Apply fault on ARSHILL4 (507711) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to FTHUMBG4 (507731) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ARSHILL4 (507711) 138.0 kV bus to FTHUMBG4 (507731) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to FTHUMBG4 (507731) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508566_SABMINT4-508562_PIRKEY_Ckt1 | 3 Phase fault on SABMINT4 (508566) 138.0 kV a. Apply fault on SABMINT4 (508566) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138.0 kV bus to PIRKEY (508562) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SABMINT4 (508566) 138.0 kV bus to PIRKEY (508562) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SABMINT4 (508566) 138.0 kV bus to PIRKEY (508562) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508566_SABMINT4-508808_LONGWD_Ckt1 | 3 Phase fault on SABMINT4 (508566) 138.0 kV a. Apply fault on SABMINT4 (508566) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 b. 2. Drop load from bus SEMRSHL4 (508569) 138.0 kV bus b. 3. Trip branch from SEMRSHL4 (508569) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 b. 4. Drop load from bus SCOTTSV4 (508567) 138.0 kV bus b. 5. Trip branch from SCOTTSV4 (508567) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SABMINT4 (508566) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 c. 2. Reclose branch from SEMRSHL4 (508569) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 c. 3. Reclose branch from SCOTTSV4 (508567) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SABMINT4 (508566) 138.0 bus to SEMRSHL4 (508569) 138.0 bus CKT 1 d. 2. Trip branch from SEMRSHL4 (508569) 138.0 bus to SCOTTSV4 (508567) 138.0 bus CKT 1 d. 3. Trip branch from SCOTTSV4 (508567) 138.0 bus to LONGWD (508808) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508566_SABMINT4-508577_SABINEM4_Ckt1 | 3 Phase fault on SABMINT4 (508566) 138.0 kV a. Apply fault on SABMINT4 (508566) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SABINEM4 (508577) 138.0 kV bus b. 2. Drop load from bus SABINEM4 (508577) 138.0 kV bus b. 3. Trip branch from SABMINT4 (508566) 138.0 bus to SABINEM4 (508577) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SABMINT4 (508566) 138.0 bus to SABINEM4 (508577) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SABMINT4 (508566) 138.0 bus to SABINEM4 (508577) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508562_PIRKEY-508595_HALLSVLS4_Ckt1 | 3 Phase fault on PIRKEY (508562) 138.0 kV a. Apply fault on PIRKEY (508562) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus HALLSVLS4 (508595) 138.0 kV bus b. 2. Trip branch from PIRKEY (508562) 138.0 bus to HALLSVLS4 (508595) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PIRKEY (508562) 138.0 bus to HALLSVLS4 (508595) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PIRKEY (508562) 138.0 bus to HALLSVLS4 (508595) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508562_PIRKEY-509092_EASTON_Ckt1 | 3 Phase fault on PIRKEY (508562) 138.0 kV a. Apply fault on PIRKEY (508562) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus EASTON (509092) 138.0 kV bus b. 2. Trip branch from PIRKEY (508562) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PIRKEY (508562) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PIRKEY (508562) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508809_LONGWD | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LONGW1-1 (508819) 13.2 kV bus to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus b. 2. Trip branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-337376_7SAREPTA% | Single Phase Fault with Stuck Breaker on 7SAREPTA% (337376) 345.0 kV bus a. Apply single-phase fault on 7SAREPTA% (337376) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7SAREPTA% (337376) 345.0 kV bus to 7EL (337562) 345.0 kV bus CKT 1 b. 2. Disconnect 1EL (337565) 13.8 kV bus to trip transformer at 1EL DORADO2 13.8 kV bus b. 3. Trip branch from 7SAREPTA% (337376) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-507760_SW | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SWSHV2-1 (507777) 13.8 kV bus to trip transformer at SWSHV2-1 13.8 kV bus b. 2. Disconnect SWSHV1-1 (507778) 13.8 kV bus to trip transformer at SWSHV1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508841_WILKES | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a. Apply single-phase fault on WILKES (508841) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WILKES (508841) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Disconnect WILKES-1 (508826) 13.2 kV bus to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508808_LONGWD | Single Phase Fault with Stuck Breaker on LONGWD (508808) 138.0 kV bus a. Apply single-phase fault on LONGWD (508808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LONGW1-1 (508819) 13.2 kV bus to trip transformer at LONGW1-1 13.200 (508819) 13.2 kV bus b. 2. Trip branch from LONGWD (508808) 138.0 kV bus to LIEBERM4 (508806) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-337561_8EL | Single Phase Fault with Stuck Breaker on 8EL (337561) 500.0 kV bus a. Apply single-phase fault on 8EL (337561) 500.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 8EL (337561) 500.0 kV bus to 8PANDA% (338440) 500.0 kV bus CKT 1 b. 2. Trip branch from 8EL (337561) 500.0 kV bus to 8MT_OLIVE% (337368) 500.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-337363_3SAREPTA! | Single Phase Fault with Stuck Breaker on 3SAREPTA! (337363) 115.0 kV bus a. Apply single-phase fault on 3SAREPTA! (337363) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 b. 2. Trip branch from 3SAREPTA! (337363) 115.0 kV bus to 3MINDEN_LA! (337361) 115.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-507759_SW | Single Phase Fault with Stuck Breaker on SW (507759) 138.0 kV bus a. Apply single-phase fault on SW (507759) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SWSHV2-1 (507777) 13.8 kV bus to trip transformer at SWSHV2-1 13.8 kV bus b. 2. Disconnect SWSHV1-1 (507778) 13.8 kV bus to trip transformer at SWSHV1-1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508840_WILKES | Single Phase Fault with Stuck Breaker on WILKES (508840) 138.0 kV bus a. Apply single-phase fault on WILKES (508840) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WILKES-1 (508826) 13.2 kV bus to trip transformer at WILKES-1 13.200 (508826) 13.2 kV bus b. 2. Trip branch from WILKES (508840) 138.0 kV bus to LSSOUTH4 (508297) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508806_LIEBERM4 | Single Phase Fault with Stuck Breaker on LIEBERM4 (508806) 138.0 kV bus a. Apply single-phase fault on LIEBERM4 (508806) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from LIEBERM4 (508806) 138.0 kV bus to LONGWD (508808) 138.0 kV bus CKT 1 b. 2. Trip branch from LIEBERM4 (508806) 138.0 kV bus to G16-167-TAP (588404) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-338440_8PANDA% | Single Phase Fault with Stuck Breaker on 8PANDA% (338440) 500.0 kV bus a. Apply single-phase fault on 8PANDA% (338440) 500.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 8PANDA% (338440) 500.0 kV bus to 8EL (337561) 500.0 kV bus CKT 1 b. 2. Trip branch from 8PANDA% (338440) 500.0 kV bus to 8EL (337561) 500.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-337539_3EL | Single Phase Fault with Stuck Breaker on 3EL (337539) 115.0 kV bus a. Apply single-phase fault on 3EL (337539) 115.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect 1EL (337564) 13.8 kV bus to trip transformer at 1EL DORADO1 13.8 kV bus b. 2. Disconnect 1EL (337566) 13.8 kV bus to trip transformer at 1EL DORADO3 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-507711_ARSHILL4 | Single Phase Fault with Stuck Breaker on ARSHILL4 (507711) 138.0 kV bus a. Apply single-phase fault on ARSHILL4 (507711) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138.0 kV bus to STLGENS4 (507789) 138.0 kV bus CKT 1 b. 2. Trip branch from ARSHILL4 (507711) 138.0 kV bus to FTHUMBG4 (507731) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508562_PIRKEY | Single Phase Fault with Stuck Breaker on PIRKEY (508562) 138.0 kV bus a. Apply single-phase fault on PIRKEY (508562) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus HALLSVLS4 (508595) 138.0 kV bus b. 2. Trip branch from PIRKEY (508562) 138.0 kV bus to HALLSVLS4 (508595) 138.0 kV bus CKT 1 b. 3. Drop load from bus EASTON (509092) 138.0 kV bus b. 4. Trip branch from PIRKEY (508562) 138.0 kV bus to EASTON (509092) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511468_LES-7-511456_OKU-7_Ckt1 | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511468_LES-7-760938_G17-171-TAP_Ckt1 | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511468_LES-7-511467_LES-4_3Winding | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at LES#4-1 (511414) to trip transformer at LES#4-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511468_LES-7-587744_G16-091-TAP_Ckt1 | 3 Phase fault on L.E.S.-7 (511468) 345.0 kV a. Apply fault on L.E.S.-7 (511468) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511456_OKU-7-762467_G18-015-TAP_Ckt1 | 3 Phase fault on O.K.U.-7 (511456) 345.0 kV a. Apply fault on O.K.U.-7 (511456) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511456_OKU-7-511565_OKLAUN_Ckt1 | 3 Phase fault on O.K.U.-7 (511456) 345.0 kV a. Apply fault on O.K.U.-7 (511456) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Drop switching device from bus OKLAUN (511565) 345.0 kV bus b. 2. Trip branch from O.K.U.-7 (511456) 345.0 bus to OKLAUN (511565) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from O.K.U.-7 (511456) 345.0 bus to OKLAUN (511565) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from O.K.U.-7 (511456) 345.0 bus to OKLAUN (511565) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_587744_G16-091-TAP-515800_GRACMNT7_Ckt1 | 3 Phase fault on G16-091-TAP (587744) 345.0 kV a. Apply fault on G16-091-TAP (587744) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_760938_G17-171-TAP-511568_TERRYRD7_Ckt1 | 3 Phase fault on G17-171-TAP (760938) 345.0 kV a. Apply fault on G17-171-TAP (760938) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511467_LES-4-511468_LES-7_3Winding | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LES#4-1 (511414) to trip transformer at LES#4-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511467_LES-4-511537_ARTVLTP4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 bus to SHERID4 (511474) 138.0 bus CKT 1 b. 2. Drop load from bus SHERID4 (511474) 138.0 kV bus b. 3. Trip branch from SHERID4 (511474) 138.0 bus to ARTVLTP4 (511537) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 bus to SHERID4 (511474) 138.0 bus CKT 1 c. 2. Reclose branch from SHERID4 (511474) 138.0 bus to ARTVLTP4 (511537) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 bus to SHERID4 (511474) 138.0 bus CKT 1 d. 2. Trip branch from SHERID4 (511474) 138.0 bus to ARTVLTP4 (511537) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511467_LES-4-511439_LWSTAP_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to LWSTAP (511439) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to LWSTAP (511439) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to LWSTAP (511439) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511467_LES-4-511494_COMMTAP4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMMTAP4 (511494) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to COMMTAP4 (511494) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMMTAP4 (511494) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511467_LES-4-511437_COMANC-4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMANC-4 (511437) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to COMANC-4 (511437) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to COMANC-4 (511437) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511467_LES-4-511466_LES-2_3Winding | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at LES#1-1 (511416) to trip transformer at LES#1-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511467_LES-4-511423_FLE_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to FLE (511423) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to FLE (511423) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to FLE (511423) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511467_LES-4-511486_ELGINJT4_Ckt1 | 3 Phase fault on L.E.S.-4 (511467) 138.0 kV a. Apply fault on L.E.S.-4 (511467) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to ELGINJT4 (511486) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-4 (511467) 138.0 kV bus to ELGINJT4 (511486) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to ELGINJT4 (511486) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515800_GRACMNT7-514801_MINCO_Ckt1 | 3 Phase fault on GRACMNT7 (515800) 345.0 kV a. Apply fault on GRACMNT7 (515800) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515800_GRACMNT7-560078_G16-037-TAP_Ckt1 | 3 Phase fault on GRACMNT7 (515800) 345.0 kV a. Apply fault on GRACMNT7 (515800) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515800_GRACMNT7-515802_GRACMNT4_3Winding | 3 Phase fault on GRACMNT7 (515800) 345.0 kV a. Apply fault on GRACMNT7 (515800) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at GRCMNT11 (515801) to trip transformer at GRCMNT11 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_762467_G18-015-TAP-762216_G17-151TAP_Ckt1 | 3 Phase fault on G18-015-TAP (762467) 345.0 kV a. Apply fault on G18-015-TAP (762467) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G18-015-TAP (762467) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G18-015-TAP (762467) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511568_TERRYRD7-515136_SUNNYSD7_Ckt1 | 3 Phase fault on TERRYRD7 (511568) 345.0 kV a. Apply fault on TERRYRD7 (511568) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511439_LWSTAP-511488_112GORE4_Ckt1 | 3 Phase fault on LWSTAP (511439) 138.0 kV a. Apply fault on LWSTAP (511439) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LWSTAP (511439) 138.0 bus to RPPAPER4 (511512) 138.0 bus CKT 1 b. 2. Drop load from bus RPPAPER4 (511512) 138.0 kV bus b. 3. Trip branch from RPPAPER4 (511512) 138.0 bus to 112GORE4 (511488) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LWSTAP (511439) 138.0 bus to RPPAPER4 (511512) 138.0 bus CKT 1 c. 2. Reclose branch from RPPAPER4 (511512) 138.0 bus to 112GORE4 (511488) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LWSTAP (511439) 138.0 bus to RPPAPER4 (511512) 138.0 bus CKT 1 d. 2. Trip branch from RPPAPER4 (511512) 138.0 bus to 112GORE4 (511488) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511439_LWSTAP-511431_LWS_Ckt1 | 3 Phase fault on LWSTAP (511439) 138.0 kV a. Apply fault on LWSTAP (511439) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus LWS (511431) 138.0 kV bus b. 2. Trip branch from LWSTAP (511439) 138.0 bus to LWS (511431) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LWSTAP (511439) 138.0 bus to LWS (511431) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LWSTAP (511439) 138.0 bus to LWS (511431) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511466_LES-2-511503_LAW_Ckt1 | 3 Phase fault on L.E.S.-2 (511466) 69.0 kV a. Apply fault on L.E.S.-2 (511466) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-S2 (511470) 69.0 bus CKT 1 b. 2. Drop load from bus LGORE-S2 (511470) 69.0 kV bus b. 3. Drop load from bus LAW (511503) 69.0 kV bus b. 4. Trip branch from LGORE-S2 (511470) 69.0 bus to LAW (511503) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-2 (511466) 69.0 bus to LGORE-S2 (511470) 69.0 bus CKT 1 c. 2. Reclose branch from LGORE-S2 (511470) 69.0 bus to LAW (511503) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-S2 (511470) 69.0 bus CKT 1 d. 2. Trip branch from LGORE-S2 (511470) 69.0 bus to LAW (511503) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511466_LES-2-511487_ELGINJT2_Ckt1 | 3 Phase fault on L.E.S.-2 (511466) 69.0 kV a. Apply fault on L.E.S.-2 (511466) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-N2 (511469) 69.0 bus CKT 1 b. 2. Drop load from bus LGORE-N2 (511469) 69.0 kV bus b. 3. Trip branch from LGORE-N2 (511469) 69.0 bus to FT.SILL2 (511461) 69.0 bus CKT 1 b. 4. Drop load from bus FT.SILL2 (511461) 69.0 kV bus b. 5. Drop switching device from bus FT.SILL2 (511461) 69.0 kV bus b. 6. Trip branch from FT.SILL2 (511461) 69.0 bus to PO.HILL2 (511473) 69.0 bus CKT 1 b. 7. Drop load from bus PO.HILL2 (511473) 69.0 kV bus b. 8. Trip branch from PO.HILL2 (511473) 69.0 bus to ELGINJT2 (511487) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from L.E.S.-2 (511466) 69.0 bus to LGORE-N2 (511469) 69.0 bus CKT 1 c. 2. Reclose branch from LGORE-N2 (511469) 69.0 bus to FT.SILL2 (511461) 69.0 bus CKT 1 c. 3. Reclose branch from FT.SILL2 (511461) 69.0 bus to PO.HILL2 (511473) 69.0 bus CKT 1 c. 4. Reclose branch from PO.HILL2 (511473) 69.0 bus to ELGINJT2 (511487) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from L.E.S.-2 (511466) 69.0 bus to LGORE-N2 (511469) 69.0 bus CKT 1 d. 2. Trip branch from LGORE-N2 (511469) 69.0 bus to FT.SILL2 (511461) 69.0 bus CKT 1 d. 3. Trip branch from FT.SILL2 (511461) 69.0 bus to PO.HILL2 (511473) 69.0 bus CKT 1 d. 4. Trip branch from PO.HILL2 (511473) 69.0 bus to ELGINJT2 (511487) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514801_MINCO-516096_NORMHLL7_Ckt1 | 3 Phase fault on MINCO (514801) 345.0 kV a. Apply fault on MINCO (514801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_560078_G16-037-TAP-511553_CHISHOLM7_Ckt1 | 3 Phase fault on G16-037-TAP (560078) 345.0 kV a. Apply fault on G16-037-TAP (560078) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-037-TAP (560078) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515802_GRACMNT4-520814_ANADARK4_Ckt1 | 3 Phase fault on GRACMNT4 (515802) 138.0 kV a. Apply fault on GRACMNT4 (515802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515802_GRACMNT4-520814_ANADARK4_Ckt2 | 3 Phase fault on GRACMNT4 (515802) 138.0 kV a. Apply fault on GRACMNT4 (515802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-511468_LES-7 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to O.K.U.-7 (511456) 345.0 kV bus CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-511456_OKU-7 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345.0 kV bus a. Apply single-phase fault on O.K.U.-7 (511456) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip branch from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-511467_LES-4 | Single Phase Fault with Stuck Breaker on L.E.S.-4 (511467) 138.0 kV bus a. Apply single-phase fault on L.E.S.-4 (511467) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect LES#5-1 (511411) 13.8 kV bus to trip transformer at LES#5-1 13.8 kV bus b. 2. Trip branch from L.E.S.-4 (511467) 138.0 kV bus to SHERID4 (511474) 138.0 kV bus CKT 1 b. 3. Drop load from bus SHERID4 (511474) 138.0 kV bus b. 4. Trip branch from SHERID4 (511474) 138.0 kV bus to ARTVLTP4 (511537) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-515800_GRACMNT7 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345.0 kV bus a. Apply single-phase fault on GRACMNT7 (515800) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345.0 kV bus to MINCO (514801) 345.0 kV bus CKT 1 b. 2. Trip branch from GRACMNT7 (515800) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-511466_LES-2 | Single Phase Fault with Stuck Breaker on L.E.S.-2 (511466) 69.0 kV bus a. Apply single-phase fault on L.E.S.-2 (511466) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-2 (511466) 69.0 kV bus to LGORE-S2 (511470) 69.0 kV bus CKT 1 b. 2. Drop load from bus LGORE-S2 (511470) 69.0 kV bus b. 3. Drop load from bus LAW (511503) 69.0 kV bus b. 4. Trip branch from LGORE-S2 (511470) 69.0 kV bus to LAW (511503) 69.0 kV bus CKT 1 b. 5. Trip branch from L.E.S.-2 (511466) 69.0 kV bus to LGORE-N2 (511469) 69.0 kV bus CKT 1 b. 6. Drop load from bus LGORE-N2 (511469) 69.0 kV bus b. 7. Trip branch from LGORE-N2 (511469) 69.0 kV bus to FT.SILL2 (511461) 69.0 kV bus CKT 1 b. 8. Drop load from bus FT.SILL2 (511461) 69.0 kV bus b. 9. Drop switching device from bus FT.SILL2 (511461) 69.0 kV bus b. 10. Trip branch from FT.SILL2 (511461) 69.0 kV bus to PO.HILL2 (511473) 69.0 kV bus CKT 1 b. 11. Drop load from bus PO.HILL2 (511473) 69.0 kV bus b. 12. Trip branch from PO.HILL2 (511473) 69.0 kV bus to ELGINJT2 (511487) 69.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-514801_MINCO | Single Phase Fault with Stuck Breaker on MINCO (514801) 345.0 kV bus a. Apply single-phase fault on MINCO (514801) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MINCO (514801) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Trip branch from MINCO (514801) 345.0 kV bus to NORMHLL7 (516096) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-515802_GRACMNT4 | Single Phase Fault with Stuck Breaker on GRACMNT4 (515802) 138.0 kV bus a. Apply single-phase fault on GRACMNT4 (515802) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 b. 2. Trip branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512648_MAID-300069_5CHOTEAU1_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512648_MAID-512656_GRDA1_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512648_MAID-301344_5CDRCRST_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 b. 2. Drop load from bus LOCSTGVKM (513050) 161.0 kV bus b. 3. Trip branch from LOCSTGVKM (513050) 161.0 bus to 5CDRCRST (301344) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 c. 2. Reclose branch from LOCSTGVKM (513050) 161.0 bus to 5CDRCRST (301344) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 d. 2. Trip branch from LOCSTGVKM (513050) 161.0 bus to 5CDRCRST (301344) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512648_MAID-512629_DRYGULCH5_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to DRYGULCH5 (512629) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to DRYGULCH5 (512629) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to DRYGULCH5 (512629) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512648_MAID-512638_CATSAGR5_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512648_MAID-512638_CATSAGR5_Ckt2 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to CATSAGR5 (512638) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512648_MAID-512626_MAID_3Winding | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MAITER2 (512837) to trip transformer at MAITER2 1 13.200 (512837) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512648_MAID-512635_KERR_Ckt1 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512648_MAID-512635_KERR_Ckt2 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to KERR (512635) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512648_MAID-512656_GRDA1_Ckt2 | 3 Phase fault on MAID (512648) 161.0 kV a. Apply fault on MAID (512648) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512656_GRDA1-512648_MAID_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 b. 2. Drop load from bus WMAIN (512742) 161.0 kV bus b. 3. Trip branch from WMAIN (512742) 161.0 bus to NWMAID5 (512757) 161.0 bus CKT 1 b. 4. Drop load from bus NWMAID5 (512757) 161.0 kV bus b. 5. Trip branch from NWMAID5 (512757) 161.0 bus to GERALDGAY5 (512760) 161.0 bus CKT 1 b. 6. Drop load from bus GERALDGAY5 (512760) 161.0 kV bus b. 7. Trip branch from GERALDGAY5 (512760) 161.0 bus to MAID (512648) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 c. 2. Reclose branch from WMAIN (512742) 161.0 bus to NWMAID5 (512757) 161.0 bus CKT 1 c. 3. Reclose branch from NWMAID5 (512757) 161.0 bus to GERALDGAY5 (512760) 161.0 bus CKT 1 c. 4. Reclose branch from GERALDGAY5 (512760) 161.0 bus to MAID (512648) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 d. 2. Trip branch from WMAIN (512742) 161.0 bus to NWMAID5 (512757) 161.0 bus CKT 1 d. 3. Trip branch from NWMAID5 (512757) 161.0 bus to GERALDGAY5 (512760) 161.0 bus CKT 1 d. 4. Trip branch from GERALDGAY5 (512760) 161.0 bus to MAID (512648) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512656_GRDA1-513570_CHOUTEAUCRK516100_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to CHOUTEAUCRK5161.00 (513570) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 kV bus to CHOUTEAUCRK5161.00 (513570) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to CHOUTEAUCRK5161.00 (513570) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512656_GRDA1-512671_HUNT_3Winding | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at GRDA1 (512816) to trip transformer at GRDA1 1 13.8 kV bus b. 2. Trip branch from GRDA1 (512727) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 b. 3. Trip branch from MAIDTP2 (512625) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512727) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 c. 2. Reclose branch from MAIDTP2 (512625) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512727) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 d. 2. Trip branch from MAIDTP2 (512625) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512656_GRDA1-512700_WAGNOR_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to WAGNOR (512700) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 kV bus to WAGNOR (512700) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to WAGNOR (512700) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512650_GRDA1-512750_TONECE7_Ckt1 | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_300069_5CHOTEAU1-301348_5CHOTEAU2_CktZ1 | 3 Phase fault on 5CHOTEAU1 (300069) 161.0 kV a. Apply fault on 5CHOTEAU1 (300069) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CHOTEAU1 (300069) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CHOTEAU1 (300069) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT Z1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CHOTEAU1 (300069) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512629_DRYGULCH5-512654_PENSA_Ckt1 | 3 Phase fault on DRYGULCH5 (512629) 161.0 kV a. Apply fault on DRYGULCH5 (512629) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512635_KERR-512714_KANSATP5_Ckt1 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 b. 2. Drop load from bus 412SUB (512637) 161.0 kV bus b. 3. Trip branch from 412SUB (512637) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 c. 2. Reclose branch from 412SUB (512637) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 d. 2. Trip branch from 412SUB (512637) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512635_KERR-512805_SALNCRK5_Ckt2 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512635_KERR-512805_SALNCRK5_Ckt1 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512635_KERR-512654_PENSA_Ckt1 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512635_KERR-512771_KERR_CktZ0 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512771) 161.0 bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 bus to KERR (512771) 161.0 bus CKT Z0 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512771) 161.0 bus CKT Z0 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512635_KERR-512770_KERR_CktZ0 | 3 Phase fault on KERR (512635) 161.0 kV a. Apply fault on KERR (512635) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512770) 161.0 bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KERR (512635) 161.0 bus to KERR (512770) 161.0 bus CKT Z0 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KERR (512635) 161.0 bus to KERR (512770) 161.0 bus CKT Z0 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512638_CATSAGR5-512627_COLINS_Ckt1 | 3 Phase fault on CATSAGR5 (512638) 161.0 kV a. Apply fault on CATSAGR5 (512638) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATSAGR5 (512638) 161.0 bus to 5ELMCRK (300993) 161.0 bus CKT 1 b. 2. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 3. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 4. Trip branch from 5ELMCRK (300993) 161.0 bus to COLINS (512627) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CATSAGR5 (512638) 161.0 bus to 5ELMCRK (300993) 161.0 bus CKT 1 c. 2. Reclose branch from 5ELMCRK (300993) 161.0 bus to COLINS (512627) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CATSAGR5 (512638) 161.0 bus to 5ELMCRK (300993) 161.0 bus CKT 1 d. 2. Trip branch from 5ELMCRK (300993) 161.0 bus to COLINS (512627) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512638_CATSAGR5-509790_CATOOSA4_3Winding | 3 Phase fault on CATSAGR5 (512638) 161.0 kV a. Apply fault on CATSAGR5 (512638) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CATTER1 (512833) to trip transformer at CATTER1 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512626_MAID-512671_HUNT_Ckt1 | 3 Phase fault on MAID (512626) 69.0 kV a. Apply fault on MAID (512626) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512626) 69.0 bus to AMERCAST (512681) 69.0 bus CKT 1 b. 2. Drop load from bus AMERCAST (512681) 69.0 kV bus b. 3. Trip branch from AMERCAST (512681) 69.0 bus to CPPTAP (512661) 69.0 bus CKT 1 b. 4. Trip branch from CPPTAP (512661) 69.0 bus to PRYORCHEM2 (512699) 69.0 bus CKT 1 b. 5. Drop load from bus PRYORCHEM2 (512699) 69.0 kV bus b. 6. Trip branch from PRYORCHEM2 (512699) 69.0 bus to AIRPROD2 (512687) 69.0 bus CKT 1 b. 7. Drop load from bus AIRPROD2 (512687) 69.0 kV bus b. 8. Trip branch from AIRPROD2 (512687) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512626) 69.0 bus to AMERCAST (512681) 69.0 bus CKT 1 c. 2. Reclose branch from AMERCAST (512681) 69.0 bus to CPPTAP (512661) 69.0 bus CKT 1 c. 3. Reclose branch from CPPTAP (512661) 69.0 bus to PRYORCHEM2 (512699) 69.0 bus CKT 1 c. 4. Reclose branch from PRYORCHEM2 (512699) 69.0 bus to AIRPROD2 (512687) 69.0 bus CKT 1 c. 5. Reclose branch from AIRPROD2 (512687) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512626) 69.0 bus to AMERCAST (512681) 69.0 bus CKT 1 d. 2. Trip branch from AMERCAST (512681) 69.0 bus to CPPTAP (512661) 69.0 bus CKT 1 d. 3. Trip branch from CPPTAP (512661) 69.0 bus to PRYORCHEM2 (512699) 69.0 bus CKT 1 d. 4. Trip branch from PRYORCHEM2 (512699) 69.0 bus to AIRPROD2 (512687) 69.0 bus CKT 1 d. 5. Trip branch from AIRPROD2 (512687) 69.0 bus to HUNT (512671) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512626_MAID-512648_MAID_3Winding | 3 Phase fault on MAID (512626) 69.0 kV a. Apply fault on MAID (512626) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MAITER2 (512837) to trip transformer at MAITER2 1 13.200 (512837) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512626_MAID-512683_AMERCAST_Ckt1 | 3 Phase fault on MAID (512626) 69.0 kV a. Apply fault on MAID (512626) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512626) 69.0 bus to REDDEN (512698) 69.0 bus CKT 1 b. 2. Drop load from bus REDDEN (512698) 69.0 kV bus b. 3. Trip branch from REDDEN (512698) 69.0 bus to CASTING (512685) 69.0 bus CKT 1 b. 4. Drop load from bus AMERCAST (512683) 69.0 kV bus b. 5. Trip branch from CASTING (512685) 69.0 bus to AMERCAST (512683) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MAID (512626) 69.0 bus to REDDEN (512698) 69.0 bus CKT 1 c. 2. Reclose branch from REDDEN (512698) 69.0 bus to CASTING (512685) 69.0 bus CKT 1 c. 3. Reclose branch from CASTING (512685) 69.0 bus to AMERCAST (512683) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MAID (512626) 69.0 bus to REDDEN (512698) 69.0 bus CKT 1 d. 2. Trip branch from REDDEN (512698) 69.0 bus to CASTING (512685) 69.0 bus CKT 1 d. 3. Trip branch from CASTING (512685) 69.0 bus to AMERCAST (512683) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512700_WAGNOR-512697_WAGNOR_3Winding | 3 Phase fault on WAGNOR (512700) 161.0 kV a. Apply fault on WAGNOR (512700) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WAGNOR1 (512818) to trip transformer at WAGNOR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512700_WAGNOR-512640_OKAYGR_Ckt1 | 3 Phase fault on WAGNOR (512700) 161.0 kV a. Apply fault on WAGNOR (512700) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512700) 161.0 kV bus to OKAYGR (512640) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512700) 161.0 kV bus to OKAYGR (512640) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512700) 161.0 kV bus to OKAYGR (512640) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_513570_CHOUTEAUCRK516100-512651_CLARMR_Ckt1 | 3 Phase fault on CHOUTEAUCRK5161.00 (513570) 161.0 kV a. Apply fault on CHOUTEAUCRK5161.00 (513570) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHOUTEAUCRK5161.00 (513570) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHOUTEAUCRK5161.00 (513570) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHOUTEAUCRK5161.00 (513570) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_301344_5CDRCRST-512648_MAID_Ckt1 | 3 Phase fault on 5CDRCRST (301344) 161.0 kV a. Apply fault on 5CDRCRST (301344) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 b. 2. Drop load from bus LOCSTGVKM (513050) 161.0 kV bus b. 3. Trip branch from LOCSTGVKM (513050) 161.0 bus to MAID (512648) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CDRCRST (301344) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 c. 2. Reclose branch from LOCSTGVKM (513050) 161.0 bus to MAID (512648) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to LOCSTGVKM (513050) 161.0 bus CKT 1 d. 2. Trip branch from LOCSTGVKM (513050) 161.0 bus to MAID (512648) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_301344_5CDRCRST-301345_2CDRCRST_Ckt1 | 3 Phase fault on 5CDRCRST (301344) 161.0 kV a. Apply fault on 5CDRCRST (301344) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to 2CDRCRST (301345) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CDRCRST (301344) 161.0 bus to 2CDRCRST (301345) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CDRCRST (301344) 161.0 bus to 2CDRCRST (301345) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_301344_5CDRCRST-512655_TAHLQH_Ckt1 | 3 Phase fault on 5CDRCRST (301344) 161.0 kV a. Apply fault on 5CDRCRST (301344) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 kV bus to TAHLQH (512655) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5CDRCRST (301344) 161.0 kV bus to TAHLQH (512655) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5CDRCRST (301344) 161.0 kV bus to TAHLQH (512655) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_300739_7BLACKBERRY-300949_7JASPER_Ckt1 | 3 Phase fault on 7BLACKBERRY (300739) 345.0 kV a. Apply fault on 7BLACKBERRY (300739) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_300739_7BLACKBERRY-532797_WOLFCRK7_Ckt1 | 3 Phase fault on 7BLACKBERRY (300739) 345.0 kV a. Apply fault on 7BLACKBERRY (300739) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_300739_7BLACKBERRY-532793_NEOSHO_Ckt1 | 3 Phase fault on 7BLACKBERRY (300739) 345.0 kV a. Apply fault on 7BLACKBERRY (300739) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7BLACKBERRY (300739) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_300741_5SPORTSMAN-301348_5CHOTEAU2_Ckt1 | 3 Phase fault on 5SPORTSMAN (300741) 161.0 kV a. Apply fault on 5SPORTSMAN (300741) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_300741_5SPORTSMAN-300740_7SPORTSMAN_Ckt1 | 3 Phase fault on 5SPORTSMAN (300741) 161.0 kV a. Apply fault on 5SPORTSMAN (300741) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_300741_5SPORTSMAN-300740_7SPORTSMAN_Ckt2 | 3 Phase fault on 5SPORTSMAN (300741) 161.0 kV a. Apply fault on 5SPORTSMAN (300741) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 5SPORTSMAN (300741) 161.0 bus to 7SPORTSMAN (300740) 161.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509852_TNO--7-510406_NES-7_Ckt1 | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509852_TNO--7-512694_CLEVLND7_Ckt1 | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509852_TNO--7-509755_WEKIWA-7_Ckt1 | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--7 (509852) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--7 (509852) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512654_PENSA-512669_KETCHUM5_Ckt1 | 3 Phase fault on PENSA (512654) 161.0 kV a. Apply fault on PENSA (512654) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus KETCHUM5 (512669) 161.0 kV bus b. 2. Trip branch from PENSA (512654) 161.0 bus to KETCHUM5 (512669) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PENSA (512654) 161.0 bus to KETCHUM5 (512669) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PENSA (512654) 161.0 bus to KETCHUM5 (512669) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512654_PENSA-512628_PENSA_3Winding | 3 Phase fault on PENSA (512654) 161.0 kV a. Apply fault on PENSA (512654) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at PENSA (512841) to trip transformer at PENSA 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509790_CATOOSA4-509752_INOLATP4_Ckt1 | 3 Phase fault on CATOOSA4 (509790) 138.0 kV a. Apply fault on CATOOSA4 (509790) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509790_CATOOSA4-509835_TERNITP4_Ckt1 | 3 Phase fault on CATOOSA4 (509790) 138.0 kV a. Apply fault on CATOOSA4 (509790) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512640_OKAYGR-505560_FT_Ckt1 | 3 Phase fault on OKAYGR (512640) 161.0 kV a. Apply fault on OKAYGR (512640) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OKAYGR (512640) 161.0 kV bus to FT (505560) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OKAYGR (512640) 161.0 kV bus to FT (505560) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OKAYGR (512640) 161.0 kV bus to FT (505560) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512640_OKAYGR-512646_OKAYGR_3Winding | 3 Phase fault on OKAYGR (512640) 161.0 kV a. Apply fault on OKAYGR (512640) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OKAY1 (512848) to trip transformer at OKAY1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512697_WAGNOR-512700_WAGNOR_3Winding | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WAGNOR1 (512818) to trip transformer at WAGNOR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512697_WAGNOR-512801_WAGCTY12_Ckt1 | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512697) 69.0 bus to WAGCTY22 (512759) 69.0 bus CKT 1 b. 2. Drop load from bus WAGCTY22 (512759) 69.0 kV bus b. 3. Drop load from bus WAGCTY12 (512801) 69.0 kV bus b. 4. Trip branch from WAGCTY22 (512759) 69.0 bus to WAGCTY12 (512801) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512697) 69.0 bus to WAGCTY22 (512759) 69.0 bus CKT 1 c. 2. Reclose branch from WAGCTY22 (512759) 69.0 bus to WAGCTY12 (512801) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512697) 69.0 bus to WAGCTY22 (512759) 69.0 bus CKT 1 d. 2. Trip branch from WAGCTY22 (512759) 69.0 bus to WAGCTY12 (512801) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512697_WAGNOR-300958_2HIGHLND_Ckt1 | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512697) 69.0 bus to 2WAGNERW (300972) 69.0 bus CKT 1 b. 2. Drop load from bus 2WAGNERW (300972) 69.0 kV bus b. 3. Trip branch from 2WAGNERW (300972) 69.0 bus to 2COWETA (300955) 69.0 bus CKT 1 b. 4. Drop load from bus 2COWETA (300955) 69.0 kV bus b. 5. Drop load from bus 2HIGHLND (300958) 69.0 kV bus b. 6. Trip branch from 2COWETA (300955) 69.0 bus to 2HIGHLND (300958) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512697) 69.0 bus to 2WAGNERW (300972) 69.0 bus CKT 1 c. 2. Reclose branch from 2WAGNERW (300972) 69.0 bus to 2COWETA (300955) 69.0 bus CKT 1 c. 3. Reclose branch from 2COWETA (300955) 69.0 bus to 2HIGHLND (300958) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512697) 69.0 bus to 2WAGNERW (300972) 69.0 bus CKT 1 d. 2. Trip branch from 2WAGNERW (300972) 69.0 bus to 2COWETA (300955) 69.0 bus CKT 1 d. 3. Trip branch from 2COWETA (300955) 69.0 bus to 2HIGHLND (300958) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512697_WAGNOR-512690_WAGNRTP2_Ckt1 | 3 Phase fault on WAGNOR (512697) 69.0 kV a. Apply fault on WAGNOR (512697) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR (512697) 69.0 kV bus to WAGNRTP2 (512690) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WAGNOR (512697) 69.0 kV bus to WAGNRTP2 (512690) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WAGNOR (512697) 69.0 kV bus to WAGNRTP2 (512690) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512651_CLARMR-510396_NES-4_3Winding | 3 Phase fault on CLARMR (512651) 161.0 kV a. Apply fault on CLARMR (512651) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CLARMR4 (512813) to trip transformer at CLARMR4 13.8 kV bus b. 2. Trip branch from CLARMR (512707) 138.0 bus to OOLOGAHKM (513124) 138.0 bus CKT 1 b. 3. Drop load from bus OOLOGAHKM (513124) 138.0 kV bus b. 4. Trip branch from OOLOGAHKM (513124) 138.0 bus to N.E.S.-4 (510396) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CLARMR (512707) 138.0 bus to OOLOGAHKM (513124) 138.0 bus CKT 1 c. 2. Reclose branch from OOLOGAHKM (513124) 138.0 bus to N.E.S.-4 (510396) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CLARMR (512707) 138.0 bus to OOLOGAHKM (513124) 138.0 bus CKT 1 d. 2. Trip branch from OOLOGAHKM (513124) 138.0 bus to N.E.S.-4 (510396) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512651_CLARMR-512679_CLARMR_3Winding | 3 Phase fault on CLARMR (512651) 161.0 kV a. Apply fault on CLARMR (512651) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CLARMR2 (512815) to trip transformer at CLARMR2 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_301345_2CDRCRST-301344_5CDRCRST_Ckt1 | 3 Phase fault on 2CDRCRST (301345) 69.0 kV a. Apply fault on 2CDRCRST (301345) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 5CDRCRST (301344) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 2CDRCRST (301345) 69.0 bus to 5CDRCRST (301344) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 5CDRCRST (301344) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_301345_2CDRCRST-513059_HULBERKM_Ckt1 | 3 Phase fault on 2CDRCRST (301345) 69.0 kV a. Apply fault on 2CDRCRST (301345) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2PEGGS (300962) 69.0 bus CKT 1 b. 2. Drop load from bus 2PEGGS (300962) 69.0 kV bus b. 3. Trip branch from 2PEGGS (300962) 69.0 bus to 2HULBERT (300975) 69.0 bus CKT 1 b. 4. Drop load from bus 2HULBERT (300975) 69.0 kV bus b. 5. Trip branch from 2HULBERT (300975) 69.0 bus to HULBERKM (513059) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 2CDRCRST (301345) 69.0 bus to 2PEGGS (300962) 69.0 bus CKT 1 c. 2. Reclose branch from 2PEGGS (300962) 69.0 bus to 2HULBERT (300975) 69.0 bus CKT 1 c. 3. Reclose branch from 2HULBERT (300975) 69.0 bus to HULBERKM (513059) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2PEGGS (300962) 69.0 bus CKT 1 d. 2. Trip branch from 2PEGGS (300962) 69.0 bus to 2HULBERT (300975) 69.0 bus CKT 1 d. 3. Trip branch from 2HULBERT (300975) 69.0 bus to HULBERKM (513059) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_301345_2CDRCRST-513062_TAHLWESTKM_Ckt1 | 3 Phase fault on 2CDRCRST (301345) 69.0 kV a. Apply fault on 2CDRCRST (301345) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2LOWERY (300960) 69.0 bus CKT 1 b. 2. Drop load from bus 2LOWERY (300960) 69.0 kV bus b. 3. Trip branch from 2LOWERY (300960) 69.0 bus to 2SLEEPYH (300968) 69.0 bus CKT 1 b. 4. Drop load from bus 2SLEEPYH (300968) 69.0 kV bus b. 5. Trip branch from 2SLEEPYH (300968) 69.0 bus to TAHLWESTKM (513062) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 2CDRCRST (301345) 69.0 bus to 2LOWERY (300960) 69.0 bus CKT 1 c. 2. Reclose branch from 2LOWERY (300960) 69.0 bus to 2SLEEPYH (300968) 69.0 bus CKT 1 c. 3. Reclose branch from 2SLEEPYH (300968) 69.0 bus to TAHLWESTKM (513062) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 2CDRCRST (301345) 69.0 bus to 2LOWERY (300960) 69.0 bus CKT 1 d. 2. Trip branch from 2LOWERY (300960) 69.0 bus to 2SLEEPYH (300968) 69.0 bus CKT 1 d. 3. Trip branch from 2SLEEPYH (300968) 69.0 bus to TAHLWESTKM (513062) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512655_TAHLQH-515956_7CLANS_Ckt1 | 3 Phase fault on TAHLQH (512655) 161.0 kV a. Apply fault on TAHLQH (512655) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus 7CLANS (515956) 161.0 kV bus b. 2. Trip branch from TAHLQH (512655) 161.0 bus to 7CLANS (515956) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TAHLQH (512655) 161.0 bus to 7CLANS (515956) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TAHLQH (512655) 161.0 bus to 7CLANS (515956) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512655_TAHLQH-513044_BRIGSKM_Ckt1 | 3 Phase fault on TAHLQH (512655) 161.0 kV a. Apply fault on TAHLQH (512655) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_300949_7JASPER-300045_7MORGAN_Ckt1 | 3 Phase fault on 7JASPER (300949) 345.0 kV a. Apply fault on 7JASPER (300949) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7JASPER (300949) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7JASPER (300949) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_300949_7JASPER-300794_5LAMAR_Ckt1 | 3 Phase fault on 7JASPER (300949) 345.0 kV a. Apply fault on 7JASPER (300949) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345.0 bus to 5JASPER (300950) 345.0 bus CKT 1 b. 2. Trip branch from 5JASPER (300950) 161.0 bus to 5LAMAR (300794) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7JASPER (300949) 345.0 bus to 5JASPER (300950) 345.0 bus CKT 1 c. 2. Reclose branch from 5JASPER (300950) 161.0 bus to 5LAMAR (300794) 161.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7JASPER (300949) 345.0 bus to 5JASPER (300950) 345.0 bus CKT 1 d. 2. Trip branch from 5JASPER (300950) 161.0 bus to 5LAMAR (300794) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_532797_WOLFCRK7-532794_ROSEHIL7_Ckt1 | 3 Phase fault on WOLFCRK7 (532797) 345.0 kV a. Apply fault on WOLFCRK7 (532797) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509755_WEKIWA-7-514803_SOONER_Ckt1 | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WEKIWA-7 (509755) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_510406_NES-7-510380_DELWARE7_Ckt1 | 3 Phase fault on N.E.S.-7 (510406) 345.0 kV a. Apply fault on N.E.S.-7 (510406) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512694_CLEVLND7-560056_G15-066T_Ckt1 | 3 Phase fault on CLEVLND7 (512694) 345.0 kV a. Apply fault on CLEVLND7 (512694) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512694_CLEVLND7-300138_4CLEVLND_3Winding | 3 Phase fault on CLEVLND7 (512694) 345.0 kV a. Apply fault on CLEVLND7 (512694) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CLEVLND1 (512817) to trip transformer at CLEVLND1 13.8 kV bus b. 2. Trip branch from CLEVLND (512729) 138.0 bus to 4CLEVLND (300138) 138.0 bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CLEVLND (512729) 138.0 bus to 4CLEVLND (300138) 138.0 bus CKT Z1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CLEVLND (512729) 138.0 bus to 4CLEVLND (300138) 138.0 bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509895_TNO2-4-509817_TNO--4_Ckt1 | 3 Phase fault on T.NO.2-4 (509895) 138.0 kV a. Apply fault on T.NO.2-4 (509895) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.2-4 (509895) 138.0 kV bus to T.NO.--4 (509817) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.2-4 (509895) 138.0 kV bus to T.NO.--4 (509817) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.2-4 (509895) 138.0 kV bus to T.NO.--4 (509817) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509895_TNO2-4-509852_TNO--7_3Winding | 3 Phase fault on T.NO.2-4 (509895) 138.0 kV a. Apply fault on T.NO.2-4 (509895) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TNO2-1 (509894) to trip transformer at TNO2-1 34.500 (509894) 34.5 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_513591_HERRON-513590_CUSTDAY1_Ckt1 | 3 Phase fault on HERRON (513591) 161.0 kV a. Apply fault on HERRON (513591) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus CUSTDAY1 (513590) 161.0 kV bus b. 2. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_513591_HERRON-513596_IGLOOV_3Winding | 3 Phase fault on HERRON (513591) 161.0 kV a. Apply fault on HERRON (513591) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HERRON (513591) 161.0 bus to IGLOOV2 (513595) 161.0 bus CKT 1 b. 2. Disconnect bus at IGLOTER2 (513594) to trip transformer at IGLOTER2 1 13.200 (513594) 13.2 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HERRON (513591) 161.0 bus to IGLOOV2 (513595) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HERRON (513591) 161.0 bus to IGLOOV2 (513595) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_513591_HERRON-513590_CUSTDAY1_Ckt2 | 3 Phase fault on HERRON (513591) 161.0 kV a. Apply fault on HERRON (513591) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus CUSTDAY1 (513590) 161.0 kV bus b. 2. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HERRON (513591) 161.0 bus to CUSTDAY1 (513590) 161.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512671_HUNT-512656_GRDA1_3Winding | 3 Phase fault on HUNT (512671) 69.0 kV a. Apply fault on HUNT (512671) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUNT (512671) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69.0 bus to GRDA1 (512727) 69.0 bus CKT 1 b. 3. Disconnect bus at GRDA1 (512816) to trip transformer at GRDA1 1 13.8 kV bus b. 4. Drop load from bus HUNT (512671) 69.0 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HUNT (512671) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 c. 2. Reclose branch from MAIDTP2 (512625) 69.0 bus to GRDA1 (512727) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HUNT (512671) 69.0 bus to MAIDTP2 (512625) 69.0 bus CKT 1 d. 2. Trip branch from MAIDTP2 (512625) 69.0 bus to GRDA1 (512727) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_512671_HUNT-512810_PRYORC12_Ckt1 | 3 Phase fault on HUNT (512671) 69.0 kV a. Apply fault on HUNT (512671) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUNT (512671) 69.0 bus to PRY0RC22 (512639) 69.0 bus CKT 1 b. 2. Drop load from bus PRY0RC22 (512639) 69.0 kV bus b. 3. Trip branch from PRY0RC22 (512639) 69.0 bus to PRYORC32 (512622) 69.0 bus CKT 1 b. 4. Drop load from bus PRYORC32 (512622) 69.0 kV bus b. 5. Trip branch from PRYORC32 (512622) 69.0 bus to PRYORC12 (512810) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from HUNT (512671) 69.0 bus to PRY0RC22 (512639) 69.0 bus CKT 1 c. 2. Reclose branch from PRY0RC22 (512639) 69.0 bus to PRYORC32 (512622) 69.0 bus CKT 1 c. 3. Reclose branch from PRYORC32 (512622) 69.0 bus to PRYORC12 (512810) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from HUNT (512671) 69.0 bus to PRY0RC22 (512639) 69.0 bus CKT 1 d. 2. Trip branch from PRY0RC22 (512639) 69.0 bus to PRYORC32 (512622) 69.0 bus CKT 1 d. 3. Trip branch from PRYORC32 (512622) 69.0 bus to PRYORC12 (512810) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_506934_FLINTCR5-504201_GENTRY_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus GENTRY (504201) 161.0 kV bus b. 2. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509817_TNO--4-509842_CDC-WT_Ckt1 | 3 Phase fault on T.NO.--4 (509817) 138.0 kV a. Apply fault on T.NO.--4 (509817) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512648_MAID | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a. Apply single-phase fault on MAID (512648) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512648) 161.0 kV bus to 5CHOTEAU1 (300069) 161.0 kV bus CKT 1 b. 2. Trip branch from MAID (512648) 161.0 kV bus to GERALDGAY5 (512760) 161.0 kV bus CKT 1 b. 3. Drop load from bus GERALDGAY5 (512760) 161.0 kV bus b. 4. Trip branch from GERALDGAY5 (512760) 161.0 kV bus to NWMAID5 (512757) 161.0 kV bus CKT 1 b. 5. Drop load from bus NWMAID5 (512757) 161.0 kV bus b. 6. Trip branch from NWMAID5 (512757) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 b. 7. Drop load from bus WMAIN (512742) 161.0 kV bus b. 8. Trip branch from WMAIN (512742) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-300740_7SPORTSMAN | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345.0 kV bus a. Apply single-phase fault on 7SPORTSMAN (300740) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 b. 2. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to 5SPORTSMAN (300741) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-513596_IGLOOV | Single Phase Fault with Stuck Breaker on IGLOOV (513596) 345.0 kV bus a. Apply single-phase fault on IGLOOV (513596) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV (513596) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Disconnect IGLOTER1 (513592) 13.2 kV bus to trip transformer at IGLOTER1 1 13.200 (513592) 13.2 kV bus b. 3. Trip branch from IGLOOV1 (513593) 161.0 kV bus to HERRON (513591) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512635_KERR | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KERR (512635) 161.0 kV bus to 412SUB (512637) 161.0 kV bus CKT 1 b. 2. Drop load from bus 412SUB (512637) 161.0 kV bus b. 3. Trip branch from 412SUB (512637) 161.0 kV bus to KANSATP5 (512714) 161.0 kV bus CKT 1 b. 4. Trip branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512638_CATSAGR5 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161.0 kV bus a. Apply single-phase fault on CATSAGR5 (512638) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CATSAGR5 (512638) 161.0 kV bus to 5ELMCRK (300993) 161.0 kV bus CKT 1 b. 2. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 3. Drop load from bus 5ELMCRK (300993) 161.0 kV bus b. 4. Trip branch from 5ELMCRK (300993) 161.0 kV bus to COLINS (512627) 161.0 kV bus CKT 1 b. 5. Trip branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512626_MAID | Single Phase Fault with Stuck Breaker on MAID (512626) 69.0 kV bus a. Apply single-phase fault on MAID (512626) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MAID (512626) 69.0 kV bus to AMERCAST (512681) 69.0 kV bus CKT 1 b. 2. Drop load from bus AMERCAST (512681) 69.0 kV bus b. 3. Trip branch from AMERCAST (512681) 69.0 kV bus to CPPTAP (512661) 69.0 kV bus CKT 1 b. 4. Trip branch from CPPTAP (512661) 69.0 kV bus to PRYORCHEM2 (512699) 69.0 kV bus CKT 1 b. 5. Drop load from bus PRYORCHEM2 (512699) 69.0 kV bus b. 6. Trip branch from PRYORCHEM2 (512699) 69.0 kV bus to AIRPROD2 (512687) 69.0 kV bus CKT 1 b. 7. Drop load from bus AIRPROD2 (512687) 69.0 kV bus b. 8. Trip branch from AIRPROD2 (512687) 69.0 kV bus to HUNT (512671) 69.0 kV bus CKT 1 b. 9. Disconnect MAITER1 (512836) 13.2 kV bus to trip transformer at MAITER1 1 13.200 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512700_WAGNOR | Single Phase Fault with Stuck Breaker on WAGNOR (512700) 161.0 kV bus a. Apply single-phase fault on WAGNOR (512700) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WAGNOR1 (512818) 13.8 kV bus to trip transformer at WAGNOR1 13.8 kV bus b. 2. Trip branch from WAGNOR (512700) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-301344_5CDRCRST | Single Phase Fault with Stuck Breaker on 5CDRCRST (301344) 161.0 kV bus a. Apply single-phase fault on 5CDRCRST (301344) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161.0 kV bus to LOCSTGVKM (513050) 161.0 kV bus CKT 1 b. 2. Drop load from bus LOCSTGVKM (513050) 161.0 kV bus b. 3. Trip branch from LOCSTGVKM (513050) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 4. Trip branch from 5CDRCRST (301344) 161.0 kV bus to 2CDRCRST (301345) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-300739_7BLACKBERRY | Single Phase Fault with Stuck Breaker on 7BLACKBERRY (300739) 345.0 kV bus a. Apply single-phase fault on 7BLACKBERRY (300739) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 b. 2. Trip branch from 7BLACKBERRY (300739) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-300741_5SPORTSMAN | Single Phase Fault with Stuck Breaker on 5SPORTSMAN (300741) 161.0 kV bus a. Apply single-phase fault on 5SPORTSMAN (300741) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 5CHOTEAU2 (301348) 161.0 kV bus CKT 1 b. 2. Trip branch from 5SPORTSMAN (300741) 161.0 kV bus to 7SPORTSMAN (300740) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512654_PENSA | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a. Apply single-phase fault on PENSA (512654) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus KETCHUM5 (512669) 161.0 kV bus b. 2. Trip branch from PENSA (512654) 161.0 kV bus to KETCHUM5 (512669) 161.0 kV bus CKT 1 b. 3. Disconnect PENSA (512841) 13.8 kV bus to trip transformer at PENSA 1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-509790_CATOOSA4 | Single Phase Fault with Stuck Breaker on CATOOSA4 (509790) 138.0 kV bus a. Apply single-phase fault on CATOOSA4 (509790) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CATOOSA4 (509790) 138.0 kV bus to INOLATP4 (509752) 138.0 kV bus CKT 1 b. 2. Trip branch from CATOOSA4 (509790) 138.0 kV bus to TERNITP4 (509835) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512651_CLARMR | Single Phase Fault with Stuck Breaker on CLARMR (512651) 161.0 kV bus a. Apply single-phase fault on CLARMR (512651) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect CLARMR4 (512813) 13.8 kV bus to trip transformer at CLARMR4 13.8 kV bus b. 2. Trip branch from CLARMR (512707) 138.0 kV bus to OOLOGAHKM (513124) 138.0 kV bus CKT 1 b. 3. Drop load from bus OOLOGAHKM (513124) 138.0 kV bus b. 4. Trip branch from OOLOGAHKM (513124) 138.0 kV bus to N.E.S.-4 (510396) 138.0 kV bus CKT 1 b. 5. Disconnect CLARMR2 (512815) 13.8 kV bus to trip transformer at CLARMR2 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512655_TAHLQH | Single Phase Fault with Stuck Breaker on TAHLQH (512655) 161.0 kV bus a. Apply single-phase fault on TAHLQH (512655) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus 7CLANS (515956) 161.0 kV bus b. 2. Trip branch from TAHLQH (512655) 161.0 kV bus to 7CLANS (515956) 161.0 kV bus CKT 1 b. 3. Trip branch from TAHLQH (512655) 161.0 kV bus to BRIGSKM (513044) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-532797_WOLFCRK7 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a. Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 b. 2. Trip branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-512671_HUNT | Single Phase Fault with Stuck Breaker on HUNT (512671) 69.0 kV bus a. Apply single-phase fault on HUNT (512671) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from HUNT (512671) 69.0 kV bus to MAIDTP2 (512625) 69.0 kV bus CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69.0 kV bus to GRDA1 (512727) 69.0 kV bus CKT 1 b. 3. Disconnect GRDA1 (512816) 13.8 kV bus to trip transformer at GRDA1 1 13.8 kV bus b. 4. Trip branch from HUNT (512671) 69.0 kV bus to PRY0RC22 (512639) 69.0 kV bus CKT 1 b. 5. Drop load from bus PRY0RC22 (512639) 69.0 kV bus b. 6. Trip branch from PRY0RC22 (512639) 69.0 kV bus to PRYORC32 (512622) 69.0 kV bus CKT 1 b. 7. Drop load from bus PRYORC32 (512622) 69.0 kV bus b. 8. Trip branch from PRYORC32 (512622) 69.0 kV bus to PRYORC12 (512810) 69.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-509817_TNO--4 | Single Phase Fault with Stuck Breaker on T.NO.--4 (509817) 138.0 kV bus a. Apply single-phase fault on T.NO.--4 (509817) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--4 (509817) 138.0 kV bus to T.NO.2-4 (509895) 138.0 kV bus CKT 1 b. 2. Trip branch from T.NO.--4 (509817) 138.0 kV bus to CDC-WT (509842) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515375_WWRDEHV7-560071_G16-003-TAP_Ckt2 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515375_WWRDEHV7-560071_G16-003-TAP_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515375_WWRDEHV7-515407_TATONGA7_Ckt2 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515375_WWRDEHV7-515407_TATONGA7_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515375_WWRDEHV7-515852_DGRASSE7_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515375_WWRDEHV7-515852_DGRASSE7_Ckt2 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to DGRASSE7 (515852) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515375_WWRDEHV7-755000_WWDBORDT_Ckt1 | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV7 (515375) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515375_WWRDEHV7-515376_WWRDEHV4_3Winding | 3 Phase fault on WWRDEHV7 (515375) 345.0 kV a. Apply fault on WWRDEHV7 (515375) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at WWDEHV31 (515795) to trip transformer at WWDEHV31 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515407_TATONGA7-515497_MATHWSN7_Ckt2 | 3 Phase fault on TATONGA7 (515407) 345.0 kV a. Apply fault on TATONGA7 (515407) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515407_TATONGA7-515497_MATHWSN7_Ckt1 | 3 Phase fault on TATONGA7 (515407) 345.0 kV a. Apply fault on TATONGA7 (515407) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515852_DGRASSE7-539801_THISTLE7_Ckt1 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515852_DGRASSE7-539801_THISTLE7_Ckt2 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to THISTLE7 (539801) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515852_DGRASSE7-515853_DGRASSE4_3Winding | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at DGRASSE1 (515854) to trip transformer at DGRASSE1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_560071_G16-003-TAP-515677_BADGER_Ckt2 | 3 Phase fault on G16-003-TAP (560071) 345.0 kV a. Apply fault on G16-003-TAP (560071) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_560071_G16-003-TAP-515677_BADGER_Ckt1 | 3 Phase fault on G16-003-TAP (560071) 345.0 kV a. Apply fault on G16-003-TAP (560071) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_755000_WWDBORDT-525832_TUCO_INT_Ckt1 | 3 Phase fault on WWDBORDT (755000) 345.0 kV a. Apply fault on WWDBORDT (755000) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 bus to TUCO_INT (525832) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWDBORDT (755000) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. 2. Reclose branch from BORDER (515458) 345.0 bus to TUCO_INT (525832) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWDBORDT (755000) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. 2. Trip branch from BORDER (515458) 345.0 bus to TUCO_INT (525832) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_755000_WWDBORDT-511553_CHISHOLM7_Ckt1 | 3 Phase fault on WWDBORDT (755000) 345.0 kV a. Apply fault on WWDBORDT (755000) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515376_WWRDEHV4-515533_REDCLFT4_Ckt1 | 3 Phase fault on WWRDEHV4 (515376) 138.0 kV a. Apply fault on WWRDEHV4 (515376) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to IODINE-4 (514796) 138.0 bus CKT 1 b. 2. Drop load from bus IODINE-4 (514796) 138.0 kV bus b. 3. Trip branch from IODINE-4 (514796) 138.0 bus to REDCLFT4 (515533) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV4 (515376) 138.0 bus to IODINE-4 (514796) 138.0 bus CKT 1 c. 2. Reclose branch from IODINE-4 (514796) 138.0 bus to REDCLFT4 (515533) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to IODINE-4 (514796) 138.0 bus CKT 1 d. 2. Trip branch from IODINE-4 (514796) 138.0 bus to REDCLFT4 (515533) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515376_WWRDEHV4-515375_WWRDEHV7_3Winding | 3 Phase fault on WWRDEHV4 (515376) 138.0 kV a. Apply fault on WWRDEHV4 (515376) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WWDEHV21 (515799) to trip transformer at WWDEHV21 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515376_WWRDEHV4-514785_WOODWRD4_Ckt1 | 3 Phase fault on WWRDEHV4 (515376) 138.0 kV a. Apply fault on WWRDEHV4 (515376) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to WWDPST (515425) 138.0 bus CKT 1 b. 2. Trip branch from WWDPST (515425) 138.0 bus to WOODWRD4 (514785) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWRDEHV4 (515376) 138.0 bus to WWDPST (515425) 138.0 bus CKT 1 c. 2. Reclose branch from WWDPST (515425) 138.0 bus to WOODWRD4 (514785) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWRDEHV4 (515376) 138.0 bus to WWDPST (515425) 138.0 bus CKT 1 d. 2. Trip branch from WWDPST (515425) 138.0 bus to WOODWRD4 (514785) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511553_CHISHOLM7-560078_G16-037-TAP_Ckt1 | 3 Phase fault on CHISHOLM7 (511553) 345.0 kV a. Apply fault on CHISHOLM7 (511553) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511553_CHISHOLM7-511557_CHISHOLM6_3Winding | 3 Phase fault on CHISHOLM7 (511553) 345.0 kV a. Apply fault on CHISHOLM7 (511553) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CHISHOLM1 (511558) to trip transformer at CHISHOLM1 13.200 (511558) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_539801_THISTLE7-532782_BUFFALO7_Ckt1 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_539801_THISTLE7-532782_BUFFALO7_Ckt2 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515853_DGRASSE4-520436_ROSEVLY4_Ckt1 | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515853_DGRASSE4-514795_KNOBHIL4_Ckt1 | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515853_DGRASSE4-515852_DGRASSE7_3Winding | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at DGRASSE1 (515854) to trip transformer at DGRASSE1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515853_DGRASSE4-520999_MOORLND4_Ckt1 | 3 Phase fault on DGRASSE4 (515853) 138.0 kV a. Apply fault on DGRASSE4 (515853) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE4 (515853) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_560078_G16-037-TAP-515800_GRACMNT7_Ckt1 | 3 Phase fault on G16-037-TAP (560078) 345.0 kV a. Apply fault on G16-037-TAP (560078) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G16-037-TAP (560078) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G16-037-TAP (560078) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511557_CHISHOLM6-511541_SWEETWT6_Ckt1 | 3 Phase fault on CHISHOLM6 (511557) 230.0 kV a. Apply fault on CHISHOLM6 (511557) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM6 (511557) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM6 (511557) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511557_CHISHOLM6-511458_ELKCTY-4_3Winding | 3 Phase fault on CHISHOLM6 (511557) 230.0 kV a. Apply fault on CHISHOLM6 (511557) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230.0 bus to ELKCITY6 (511490) 230.0 bus CKT 1 b. 2. Disconnect bus at ELKC2-1 (511482) to trip transformer at ELKC2-1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM6 (511557) 230.0 bus to ELKCITY6 (511490) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM6 (511557) 230.0 bus to ELKCITY6 (511490) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511557_CHISHOLM6-511553_CHISHOLM7_3Winding | 3 Phase fault on CHISHOLM6 (511557) 230.0 kV a. Apply fault on CHISHOLM6 (511557) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CHISHOLM1 (511558) to trip transformer at CHISHOLM1 13.200 (511558) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525832_TUCO_INT-755000_WWDBORDT_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 c. 2. Reclose branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 bus to BORDER (515458) 345.0 bus CKT 1 d. 2. Trip branch from BORDER (515458) 345.0 bus to WWDBORDT (755000) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_525832_TUCO_INT-762216_G17-151TAP_Ckt1 | 3 Phase fault on TUCO_INT (525832) 345.0 kV a. Apply fault on TUCO_INT (525832) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-515375_WWRDEHV7 | Single Phase Fault with Stuck Breaker on WWRDEHV7 (515375) 345.0 kV bus a. Apply single-phase fault on WWRDEHV7 (515375) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 b. 2. Trip branch from WWRDEHV7 (515375) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-515407_TATONGA7 | Single Phase Fault with Stuck Breaker on TATONGA7 (515407) 345.0 kV bus a. Apply single-phase fault on TATONGA7 (515407) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 2 b. 2. Trip branch from TATONGA7 (515407) 345.0 kV bus to MATHWSN7 (515497) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-515852_DGRASSE7 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345.0 kV bus a. Apply single-phase fault on DGRASSE7 (515852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 b. 2. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-560071_G16-003-TAP | Single Phase Fault with Stuck Breaker on G16-003-TAP (560071) 345.0 kV bus a. Apply single-phase fault on G16-003-TAP (560071) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from G16-003-TAP (560071) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 b. 2. Trip branch from G16-003-TAP (560071) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-755000_WWDBORDT | Single Phase Fault with Stuck Breaker on WWDBORDT (755000) 345.0 kV bus a. Apply single-phase fault on WWDBORDT (755000) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 4. Trip branch from WWDBORDT (755000) 345.0 kV bus to CHISHOLM7 (511553) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-515376_WWRDEHV4 | Single Phase Fault with Stuck Breaker on WWRDEHV4 (515376) 138.0 kV bus a. Apply single-phase fault on WWRDEHV4 (515376) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138.0 kV bus to IODINE-4 (514796) 138.0 kV bus CKT 1 b. 2. Drop load from bus IODINE-4 (514796) 138.0 kV bus b. 3. Trip branch from IODINE-4 (514796) 138.0 kV bus to REDCLFT4 (515533) 138.0 kV bus CKT 1 b. 4. Disconnect WWDEHV31 (515795) 13.8 kV bus to trip transformer at WWDEHV31 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-511553_CHISHOLM7 | Single Phase Fault with Stuck Breaker on CHISHOLM7 (511553) 345.0 kV bus a. Apply single-phase fault on CHISHOLM7 (511553) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to G16-037-TAP (560078) 345.0 kV bus CKT 1 b. 2. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-515497_MATHWSN7 | Single Phase Fault with Stuck Breaker on MATHWSN7 (515497) 345.0 kV bus a. Apply single-phase fault on MATHWSN7 (515497) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 2 b. 2. Trip branch from MATHWSN7 (515497) 345.0 kV bus to TATONGA7 (515407) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-539801_THISTLE7 | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345.0 kV bus a. Apply single-phase fault on THISTLE7 (539801) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 1 b. 2. Trip branch from THISTLE7 (539801) 345.0 kV bus to BUFFALO7 (532782) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-515677_BADGER | Single Phase Fault with Stuck Breaker on BADGER (515677) 345.0 kV bus a. Apply single-phase fault on BADGER (515677) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BADGER (515677) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 2 b. 2. Trip branch from BADGER (515677) 345.0 kV bus to G16-003-TAP (560071) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-525832_TUCO_INT | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a. Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Drop switching device from bus BORDER (515458) 345.0 kV bus b. 3. Trip branch from BORDER (515458) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 b. 4. Trip branch from TUCO_INT (525832) 345.0 kV bus to G17-151TAP (762216) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511541_SWEETWT6-511557_CHISHOLM6_Ckt1 | 3 Phase fault on SWEETWT6 (511541) 230.0 kV a. Apply fault on SWEETWT6 (511541) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230.0 kV bus to CHISHOLM6 (511557) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWEETWT6 (511541) 230.0 kV bus to CHISHOLM6 (511557) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWEETWT6 (511541) 230.0 kV bus to CHISHOLM6 (511557) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2019-013 (763541) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511541_SWEETWT6-523777_WHEELER_Ckt1 | 3 Phase fault on SWEETWT6 (511541) 230.0 kV a. Apply fault on SWEETWT6 (511541) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 b. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to WHEELER (523777) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SWEETWT6 (511541) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 c. 2. Reclose branch from STLN-DEMARC6230.00 (523779) 230.0 bus to WHEELER (523777) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SWEETWT6 (511541) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 d. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to WHEELER (523777) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523777_WHEELER-523771_GRAPEVINE_Ckt1 | 3 Phase fault on WHEELER (523777) 230.0 kV a. Apply fault on WHEELER (523777) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER (523777) 230.0 kV bus to GRAPEVINE (523771) 230.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WHEELER (523777) 230.0 kV bus to GRAPEVINE (523771) 230.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WHEELER (523777) 230.0 kV bus to GRAPEVINE (523771) 230.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523777_WHEELER-511541_SWEETWT6_Ckt1 | 3 Phase fault on WHEELER (523777) 230.0 kV a. Apply fault on WHEELER (523777) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER (523777) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 b. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to SWEETWT6 (511541) 230.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WHEELER (523777) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 c. 2. Reclose branch from STLN-DEMARC6230.00 (523779) 230.0 bus to SWEETWT6 (511541) 230.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WHEELER (523777) 230.0 bus to STLN-DEMARC6230.00 (523779) 230.0 bus CKT 1 d. 2. Trip branch from STLN-DEMARC6230.00 (523779) 230.0 bus to SWEETWT6 (511541) 230.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_523777_WHEELER-523776_WHEELER_3Winding | 3 Phase fault on WHEELER (523777) 230.0 kV a. Apply fault on WHEELER (523777) 230.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at WHEELER_TR1113.200 (523774) to trip transformer at WHEELER_TR1113.200 (523774) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_511553_CHISHOLM7-755000_WWDBORDT_Ckt1 | 3 Phase fault on CHISHOLM7 (511553) 345.0 kV a. Apply fault on CHISHOLM7 (511553) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHISHOLM7 (511553) 345.0 kV bus to WWDBORDT (755000) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_755000_WWDBORDT-515375_WWRDEHV7_Ckt1 | 3 Phase fault on WWDBORDT (755000) 345.0 kV a. Apply fault on WWDBORDT (755000) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WWDBORDT (755000) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WWDBORDT (755000) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515852_DGRASSE7-515375_WWRDEHV7_Ckt1 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_515852_DGRASSE7-515375_WWRDEHV7_Ckt2 | 3 Phase fault on DGRASSE7 (515852) 345.0 kV a. Apply fault on DGRASSE7 (515852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DGRASSE7 (515852) 345.0 kV bus to WWRDEHV7 (515375) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514795_KNOBHIL4-514794_KNOBHIL2_3Winding | 3 Phase fault on KNOBHIL4 (514795) 138.0 kV a. Apply fault on KNOBHIL4 (514795) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at KNOBHIL1 (515732) to trip transformer at KNOBHIL1 13.200 (515732) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514795_KNOBHIL4-520430_NOELSW_Ckt2 | 3 Phase fault on KNOBHIL4 (514795) 138.0 kV a. Apply fault on KNOBHIL4 (514795) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 2 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514795_KNOBHIL4-520430_NOELSW_Ckt1 | 3 Phase fault on KNOBHIL4 (514795) 138.0 kV a. Apply fault on KNOBHIL4 (514795) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_520436_ROSEVLY4-520430_NOELSW_Ckt1 | 3 Phase fault on ROSEVLY4 (520436) 138.0 kV a. Apply fault on ROSEVLY4 (520436) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_520436_ROSEVLY4-520601_AVARD_Ckt1 | 3 Phase fault on ROSEVLY4 (520436) 138.0 kV a. Apply fault on ROSEVLY4 (520436) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus AVARD (520601) 138.0 kV bus b. 2. Trip branch from ROSEVLY4 (520436) 138.0 bus to AVARD (520601) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ROSEVLY4 (520436) 138.0 bus to AVARD (520601) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ROSEVLY4 (520436) 138.0 bus to AVARD (520601) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_520999_MOORLND4-520848_CDRDLTP4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 bus to PIC4 (520425) 138.0 bus CKT 1 b. 2. Drop load from bus PIC4 (520425) 138.0 kV bus b. 3. Trip branch from PIC4 (520425) 138.0 bus to CDRDLTP4 (520848) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to PIC4 (520425) 138.0 bus CKT 1 c. 2. Reclose branch from PIC4 (520425) 138.0 bus to CDRDLTP4 (520848) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to PIC4 (520425) 138.0 bus CKT 1 d. 2. Trip branch from PIC4 (520425) 138.0 bus to CDRDLTP4 (520848) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_520999_MOORLND4-514778_CLEOCOR4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 bus to GLASMTN4 (514788) 138.0 bus CKT 1 b. 2. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 3. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 4. Trip branch from GLASMTN4 (514788) 138.0 bus to CLEOCOR4 (514778) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to GLASMTN4 (514788) 138.0 bus CKT 1 c. 2. Reclose branch from GLASMTN4 (514788) 138.0 bus to CLEOCOR4 (514778) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to GLASMTN4 (514788) 138.0 bus CKT 1 d. 2. Trip branch from GLASMTN4 (514788) 138.0 bus to CLEOCOR4 (514778) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_520999_MOORLND4-515785_WINDFRM4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_520999_MOORLND4-520553_SEILING4_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SEILING4 (520553) 138.0 kV bus b. 2. Trip branch from MOORLND4 (520999) 138.0 bus to SEILING4 (520553) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to SEILING4 (520553) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to SEILING4 (520553) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_520999_MOORLND4-520462_ASPEN_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus ASPEN (520462) 138.0 kV bus b. 2. Trip branch from MOORLND4 (520999) 138.0 bus to ASPEN (520462) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to ASPEN (520462) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to ASPEN (520462) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_520999_MOORLND4-521197_CRTSJCT2_3Winding | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at MLNDTERT (521180) to trip transformer at MLNDTERT 2.4000 (521180) 2.4000000953674316 kV bus b. 2. Trip branch from MOORLND2 (520995) 69.0 bus to CRTSJCT2 (521197) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND2 (520995) 69.0 bus to CRTSJCT2 (521197) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND2 (520995) 69.0 bus to CRTSJCT2 (521197) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_520999_MOORLND4-520957_IODINE_Ckt1 | 3 Phase fault on MOORLND4 (520999) 138.0 kV a. Apply fault on MOORLND4 (520999) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus IODINE (520957) 138.0 kV bus b. 2. Trip branch from MOORLND4 (520999) 138.0 bus to IODINE (520957) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from MOORLND4 (520999) 138.0 bus to IODINE (520957) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from MOORLND4 (520999) 138.0 bus to IODINE (520957) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_539801_THISTLE7-539800_CLARKCOUNTY734500_Ckt1 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_539801_THISTLE7-539800_CLARKCOUNTY734500_Ckt2 | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE7 (539801) 345.0 kV bus to CLARKCOUNTY7345.00 (539800) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_539801_THISTLE7-539638_FLATRDG4_3Winding | 3 Phase fault on THISTLE7 (539801) 345.0 kV a. Apply fault on THISTLE7 (539801) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at THISTLE (539802) to trip transformer at THISTLE T1 13.8 kV bus b. 2. Trip branch from THISTLE4 (539804) 138.0 bus to FLATRDG4 (539638) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from THISTLE4 (539804) 138.0 bus to FLATRDG4 (539638) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from THISTLE4 (539804) 138.0 bus to FLATRDG4 (539638) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_520430_NOELSW-521200_DRIFTWD4_Ckt1 | 3 Phase fault on NOELSW (520430) 138.0 kV a. Apply fault on NOELSW (520430) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW (520430) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 b. 2. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 3. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 4. Trip branch from SALTPLN4 (520437) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 b. 5. Drop load from bus CHRKCTY4 (520431) 138.0 kV bus b. 6. Trip branch from CHRKCTY4 (520431) 138.0 bus to DRIFTWD4 (521200) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NOELSW (520430) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 c. 2. Reclose branch from SALTPLN4 (520437) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 c. 3. Reclose branch from CHRKCTY4 (520431) 138.0 bus to DRIFTWD4 (521200) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NOELSW (520430) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 d. 2. Trip branch from SALTPLN4 (520437) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 d. 3. Trip branch from CHRKCTY4 (520431) 138.0 bus to DRIFTWD4 (521200) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514794_KNOBHIL2-514795_KNOBHIL4_3Winding | 3 Phase fault on KNOBHIL2 (514794) 69.0 kV a. Apply fault on KNOBHIL2 (514794) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at KNOBHIL1 (515732) to trip transformer at KNOBHIL1 13.200 (515732) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514794_KNOBHIL2-514792_ALVAOGE2_Ckt1 | 3 Phase fault on KNOBHIL2 (514794) 69.0 kV a. Apply fault on KNOBHIL2 (514794) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69.0 kV bus to ALVAOGE2 (514792) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL2 (514794) 69.0 kV bus to ALVAOGE2 (514792) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL2 (514794) 69.0 kV bus to ALVAOGE2 (514792) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_514794_KNOBHIL2-515371_HELENAT2_Ckt1 | 3 Phase fault on KNOBHIL2 (514794) 69.0 kV a. Apply fault on KNOBHIL2 (514794) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69.0 bus to CZYCRVT2 (515560) 69.0 bus CKT 1 b. 2. Drop load from bus CZYCRVT2 (515560) 69.0 kV bus b. 3. Drop fixed shunt from bus CZYCRVT2 (515560) 69.0 kV bus b. 4. Trip branch from CZYCRVT2 (515560) 69.0 bus to SALINE (514716) 69.0 bus CKT 1 b. 5. Drop load from bus SALINE (514716) 69.0 kV bus b. 6. Trip branch from SALINE (514716) 69.0 bus to HELENAT2 (515371) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOBHIL2 (514794) 69.0 bus to CZYCRVT2 (515560) 69.0 bus CKT 1 c. 2. Reclose branch from CZYCRVT2 (515560) 69.0 bus to SALINE (514716) 69.0 bus CKT 1 c. 3. Reclose branch from SALINE (514716) 69.0 bus to HELENAT2 (515371) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOBHIL2 (514794) 69.0 bus to CZYCRVT2 (515560) 69.0 bus CKT 1 d. 2. Trip branch from CZYCRVT2 (515560) 69.0 bus to SALINE (514716) 69.0 bus CKT 1 d. 3. Trip branch from SALINE (514716) 69.0 bus to HELENAT2 (515371) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_532782_BUFFALO7-532796_WICHITA7_Ckt1 | 3 Phase fault on BUFFALO7 (532782) 345.0 kV a. Apply fault on BUFFALO7 (532782) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_532782_BUFFALO7-532796_WICHITA7_Ckt2 | 3 Phase fault on BUFFALO7 (532782) 345.0 kV a. Apply fault on BUFFALO7 (532782) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_521200_DRIFTWD4-520430_NOELSW_Ckt1 | 3 Phase fault on DRIFTWD4 (521200) 138.0 kV a. Apply fault on DRIFTWD4 (521200) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD4 (521200) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 b. 2. Drop load from bus CHRKCTY4 (520431) 138.0 kV bus b. 3. Trip branch from CHRKCTY4 (520431) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 b. 4. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 5. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 6. Trip branch from SALTPLN4 (520437) 138.0 bus to NOELSW (520430) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DRIFTWD4 (521200) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 c. 2. Reclose branch from CHRKCTY4 (520431) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 c. 3. Reclose branch from SALTPLN4 (520437) 138.0 bus to NOELSW (520430) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DRIFTWD4 (521200) 138.0 bus to CHRKCTY4 (520431) 138.0 bus CKT 1 d. 2. Trip branch from CHRKCTY4 (520431) 138.0 bus to SALTPLN4 (520437) 138.0 bus CKT 1 d. 3. Trip branch from SALTPLN4 (520437) 138.0 bus to NOELSW (520430) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_521200_DRIFTWD4-520432_BYRONTP4_Ckt1 | 3 Phase fault on DRIFTWD4 (521200) 138.0 kV a. Apply fault on DRIFTWD4 (521200) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD4 (521200) 138.0 kV bus to BYRONTP4 (520432) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DRIFTWD4 (521200) 138.0 kV bus to BYRONTP4 (520432) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DRIFTWD4 (521200) 138.0 kV bus to BYRONTP4 (520432) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_521200_DRIFTWD4-521201_DRIFTWD2_3Winding | 3 Phase fault on DRIFTWD4 (521200) 138.0 kV a. Apply fault on DRIFTWD4 (521200) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at DRFTWDTERT (521185) to trip transformer at DRFTWDTERT 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-515853_DGRASSE4 | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138.0 kV bus a. Apply single-phase fault on DGRASSE4 (515853) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 b. 2. Trip branch from DGRASSE4 (515853) 138.0 kV bus to KNOBHIL4 (514795) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-514795_KNOBHIL4 | Single Phase Fault with Stuck Breaker on KNOBHIL4 (514795) 138.0 kV bus a. Apply single-phase fault on KNOBHIL4 (514795) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL4 (514795) 138.0 kV bus to DGRASSE4 (515853) 138.0 kV bus CKT 1 b. 2. Disconnect KNOBHIL1 (515732) 13.2 kV bus to trip transformer at KNOBHIL1 13.200 (515732) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-520436_ROSEVLY4 | Single Phase Fault with Stuck Breaker on ROSEVLY4 (520436) 138.0 kV bus a. Apply single-phase fault on ROSEVLY4 (520436) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to DGRASSE4 (515853) 138.0 kV bus CKT 1 b. 2. Trip branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-520999_MOORLND4 | Single Phase Fault with Stuck Breaker on MOORLND4 (520999) 138.0 kV bus a. Apply single-phase fault on MOORLND4 (520999) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138.0 kV bus to PIC4 (520425) 138.0 kV bus CKT 1 b. 2. Drop load from bus PIC4 (520425) 138.0 kV bus b. 3. Trip branch from PIC4 (520425) 138.0 kV bus to CDRDLTP4 (520848) 138.0 kV bus CKT 1 b. 4. Trip branch from MOORLND4 (520999) 138.0 kV bus to GLASMTN4 (514788) 138.0 kV bus CKT 1 b. 5. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 6. Drop load from bus GLASMTN4 (514788) 138.0 kV bus b. 7. Trip branch from GLASMTN4 (514788) 138.0 kV bus to CLEOCOR4 (514778) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-520430_NOELSW | Single Phase Fault with Stuck Breaker on NOELSW (520430) 138.0 kV bus a. Apply single-phase fault on NOELSW (520430) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW (520430) 138.0 kV bus to SALTPLN4 (520437) 138.0 kV bus CKT 1 b. 2. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 3. Drop load from bus SALTPLN4 (520437) 138.0 kV bus b. 4. Trip branch from SALTPLN4 (520437) 138.0 kV bus to CHRKCTY4 (520431) 138.0 kV bus CKT 1 b. 5. Drop load from bus CHRKCTY4 (520431) 138.0 kV bus b. 6. Trip branch from CHRKCTY4 (520431) 138.0 kV bus to DRIFTWD4 (521200) 138.0 kV bus CKT 1 b. 7. Trip branch from NOELSW (520430) 138.0 kV bus to ROSEVLY4 (520436) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-532782_BUFFALO7 | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345.0 kV bus a. Apply single-phase fault on BUFFALO7 (532782) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 b. 2. Trip branch from BUFFALO7 (532782) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_763010_G19-065-TAP-509076_NWHENDR4_Ckt1 | 3 Phase fault on G19-065-TAP (763010) 138.0 kV a. Apply fault on G19-065-TAP (763010) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G19-065-TAP (763010) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 b. 2. Drop load from bus LONDON (509072) 138.0 kV bus b. 3. Trip branch from LONDON (509072) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 b. 4. Drop load from bus FRIARSW4 (509062) 138.0 kV bus b. 5. Trip branch from FRIARSW4 (509062) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 b. 6. Drop load from bus FRIRSWR4 (509063) 138.0 kV bus b. 7. Trip branch from FRIRSWR4 (509063) 138.0 bus to NWHENDR4 (509076) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G19-065-TAP (763010) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 c. 2. Reclose branch from LONDON (509072) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 c. 3. Reclose branch from FRIARSW4 (509062) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 c. 4. Reclose branch from FRIRSWR4 (509063) 138.0 bus to NWHENDR4 (509076) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G19-065-TAP (763010) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 d. 2. Trip branch from LONDON (509072) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 d. 3. Trip branch from FRIARSW4 (509062) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 d. 4. Trip branch from FRIRSWR4 (509063) 138.0 bus to NWHENDR4 (509076) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_763010_G19-065-TAP-509080_OVERTON4_Ckt1 | 3 Phase fault on G19-065-TAP (763010) 138.0 kV a. Apply fault on G19-065-TAP (763010) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G19-065-TAP (763010) 138.0 kV bus to OVERTON4 (509080) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G19-065-TAP (763010) 138.0 kV bus to OVERTON4 (509080) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G19-065-TAP (763010) 138.0 kV bus to OVERTON4 (509080) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509080_OVERTON4-508548_KNOXLEE4_Ckt1 | 3 Phase fault on OVERTON4 (509080) 138.0 kV a. Apply fault on OVERTON4 (509080) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 b. 2. Drop load from bus LEVERET4 (509069) 138.0 kV bus b. 3. Trip branch from LEVERET4 (509069) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 b. 4. Drop load from bus KILGORR4 (509067) 138.0 kV bus b. 5. Trip branch from KILGORR4 (509067) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 b. 6. Drop load from bus MONROER4 (509073) 138.0 kV bus b. 7. Trip branch from MONROER4 (509073) 138.0 bus to KNOXLEE4 (508548) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON4 (509080) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 c. 2. Reclose branch from LEVERET4 (509069) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 c. 3. Reclose branch from KILGORR4 (509067) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 c. 4. Reclose branch from MONROER4 (509073) 138.0 bus to KNOXLEE4 (508548) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON4 (509080) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 d. 2. Trip branch from LEVERET4 (509069) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 d. 3. Trip branch from KILGORR4 (509067) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 d. 4. Trip branch from MONROER4 (509073) 138.0 bus to KNOXLEE4 (508548) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509080_OVERTON4-509079_OVERTON2_3Winding | 3 Phase fault on OVERTON4 (509080) 138.0 kV a. Apply fault on OVERTON4 (509080) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OVTON1-1 (509097) to trip transformer at OVTON1-1 13.200 (509097) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509080_OVERTON4-509241_CROCKET7_3Winding | 3 Phase fault on OVERTON4 (509080) 138.0 kV a. Apply fault on OVERTON4 (509080) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 b. 2. Trip branch from JACKSNV4 (509242) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 b. 3. Drop load from bus PINEGRV4 (509324) 138.0 kV bus b. 4. Trip branch from PINEGRV4 (509324) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 b. 5. Drop load from bus ALTO (509320) 138.0 kV bus b. 6. Trip branch from ALTO (509320) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 b. 7. Drop load from bus SLOCUM (509326) 138.0 kV bus b. 8. Drop switching device from bus SLOCUM (509326) 138.0 kV bus b. 9. Trip branch from SLOCUM (509326) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 b. 10. Drop load from bus GRAPLND4 (509322) 138.0 kV bus b. 11. Trip branch from GRAPLND4 (509322) 138.0 bus to CROCKET4 (509240) 138.0 bus CKT 1 b. 12. Disconnect bus at CROCK-B1 (509243) to trip transformer at CROCK-B1 13.8 kV bus b. 13. Drop switching device from bus OVERTON4 (509080) 138.0 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON4 (509080) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 c. 2. Reclose branch from JACKSNV4 (509242) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 c. 3. Reclose branch from PINEGRV4 (509324) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 c. 4. Reclose branch from ALTO (509320) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 c. 5. Reclose branch from SLOCUM (509326) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 c. 6. Reclose branch from GRAPLND4 (509322) 138.0 bus to CROCKET4 (509240) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON4 (509080) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 d. 2. Trip branch from JACKSNV4 (509242) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 d. 3. Trip branch from PINEGRV4 (509324) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 d. 4. Trip branch from ALTO (509320) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 d. 5. Trip branch from SLOCUM (509326) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 d. 6. Trip branch from GRAPLND4 (509322) 138.0 bus to CROCKET4 (509240) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509241_CROCKET7-508585_TENRUSK7_Ckt1 | 3 Phase fault on CROCKET7 (509241) 345.0 kV a. Apply fault on CROCKET7 (509241) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509241_CROCKET7-334028_7GRIMES%_Ckt1 | 3 Phase fault on CROCKET7 (509241) 345.0 kV a. Apply fault on CROCKET7 (509241) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509241_CROCKET7-509080_OVERTON4_3Winding | 3 Phase fault on CROCKET7 (509241) 345.0 kV a. Apply fault on CROCKET7 (509241) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CROCK-B1 (509243) to trip transformer at CROCK-B1 13.8 kV bus b. 2. Trip branch from CROCKET4 (509240) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 b. 3. Drop load from bus GRAPLND4 (509322) 138.0 kV bus b. 4. Trip branch from GRAPLND4 (509322) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 b. 5. Drop load from bus SLOCUM (509326) 138.0 kV bus b. 6. Drop switching device from bus SLOCUM (509326) 138.0 kV bus b. 7. Trip branch from SLOCUM (509326) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 b. 8. Drop load from bus ALTO (509320) 138.0 kV bus b. 9. Trip branch from ALTO (509320) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 b. 10. Drop load from bus PINEGRV4 (509324) 138.0 kV bus b. 11. Trip branch from PINEGRV4 (509324) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 b. 12. Trip branch from JACKSNV4 (509242) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CROCKET4 (509240) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 c. 2. Reclose branch from GRAPLND4 (509322) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 c. 3. Reclose branch from SLOCUM (509326) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 c. 4. Reclose branch from ALTO (509320) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 c. 5. Reclose branch from PINEGRV4 (509324) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 c. 6. Reclose branch from JACKSNV4 (509242) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CROCKET4 (509240) 138.0 bus to GRAPLND4 (509322) 138.0 bus CKT 1 d. 2. Trip branch from GRAPLND4 (509322) 138.0 bus to SLOCUM (509326) 138.0 bus CKT 1 d. 3. Trip branch from SLOCUM (509326) 138.0 bus to ALTO (509320) 138.0 bus CKT 1 d. 4. Trip branch from ALTO (509320) 138.0 bus to PINEGRV4 (509324) 138.0 bus CKT 1 d. 5. Trip branch from PINEGRV4 (509324) 138.0 bus to JACKSNV4 (509242) 138.0 bus CKT 1 d. 6. Trip branch from JACKSNV4 (509242) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509079_OVERTON2-508546_KILGORE2_Ckt1 | 3 Phase fault on OVERTON2 (509079) 69.0 kV a. Apply fault on OVERTON2 (509079) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509079_OVERTON2-509080_OVERTON4_3Winding | 3 Phase fault on OVERTON2 (509079) 69.0 kV a. Apply fault on OVERTON2 (509079) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at OVTON1-1 (509097) to trip transformer at OVTON1-1 13.200 (509097) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509079_OVERTON2-509089_TURNERT2_Ckt1 | 3 Phase fault on OVERTON2 (509079) 69.0 kV a. Apply fault on OVERTON2 (509079) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus TURNERT2 (509089) 69.0 kV bus b. 2. Trip branch from OVERTON2 (509079) 69.0 bus to TURNERT2 (509089) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OVERTON2 (509079) 69.0 bus to TURNERT2 (509089) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OVERTON2 (509079) 69.0 bus to TURNERT2 (509089) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509076_NWHENDR4-509078_OAK2HIL4_Ckt1 | 3 Phase fault on NWHENDR4 (509076) 138.0 kV a. Apply fault on NWHENDR4 (509076) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to OAK1HIL4 (509077) 138.0 bus CKT 1 b. 2. Drop load from bus OAK1HIL4 (509077) 138.0 kV bus b. 3. Drop load from bus OAK2HIL4 (509078) 138.0 kV bus b. 4. Trip branch from OAK1HIL4 (509077) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR4 (509076) 138.0 bus to OAK1HIL4 (509077) 138.0 bus CKT 1 c. 2. Reclose branch from OAK1HIL4 (509077) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to OAK1HIL4 (509077) 138.0 bus CKT 1 d. 2. Trip branch from OAK1HIL4 (509077) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-509080_OVERTON4 | Single Phase Fault with Stuck Breaker on OVERTON4 (509080) 138.0 kV bus a. Apply single-phase fault on OVERTON4 (509080) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138.0 kV bus to LEVERET4 (509069) 138.0 kV bus CKT 1 b. 2. Drop load from bus LEVERET4 (509069) 138.0 kV bus b. 3. Trip branch from LEVERET4 (509069) 138.0 kV bus to KILGORR4 (509067) 138.0 kV bus CKT 1 b. 4. Drop load from bus KILGORR4 (509067) 138.0 kV bus b. 5. Trip branch from KILGORR4 (509067) 138.0 kV bus to MONROER4 (509073) 138.0 kV bus CKT 1 b. 6. Drop load from bus MONROER4 (509073) 138.0 kV bus b. 7. Trip branch from MONROER4 (509073) 138.0 kV bus to KNOXLEE4 (508548) 138.0 kV bus CKT 1 b. 8. Trip branch from OVERTON4 (509080) 138.0 kV bus to G19-065-TAP (763010) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509076_NWHENDR4-509075_NWHENDR2_3Winding | 3 Phase fault on NWHENDR4 (509076) 138.0 kV a. Apply fault on NWHENDR4 (509076) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NWHEN2-1 (509096) to trip transformer at NWHEN2-1 13.200 (509096) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509076_NWHENDR4-763010_G19-065-TAP_Ckt1 | 3 Phase fault on NWHENDR4 (509076) 138.0 kV a. Apply fault on NWHENDR4 (509076) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 b. 2. Drop load from bus FRIRSWR4 (509063) 138.0 kV bus b. 3. Trip branch from FRIRSWR4 (509063) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 b. 4. Drop load from bus FRIARSW4 (509062) 138.0 kV bus b. 5. Trip branch from FRIARSW4 (509062) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 b. 6. Drop load from bus LONDON (509072) 138.0 kV bus b. 7. Trip branch from LONDON (509072) 138.0 bus to G19-065-TAP (763010) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR4 (509076) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 c. 2. Reclose branch from FRIRSWR4 (509063) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 c. 3. Reclose branch from FRIARSW4 (509062) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 c. 4. Reclose branch from LONDON (509072) 138.0 bus to G19-065-TAP (763010) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR4 (509076) 138.0 bus to FRIRSWR4 (509063) 138.0 bus CKT 1 d. 2. Trip branch from FRIRSWR4 (509063) 138.0 bus to FRIARSW4 (509062) 138.0 bus CKT 1 d. 3. Trip branch from FRIARSW4 (509062) 138.0 bus to LONDON (509072) 138.0 bus CKT 1 d. 4. Trip branch from LONDON (509072) 138.0 bus to G19-065-TAP (763010) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508548_KNOXLEE4-508562_PIRKEY_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to BRANDYBR (508596) 138.0 bus CKT 1 b. 2. Trip branch from BRANDYBR (508596) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 b. 3. Drop load from bus EASTON (509092) 138.0 kV bus b. 4. Trip branch from EASTON (509092) 138.0 bus to PIRKEY (508562) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to BRANDYBR (508596) 138.0 bus CKT 1 c. 2. Reclose branch from BRANDYBR (508596) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 c. 3. Reclose branch from EASTON (509092) 138.0 bus to PIRKEY (508562) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to BRANDYBR (508596) 138.0 bus CKT 1 d. 2. Trip branch from BRANDYBR (508596) 138.0 bus to EASTON (509092) 138.0 bus CKT 1 d. 3. Trip branch from EASTON (509092) 138.0 bus to PIRKEY (508562) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508548_KNOXLEE4-509059_CHEROKE4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus CHEROKE4 (509059) 138.0 kV bus b. 2. Trip branch from KNOXLEE4 (508548) 138.0 bus to CHEROKE4 (509059) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to CHEROKE4 (509059) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to CHEROKE4 (509059) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508548_KNOXLEE4-509078_OAK2HIL4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus OAK2HIL4 (509078) 138.0 kV bus b. 2. Trip branch from KNOXLEE4 (508548) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to OAK2HIL4 (509078) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508548_KNOXLEE4-509080_OVERTON4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 b. 2. Drop load from bus MONROER4 (509073) 138.0 kV bus b. 3. Trip branch from MONROER4 (509073) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 b. 4. Drop load from bus KILGORR4 (509067) 138.0 kV bus b. 5. Trip branch from KILGORR4 (509067) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 b. 6. Drop load from bus LEVERET4 (509069) 138.0 kV bus b. 7. Trip branch from LEVERET4 (509069) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 c. 2. Reclose branch from MONROER4 (509073) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 c. 3. Reclose branch from KILGORR4 (509067) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 c. 4. Reclose branch from LEVERET4 (509069) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to MONROER4 (509073) 138.0 bus CKT 1 d. 2. Trip branch from MONROER4 (509073) 138.0 bus to KILGORR4 (509067) 138.0 bus CKT 1 d. 3. Trip branch from KILGORR4 (509067) 138.0 bus to LEVERET4 (509069) 138.0 bus CKT 1 d. 4. Trip branch from LEVERET4 (509069) 138.0 bus to OVERTON4 (509080) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508548_KNOXLEE4-508544_HARRISN4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to HARRISN4 (508544) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 kV bus to HARRISN4 (508544) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to HARRISN4 (508544) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508548_KNOXLEE4-508570_SOTXEST4_Ckt1 | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SOTXEST4 (508570) 138.0 kV bus b. 2. Trip branch from KNOXLEE4 (508548) 138.0 bus to SOTXEST4 (508570) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE4 (508548) 138.0 bus to SOTXEST4 (508570) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE4 (508548) 138.0 bus to SOTXEST4 (508570) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508548_KNOXLEE4-508568_SELONGV2_3Winding | 3 Phase fault on KNOXLEE4 (508548) 138.0 kV a. Apply fault on KNOXLEE4 (508548) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at KXLEE-1 (508584) to trip transformer at KXLEE-1 12.470 (508584) 12.470000267028809 kV bus b. 2. Drop load from bus KNOXLEE2 (508547) 69.0 kV bus b. 3. Drop switching device from bus KNOXLEE2 (508547) 69.0 kV bus b. 4. Trip branch from KNOXLEE2 (508547) 69.0 bus to SELONGV2 (508568) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KNOXLEE2 (508547) 69.0 bus to SELONGV2 (508568) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KNOXLEE2 (508547) 69.0 bus to SELONGV2 (508568) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_334028_7GRIMES%-334026_4GRIMES%_3Winding | 3 Phase fault on 7GRIMES% (334028) 345.0 kV a. Apply fault on 7GRIMES% (334028) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at 1GRIMES_2 (334018) to trip transformer at 1GRIMES_2 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_334028_7GRIMES%-334027_6GRIMES!_Ckt1 | 3 Phase fault on 7GRIMES% (334028) 345.0 kV a. Apply fault on 7GRIMES% (334028) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 6GRIMES! (334027) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7GRIMES% (334028) 345.0 bus to 6GRIMES! (334027) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 6GRIMES! (334027) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_334028_7GRIMES%-334197_7ROCKYCRK%_Ckt1 | 3 Phase fault on 7GRIMES% (334028) 345.0 kV a. Apply fault on 7GRIMES% (334028) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 7ROCKYCRK% (334197) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7GRIMES% (334028) 345.0 bus to 7ROCKYCRK% (334197) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7GRIMES% (334028) 345.0 bus to 7ROCKYCRK% (334197) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508585_TENRUSK7-508572_LEBROCK7_Ckt1 | 3 Phase fault on TENRUSK7 (508585) 345.0 kV a. Apply fault on TENRUSK7 (508585) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508546_KILGORE2-508573_SPIPETP2_Ckt1 | 3 Phase fault on KILGORE2 (508546) 69.0 kV a. Apply fault on KILGORE2 (508546) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69.0 bus to HOWELL (508545) 69.0 bus CKT 1 b. 2. Drop load from bus HOWELL (508545) 69.0 kV bus b. 3. Drop switching device from bus HOWELL (508545) 69.0 kV bus b. 4. Trip branch from HOWELL (508545) 69.0 bus to SABINE (508565) 69.0 bus CKT 1 b. 5. Drop load from bus SABINE (508565) 69.0 kV bus b. 6. Drop switching device from bus SABINE (508565) 69.0 kV bus b. 7. Trip branch from SABINE (508565) 69.0 bus to SPIPETP2 (508573) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KILGORE2 (508546) 69.0 bus to HOWELL (508545) 69.0 bus CKT 1 c. 2. Reclose branch from HOWELL (508545) 69.0 bus to SABINE (508565) 69.0 bus CKT 1 c. 3. Reclose branch from SABINE (508565) 69.0 bus to SPIPETP2 (508573) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KILGORE2 (508546) 69.0 bus to HOWELL (508545) 69.0 bus CKT 1 d. 2. Trip branch from HOWELL (508545) 69.0 bus to SABINE (508565) 69.0 bus CKT 1 d. 3. Trip branch from SABINE (508565) 69.0 bus to SPIPETP2 (508573) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508546_KILGORE2-508574_WHITNEY2_Ckt1 | 3 Phase fault on KILGORE2 (508546) 69.0 kV a. Apply fault on KILGORE2 (508546) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69.0 bus to MONROCR2 (508558) 69.0 bus CKT 1 b. 2. Drop load from bus MONROCR2 (508558) 69.0 kV bus b. 3. Trip branch from MONROCR2 (508558) 69.0 bus to WHITNEY2 (508574) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KILGORE2 (508546) 69.0 bus to MONROCR2 (508558) 69.0 bus CKT 1 c. 2. Reclose branch from MONROCR2 (508558) 69.0 bus to WHITNEY2 (508574) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KILGORE2 (508546) 69.0 bus to MONROCR2 (508558) 69.0 bus CKT 1 d. 2. Trip branch from MONROCR2 (508558) 69.0 bus to WHITNEY2 (508574) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509075_NWHENDR2-509081_POYNTER2_Ckt1 | 3 Phase fault on NWHENDR2 (509075) 69.0 kV a. Apply fault on NWHENDR2 (509075) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to POYNTER2 (509081) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR2 (509075) 69.0 kV bus to POYNTER2 (509081) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to POYNTER2 (509081) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509075_NWHENDR2-509076_NWHENDR4_3Winding | 3 Phase fault on NWHENDR2 (509075) 69.0 kV a. Apply fault on NWHENDR2 (509075) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NWHEN2-1 (509096) to trip transformer at NWHEN2-1 13.200 (509096) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_509075_NWHENDR2-509061_EVENSID2_Ckt1 | 3 Phase fault on NWHENDR2 (509075) 69.0 kV a. Apply fault on NWHENDR2 (509075) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to EVENSID2 (509061) 69.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NWHENDR2 (509075) 69.0 kV bus to EVENSID2 (509061) 69.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NWHENDR2 (509075) 69.0 kV bus to EVENSID2 (509061) 69.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_334026_4GRIMES%-334028_7GRIMES%_3Winding | 3 Phase fault on 4GRIMES% (334026) 138.0 kV a. Apply fault on 4GRIMES% (334026) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at 1GRIMES_2 (334018) to trip transformer at 1GRIMES_2 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508572_LEBROCK7-508563_PIRKEY_Ckt2 | 3 Phase fault on LEBROCK7 (508572) 345.0 kV a. Apply fault on LEBROCK7 (508572) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P1_508572_LEBROCK7-508563_PIRKEY_Ckt1 | 3 Phase fault on LEBROCK7 (508572) 345.0 kV a. Apply fault on LEBROCK7 (508572) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LEBROCK7 (508572) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-509241_CROCKET7 | Single Phase Fault with Stuck Breaker on CROCKET7 (509241) 345.0 kV bus a. Apply single-phase fault on CROCKET7 (509241) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Trip branch from CROCKET7 (509241) 345.0 kV bus to 7GRIMES% (334028) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-509079_OVERTON2 | Single Phase Fault with Stuck Breaker on OVERTON2 (509079) 69.0 kV bus a. Apply single-phase fault on OVERTON2 (509079) 69.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69.0 kV bus to KILGORE2 (508546) 69.0 kV bus CKT 1 b. 2. Disconnect OVTON2-1 (509098) 13.2 kV bus to trip transformer at OVTON2-1 13.200 (509098) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-509076_NWHENDR4 | Single Phase Fault with Stuck Breaker on NWHENDR4 (509076) 138.0 kV bus a. Apply single-phase fault on NWHENDR4 (509076) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR4 (509076) 138.0 kV bus to OAK1HIL4 (509077) 138.0 kV bus CKT 1 b. 2. Drop load from bus OAK1HIL4 (509077) 138.0 kV bus b. 3. Drop load from bus OAK2HIL4 (509078) 138.0 kV bus b. 4. Trip branch from OAK1HIL4 (509077) 138.0 kV bus to OAK2HIL4 (509078) 138.0 kV bus CKT 1 b. 5. Disconnect NWHEN1-1 (509095) 13.2 kV bus to trip transformer at NWHEN1-1 13.200 (509095) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508548_KNOXLEE4 | Single Phase Fault with Stuck Breaker on KNOXLEE4 (508548) 138.0 kV bus a. Apply single-phase fault on KNOXLEE4 (508548) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to BRANDYBR (508596) 138.0 kV bus CKT 1 b. 2. Trip branch from BRANDYBR (508596) 138.0 kV bus to EASTON (509092) 138.0 kV bus CKT 1 b. 3. Drop load from bus EASTON (509092) 138.0 kV bus b. 4. Trip branch from EASTON (509092) 138.0 kV bus to PIRKEY (508562) 138.0 kV bus CKT 1 b. 5. Drop load from bus KNOXL5-1 (509398) 22.0 kV bus b. 6. Trip branch from KNOXLEE4 (508548) 138.0 kV bus to KNOXL5-1 (509398) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-334028_7GRIMES% | Single Phase Fault with Stuck Breaker on 7GRIMES% (334028) 345.0 kV bus a. Apply single-phase fault on 7GRIMES% (334028) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Disconnect 1GRIMES_1 (334163) 13.8 kV bus to trip transformer at 1GRIMES_1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508585_TENRUSK7 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TENRUSK7 (508585) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Trip branch from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-508586_TENGEN | Single Phase Fault with Stuck Breaker on TENGEN (508586) 345.0 kV bus a. Apply single-phase fault on TENGEN (508586) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TENGEN (508586) 345.0 kV bus to TENGAS (506745) 18.0 kV bus CKT 1 b. 2. Trip branch from TENGEN (508586) 345.0 kV bus to TENGAS (506746) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_HOL-334026_4GRIMES% | Single Phase Fault with Stuck Breaker on 4GRIMES% (334026) 138.0 kV bus a. Apply single-phase fault on 4GRIMES% (334026) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect 1GRIMES_1 (334163) 13.8 kV bus to trip transformer at 1GRIMES_1 13.8 kV bus b. 2. Disconnect 1GRIMES_2 (334018) 13.8 kV bus to trip transformer at 1GRIMES_2 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-300997_5KETONVL-ConID-109484 | Single Phase Fault with Stuck Breaker on 5KETONVL (300997) 161.0 kV bus a. Apply single-phase fault on 5KETONVL (300997) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from COLINS (512627) 161.0 kV bus to COLLIN3 (512840) 13.8 kV bus to COLNSGR2 (512870) 69.0 kV bus CKT 2 b. 2. Disconnect 5KETONVL (300997) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-300997_5KETONVL-ConID-109485 | Single Phase Fault with Stuck Breaker on 5KETONVL (300997) 161.0 kV bus a. Apply single-phase fault on 5KETONVL (300997) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from COLINS (512627) 161.0 kV bus to COLLIN2 (512839) 13.8 kV bus to COLNSGR2 (512870) 69.0 kV bus CKT 1 b. 2. Disconnect 5KETONVL (300997) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-500250_DOLHILL7-ConID-80023 | Single Phase Fault with Stuck Breaker on DOLHILL7 (500250) 345.0 kV bus a. Apply single-phase fault on DOLHILL7 (500250) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect DOLHILL7 (500250) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-506935_FLINTCR7-ConID-84210 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT1-1 (506921) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-506935_FLINTCR7-ConID-84211 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT1-1 (506921) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-506935_FLINTCR7-ConID-84212 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT2-1 (506920) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-506935_FLINTCR7-ConID-84213 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 b. 2. Trip transformer from FLINT2-1 (506920) 13.8 kV bus to FLINTCR5 (506934) 161.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-506935_FLINTCR7-ConID-84214 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 2. Trip line from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-506945_CHAMSPR7-ConID-84207 | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345.0 kV bus a. Apply single-phase fault on CHAMSPR7 (506945) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 b. 2. Trip transformer from CHAMSPR1 (506919) 13.8 kV bus to CHAMSPR5 (506944) 161.0 kV bus to CHAMSPR7 (506945) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-506945_CHAMSPR7-ConID-84208 | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345.0 kV bus a. Apply single-phase fault on CHAMSPR7 (506945) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHAMSPR7 (506945) 345.0 kV bus to TONTITN7 (506959) 345.0 kV bus CKT 1 b. 2. Trip transformer from CHAMSPR1 (506919) 13.8 kV bus to CHAMSPR5 (506944) 161.0 kV bus to CHAMSPR7 (506945) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-506945_CHAMSPR7-ConID-84209 | Single Phase Fault with Stuck Breaker on CHAMSPR7 (506945) 345.0 kV bus a. Apply single-phase fault on CHAMSPR7 (506945) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 b. 2. Trip line from CHAMSPR7 (506945) 345.0 kV bus to TONTITN7 (506959) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-506979_SHIPERD7-ConID-84215 | Single Phase Fault with Stuck Breaker on SHIPERD7 (506979) 345.0 kV bus a. Apply single-phase fault on SHIPERD7 (506979) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 2. Trip transformer from SHIPERD7 (506979) 345.0 kV bus to SHIPERD5 (506980) 161.0 kV bus to SHIPERD1 (506981) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-507455_TURK-ConID-84200 | Single Phase Fault with Stuck Breaker on TURK (507455) 345.0 kV bus a. Apply single-phase fault on TURK (507455) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TURK (507455) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 b. 2. Trip transformer from TURK (507454) 138.0 kV bus to TURK (507455) 345.0 kV bus to TURK (507457) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-507760_SW-ConID-84164 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-507760_SW-ConID-84165 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV1-1 (507778) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-507760_SW-ConID-84166 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV2-1 (507777) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-507760_SW-ConID-84167 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DOLHILL7 (500250) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV2-1 (507777) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-507760_SW-ConID-84168 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a. Apply single-phase fault on SW (507760) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DOLHILL7 (500250) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 2. Trip transformer from SW (507759) 138.0 kV bus to SW (507760) 345.0 kV bus to SWSHV1-1 (507778) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508072_NWTXARK7-ConID-84194 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TURK (507455) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 b. 2. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX1-1 (508100) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508072_NWTXARK7-ConID-84197 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX2-1 (508101) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508072_NWTXARK7-ConID-84198 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from TURK (507455) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508072_NWTXARK7-ConID-84199 | Single Phase Fault with Stuck Breaker on NWTXARK7 (508072) 345.0 kV bus a. Apply single-phase fault on NWTXARK7 (508072) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508298_LYDIA-ConID-84187 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508298_LYDIA-ConID-84189 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Disconnect WELSH3-1 (509406) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508298_LYDIA-ConID-84195 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX2-1 (508101) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508298_LYDIA-ConID-84196 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Trip transformer from NWTXARK4 (508071) 138.0 kV bus to NWTXARK7 (508072) 345.0 kV bus to NWTEX1-1 (508100) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508298_LYDIA-ConID-84206 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 3. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 4. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508298_LYDIA-ConID-91933 | Single Phase Fault with Stuck Breaker on LYDIA (508298) 345.0 kV bus a. Apply single-phase fault on LYDIA (508298) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from LYDIA (508298) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 3. Trip line from NWTXARK7 (508072) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 b. 4. Trip line from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508359_WELSH-ConID-84181 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Disconnect WILKE3-1 (509409) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508359_WELSH-ConID-84184 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 2. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508359_WELSH-ConID-84190 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a. Apply single-phase fault on WELSH (508359) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84154 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84155 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84156 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84157 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84159 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY2-1 (508588) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84160 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 2 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY2-1 (508588) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84161 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY1-1 (508587) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84162 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 2 b. 2. Trip transformer from PIRKEY (508562) 138.0 kV bus to PIRKEY (508563) 345.0 kV bus to PIRKY1-1 (508587) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508563_PIRKEY-ConID-84163 | Single Phase Fault with Stuck Breaker on PIRKEY (508563) 345.0 kV bus a. Apply single-phase fault on PIRKEY (508563) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip line from PIRKEY (508563) 345.0 kV bus to LEBROCK7 (508572) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508572_LEBROCK7-ConID-84153 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a. Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508572_LEBROCK7-ConID-84158 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a. Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Disconnect LEBROCG1 (506752) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508585_TENRUSK7-ConID-84150 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip line from TENRUSK7 (508585) 345.0 kV bus to TENGEN (508586) 345.0 kV bus CKT 1 b. 3. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508585_TENRUSK7-ConID-84151 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip line from TENRUSK7 (508585) 345.0 kV bus to TENGEN (508586) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508585_TENRUSK7-ConID-84152 | Single Phase Fault with Stuck Breaker on TENRUSK7 (508585) 345.0 kV bus a. Apply single-phase fault on TENRUSK7 (508585) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Trip line from TENRUSK7 (508585) 345.0 kV bus to TENGEN (508586) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508809_LONGWD-ConID-84169 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 7SAREPTA% (337376) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip transformer from LONGWD (508808) 138.0 kV bus to LONGWD (508809) 345.0 kV bus to LONGW1-1 (508819) 13.2 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508809_LONGWD-ConID-84170 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508809_LONGWD-ConID-84171 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Trip transformer from LONGWD (508808) 138.0 kV bus to LONGWD (508809) 345.0 kV bus to LONGW1-1 (508819) 13.2 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508809_LONGWD-ConID-84172 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a. Apply single-phase fault on LONGWD (508809) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 2. Trip line from 7SAREPTA% (337376) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508832_DIANA-ConID-84173 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-N1 (508845) 13.8 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508832_DIANA-ConID-84174 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-N1 (508845) 13.8 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508832_DIANA-ConID-84175 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-M1 (508843) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508832_DIANA-ConID-84176 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PIRKEY (508563) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508832_DIANA-ConID-84177 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 2. Trip line from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508832_DIANA-ConID-84178 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-S1 (508844) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508832_DIANA-ConID-84179 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a. Apply single-phase fault on DIANA (508832) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-S1 (508844) 13.8 kV bus CKT 1 b. 2. Trip transformer from DIANA (508831) 138.0 kV bus to DIANA (508832) 345.0 kV bus to DIANA-M1 (508843) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508841_WILKES-ConID-84180 | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a. Apply single-phase fault on WILKES (508841) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Trip transformer from WILKES-1 (508826) 13.2 kV bus to WILKES (508840) 138.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-508841_WILKES-ConID-84182 | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a. Apply single-phase fault on WILKES (508841) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509241_CROCKET7-ConID-84148 | Single Phase Fault with Stuck Breaker on CROCKET7 (509241) 345.0 kV bus a. Apply single-phase fault on CROCKET7 (509241) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TENRUSK7 (508585) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip transformer from CROCKET4 (509240) 138.0 kV bus to CROCKET7 (509241) 345.0 kV bus to CROCK-B1 (509243) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509241_CROCKET7-ConID-84149 | Single Phase Fault with Stuck Breaker on CROCKET7 (509241) 345.0 kV bus a. Apply single-phase fault on CROCKET7 (509241) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 7GRIMES% (334028) 345.0 kV bus to CROCKET7 (509241) 345.0 kV bus CKT 1 b. 2. Trip transformer from CROCKET4 (509240) 138.0 kV bus to CROCKET7 (509241) 345.0 kV bus to CROCK-B1 (509243) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509404_WELSH1-1-ConID-84185 | Single Phase Fault with Stuck Breaker on WELSH1-1 (509404) 18.0 kV bus a. Apply single-phase fault on WELSH1-1 (509404) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Disconnect WELSH1-1 (509404) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509404_WELSH1-1-ConID-84186 | Single Phase Fault with Stuck Breaker on WELSH1-1 (509404) 18.0 kV bus a. Apply single-phase fault on WELSH1-1 (509404) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b. 2. Disconnect WELSH1-1 (509404) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509404_WELSH1-1-ConID-84191 | Single Phase Fault with Stuck Breaker on WELSH1-1 (509404) 18.0 kV bus a. Apply single-phase fault on WELSH1-1 (509404) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WELSH1-1 (509404) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509406_WELSH3-1-ConID-84188 | Single Phase Fault with Stuck Breaker on WELSH3-1 (509406) 18.0 kV bus a. Apply single-phase fault on WELSH3-1 (509406) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WELSH3-1 (509406) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509409_WILKE3-1-ConID-84183 | Single Phase Fault with Stuck Breaker on WILKE3-1 (509409) 22.0 kV bus a. Apply single-phase fault on WILKE3-1 (509409) 22.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from WILKES-1 (508826) 13.2 kV bus to WILKES (508840) 138.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 2. Disconnect WILKE3-1 (509409) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509755_WEKIWA-7-ConID-84239 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345.0 kV bus a. Apply single-phase fault on WEKIWA-7 (509755) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 b. 2. Trip transformer from WEKIWA-7 (509755) 345.0 kV bus to WEKIWA-4 (509757) 138.0 kV bus to WEKIW1-1 (509879) 34.5 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509755_WEKIWA-7-ConID-84240 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345.0 kV bus a. Apply single-phase fault on WEKIWA-7 (509755) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip transformer from WEKIWA-7 (509755) 345.0 kV bus to WEKIWA-4 (509757) 138.0 kV bus to WEKIW1-1 (509879) 34.5 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509755_WEKIWA-7-ConID-84241 | Single Phase Fault with Stuck Breaker on WEKIWA-7 (509755) 345.0 kV bus a. Apply single-phase fault on WEKIWA-7 (509755) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509782_RSS-7-ConID-84233 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345.0 kV bus a. Apply single-phase fault on R.S.S.-7 (509782) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 b. 2. Trip transformer from RSS (509773) 138.0 kV bus to R.S.S.-7 (509782) 345.0 kV bus to RSST1 (509882) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509782_RSS-7-ConID-84234 | Single Phase Fault with Stuck Breaker on R.S.S.-7 (509782) 345.0 kV bus a. Apply single-phase fault on R.S.S.-7 (509782) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 b. 2. Trip line from R.S.S.-7 (509782) 345.0 kV bus to COGENT (509834) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84248 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Disconnect NES3-1 (511840) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84249 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84256 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CLARKSV7 (509745) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84257 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CLARKSV7 (509745) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 b. 2. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84258 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from R.S.S.-7 (509782) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84259 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA2-1 (509868) 34.5 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84260 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA1-1 (509881) 13.8 kV bus CKT 1 b. 2. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA2-1 (509868) 34.5 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84262 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84263 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 b. 2. Trip line from ONETA--7 (509807) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84265 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 b. 2. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA5-1 (509874) 34.5 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509807_ONETA--7-ConID-84266 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509852_TNO--7-ConID-84242 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 b. 2. Trip transformer from T.NO.--7 (509852) 345.0 kV bus to TNO2-1 (509894) 34.5 kV bus to T.NO.2-4 (509895) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509852_TNO--7-ConID-84243 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip transformer from T.NO.--7 (509852) 345.0 kV bus to TNO2-1 (509894) 34.5 kV bus to T.NO.2-4 (509895) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509852_TNO--7-ConID-84244 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 b. 2. Trip line from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509870_SAPLPRD7-ConID-84236 | Single Phase Fault with Stuck Breaker on SAPLPRD7 (509870) 345.0 kV bus a. Apply single-phase fault on SAPLPRD7 (509870) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip transformer from SAPLPRD7 (509870) 345.0 kV bus to SAPLPRD4 (509871) 138.0 kV bus to SAPLPRD1 (509872) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509870_SAPLPRD7-ConID-84237 | Single Phase Fault with Stuck Breaker on SAPLPRD7 (509870) 345.0 kV bus a. Apply single-phase fault on SAPLPRD7 (509870) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 b. 2. Trip line from R.S.S.-7 (509782) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509874_ONETA5-1-ConID-84264 | Single Phase Fault with Stuck Breaker on ONETA5-1 (509874) 34.5 kV bus a. Apply single-phase fault on ONETA5-1 (509874) 34.5 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA5-1 (509874) 34.5 kV bus CKT 3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-509881_ONETA1-1-ConID-84261 | Single Phase Fault with Stuck Breaker on ONETA1-1 (509881) 13.8 kV bus a. Apply single-phase fault on ONETA1-1 (509881) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from ONETA--4 (509806) 138.0 kV bus to ONETA--7 (509807) 345.0 kV bus to ONETA1-1 (509881) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510370_DELAWAR1-ConID-8425301 | Single Phase Fault with Stuck Breaker on DELAWAR1 (510370) 13.8 kV bus a. Apply single-phase fault on DELAWAR1 (510370) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G17-009-TAP (532777) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510380_DELWARE7-ConID-84253 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510380_DELWARE7-ConID-842530 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510380_DELWARE7-ConID-84254 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510380_DELWARE7-ConID-842540 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip line from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510380_DELWARE7-ConID-84255 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip transformer from DELAWAR1 (510370) 13.8 kV bus to DELWARE4 (510379) 138.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510406_NES-7-ConID-84250 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510406_NES-7-ConID-84251 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510406_NES-7-ConID-84252 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510907_PITTSB-7-ConID-84223 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510907_PITTSB-7-ConID-84224 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510907_PITTSB-7-ConID-84225 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to KIOWA (510925) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510907_PITTSB-7-ConID-84226 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510907_PITTSB-7-ConID-84227 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 b. 2. Trip line from PITTSB-7 (510907) 345.0 kV bus to KIOWA (510925) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510911_VALIANT7-ConID-84201 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN3-1 (510939) 13.8 kV bus CKT 1 b. 2. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN2-1 (510938) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510911_VALIANT7-ConID-84202 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN3-1 (510939) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510911_VALIANT7-ConID-84203 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip transformer from VALIANT7 (510911) 345.0 kV bus to VALIANT4 (510918) 138.0 kV bus to VALN2-1 (510938) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-510911_VALIANT7-ConID-91932 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345.0 kV bus a. Apply single-phase fault on VALIANT7 (510911) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from NWTXARK7 (508072) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 b. 2. Trip line from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511411_LES#5-1-ConID-8422101 | Single Phase Fault with Stuck Breaker on LES#5-1 (511411) 13.8 kV bus a. Apply single-phase fault on LES#5-1 (511411) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#5-1 (511411) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511456_OKU-7-ConID-84217 | Single Phase Fault with Stuck Breaker on O.K.U.-7 (511456) 345.0 kV bus a. Apply single-phase fault on O.K.U.-7 (511456) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from O.K.U.-7 (511456) 345.0 kV bus to G18-015-TAP (762467) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511467_LES-4-ConID-9193401 | Single Phase Fault with Stuck Breaker on L.E.S.-4 (511467) 138.0 kV bus a. Apply single-phase fault on L.E.S.-4 (511467) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511468_LES-7-ConID-84218 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511468_LES-7-ConID-842180 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511468_LES-7-ConID-84221 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#5-1 (511411) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511468_LES-7-ConID-842210 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G16-091-TAP (587744) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#5-1 (511411) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511468_LES-7-ConID-84222 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#5-1 (511411) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511468_LES-7-ConID-842720 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511468_LES-7-ConID-842730 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511468_LES-7-ConID-91934 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511468_LES-7-ConID-919340 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511468_LES-7-ConID-91937 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511468_LES-7-ConID-919370 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511468_LES-7-ConID-9193701 | Single Phase Fault with Stuck Breaker on L.E.S.-7 (511468) 345.0 kV bus a. Apply single-phase fault on L.E.S.-7 (511468) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from O.K.U.-7 (511456) 345.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 b. 2. Trip line from L.E.S.-7 (511468) 345.0 kV bus to G17-171-TAP (760938) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511568_TERRYRD7-ConID-84272 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511568_TERRYRD7-ConID-8427201 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511568_TERRYRD7-ConID-84273 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511568_TERRYRD7-ConID-8427301 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 2. Trip line from G17-171-TAP (760938) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511568_TERRYRD7-ConID-84274 | Single Phase Fault with Stuck Breaker on TERRYRD7 (511568) 345.0 kV bus a. Apply single-phase fault on TERRYRD7 (511568) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TERRYRD7 (511568) 345.0 kV bus to RUSHSPR7 (511571) 345.0 kV bus CKT 1 b. 2. Trip line from TERRYRD7 (511568) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-511840_NES3-1-ConID-84247 | Single Phase Fault with Stuck Breaker on NES3-1 (511840) 22.0 kV bus a. Apply single-phase fault on NES3-1 (511840) 22.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect NES3-1 (511840) 22.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-512635_KERR-ConID-109452 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Trip line from KERR (512635) 161.0 kV bus to KERR (512770) 161.0 kV bus CKT Z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-512635_KERR-ConID-109453 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Trip line from KERR (512635) 161.0 kV bus to KERR (512770) 161.0 kV bus CKT Z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-512635_KERR-ConID-109454 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a. Apply single-phase fault on KERR (512635) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from KERR (512635) 161.0 kV bus to 412SUB (512637) 161.0 kV bus CKT 1 b. 2. Trip line from KERR (512635) 161.0 kV bus to KERR (512771) 161.0 kV bus CKT Z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-512638_CATSAGR5-ConID-109479 | Single Phase Fault with Stuck Breaker on CATSAGR5 (512638) 161.0 kV bus a. Apply single-phase fault on CATSAGR5 (512638) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Trip transformer from CATOOSA4 (509790) 138.0 kV bus to CATSAGR5 (512638) 161.0 kV bus to CATTER2 (512834) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-512651_CLARMR-ConID-109481 | Single Phase Fault with Stuck Breaker on CLARMR (512651) 161.0 kV bus a. Apply single-phase fault on CLARMR (512651) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 5KETONVL (300997) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 b. 2. Trip line from CLARMR (512651) 161.0 kV bus to CHOUTEAUCRK5 (513570) 161.0 kV bus CKT 1 b. 3. Trip transformer from CLARMR (512651) 161.0 kV bus to CLARMR (512679) 69.0 kV bus to CLARMR1 (512814) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-512651_CLARMR-ConID-109482 | Single Phase Fault with Stuck Breaker on CLARMR (512651) 161.0 kV bus a. Apply single-phase fault on CLARMR (512651) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from 5KETONVL (300997) 161.0 kV bus to CLARMR (512651) 161.0 kV bus CKT 1 b. 2. Trip line from CLARMR (512651) 161.0 kV bus to CHOUTEAUCRK5 (513570) 161.0 kV bus CKT 1 b. 3. Trip transformer from CLARMR (512651) 161.0 kV bus to CLARMR (512679) 69.0 kV bus to CLARMR1 (512814) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-512656_GRDA1-ConID-109486 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect WAGNOR (512700) 161.0 kV bus b. 2. Trip transformer from GRDA1 (512650) 345.0 kV bus to GRDA1 (512656) 161.0 kV bus to GRDA1 (512821) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-512656_GRDA1-ConID-109487 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from CHOUTEAUCRK5 (513570) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Trip transformer from GRDA1 (512650) 345.0 kV bus to GRDA1 (512656) 161.0 kV bus to GRDA2 (512826) 13.8 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-512656_GRDA1-ConID-109488 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from GRDA1 (512656) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 b. 2. Trip transformer from GRDA1 (512650) 345.0 kV bus to GRDA1 (512656) 161.0 kV bus to GRDA1 (512821) 13.8 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-512686_SALINA-ConID-109461 | Single Phase Fault with Stuck Breaker on SALINA (512686) 161.0 kV bus a. Apply single-phase fault on SALINA (512686) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SALINA (512686) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-512707_CLARMR-ConID-109480 | Single Phase Fault with Stuck Breaker on CLARMR (512707) 138.0 kV bus a. Apply single-phase fault on CLARMR (512707) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from CLARMR (512651) 161.0 kV bus to CLARMR (512679) 69.0 kV bus to CLARMR2 (512815) 13.8 kV bus CKT 2 b. 2. Disconnect CLARMR (512707) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-512714_KANSATP5-ConID-109462 | Single Phase Fault with Stuck Breaker on KANSATP5 (512714) 161.0 kV bus a. Apply single-phase fault on KANSATP5 (512714) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect SILSPWW5 (512642) 161.0 kV bus b. 2. Disconnect KANSATP5 (512714) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-514808_JOHNCO-ConID-118718 | Single Phase Fault with Stuck Breaker on JOHNCO (514808) 138.0 kV bus a. Apply single-phase fault on JOHNCO (514808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 b. 2. Trip line from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-514808_JOHNCO-ConID-118719 | Single Phase Fault with Stuck Breaker on JOHNCO (514808) 138.0 kV bus a. Apply single-phase fault on JOHNCO (514808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from JOHNCO (514808) 138.0 kV bus to JOHNCO (514809) 345.0 kV bus to JOHNCO11 (514810) 13.8 kV bus CKT 1 b. 2. Trip line from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-514808_JOHNCO-ConID-118720 | Single Phase Fault with Stuck Breaker on JOHNCO (514808) 138.0 kV bus a. Apply single-phase fault on JOHNCO (514808) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 b. 2. Trip line from JOHNCO (514808) 138.0 kV bus to SXMLCKT4 (515122) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-515136_SUNNYSD7-ConID-118867 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a. Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from SUNNYSD4 (515135) 138.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus to SUNYSD (515405) 13.8 kV bus CKT 1 b. 2. Trip line from SUNNYSD7 (515136) 345.0 kV bus to G17-075-TAP (560088) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-515136_SUNNYSD7-ConID-1188670 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a. Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from SUNNYSD4 (515135) 138.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus to SUNYSD (515405) 13.8 kV bus CKT 1 b. 2. Trip line from SUNNYSD7 (515136) 345.0 kV bus to G17-075-TAP (560088) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-515405_SUNYSD-ConID-11886701 | Single Phase Fault with Stuck Breaker on SUNYSD (515405) 13.8 kV bus a. Apply single-phase fault on SUNYSD (515405) 13.8 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from SUNNYSD4 (515135) 138.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus to SUNYSD (515405) 13.8 kV bus CKT 1 b. 2. Trip line from G17-075-TAP (560088) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-515458_BORDER-ConID-118552 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a. Apply single-phase fault on BORDER (515458) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 2. Trip line from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-515554_BVRCNTY7-ConID-118540 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 b. 2. Trip line from BVRCNTY7 (515554) 345.0 kV bus to BALKOW (515618) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-515554_BVRCNTY7-ConID-80821 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a. Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 b. 2. Trip line from BVRCNTY7 (515554) 345.0 kV bus to PALDR2W7 (515590) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-515802_GRACMNT4-ConID-118667 | Single Phase Fault with Stuck Breaker on GRACMNT4 (515802) 138.0 kV bus a. Apply single-phase fault on GRACMNT4 (515802) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 2 b. 2. Trip line from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-525844_ELK_1-ConID-108439 | Single Phase Fault with Stuck Breaker on ELK_1 (525844) 18.0 kV bus a. Apply single-phase fault on ELK_1 (525844) 18.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Disconnect ELK_CT1 (525850) 345.0 kV bus b. 3. Disconnect ELK_1 (525844) 18.0 kV bus b. 4. Disconnect ELK_2 (525845) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108434 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108435 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 4. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108436 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip transformer from YOAKUM (526935) 230.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus to YOAKUM_TR1 (526937) 13.2 kV bus CKT 1 b. 2. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 3. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-526936_YOAKUM_345-ConID-108442 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a. Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from TUCO_INT (525832) 345.0 kV bus to YOAKUM_345 (526936) 345.0 kV bus CKT 1 b. 2. Trip line from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_345 (526936) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-532777_G17-009-TAP-ConID-8425401 | Single Phase Fault with Stuck Breaker on G17-009-TAP (532777) 345.0 kV bus a. Apply single-phase fault on G17-009-TAP (532777) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip line from G17-009-TAP (532777) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_CON-587744_G16-091-TAP-ConID-8421801 | Single Phase Fault with Stuck Breaker on G16-091-TAP (587744) 345.0 kV bus a. Apply single-phase fault on G16-091-TAP (587744) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip line from G16-091-TAP (587744) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Trip transformer from LES#4-1 (511414) 13.8 kV bus to L.E.S.-4 (511467) 138.0 kV bus to L.E.S.-7 (511468) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. Frequency and Voltage protection trips GEN-2016-095 (587773) | GEN-2018-115 model tuned to not trip during fault conditions. No additional system issues observed. Protection disabled with no impact on stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-507760_SW-ConID-AEPW-10 | Single Phase Fault with Stuck Breaker on SW (507760) 345.0 kV bus a.Apply single-phase fault on SW (507760) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from SW (507760) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from SW (507760) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b. 3. Clear fault from SW (507760) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-508359_WELSH-ConID-AEPW-3 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a.Apply single-phase fault on WELSH (508359) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from WELSH (508359) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from WELSH (508359) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b. 3. Clear fault from WELSH (508359) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-508359_WELSH-ConID-AEPW-4 | Single Phase Fault with Stuck Breaker on WELSH (508359) 345.0 kV bus a.Apply single-phase fault on WELSH (508359) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from WELSH (508359) 345.0 kV bus to DIANA (508832) 345.0 kV bus CKT 2 b. 3. Clear fault from WELSH (508359) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-508572_LEBROCK7-ConID-ETEC-4 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a.Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Clear fault from LEBROCK7 (508572) b. 3. Drop generator from LEBROCG1 (506752 ID 1) 18.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-508572_LEBROCK7-ConID-ETEC-5 | Single Phase Fault with Stuck Breaker on LEBROCK7 (508572) 345.0 kV bus a.Apply single-phase fault on LEBROCK7 (508572) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from LEBROCK7 (508572) 345.0 kV bus to TENRUSK7 (508585) 345.0 kV bus CKT 1 b. 2. Clear fault from LEBROCK7 (508572) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-508809_LONGWD-ConID-AEPW-8 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a.Apply single-phase fault on LONGWD (508809) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from LONGWD (508809) 345.0 kV bus to WILKES (508841) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from LONGWD (508809) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-508809_LONGWD-ConID-AEPW-9 | Single Phase Fault with Stuck Breaker on LONGWD (508809) 345.0 kV bus a.Apply single-phase fault on LONGWD (508809) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from LONGWD (508809) 345.0 kV bus to 7SAREPTA% (337376) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from LONGWD (508809) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from LONGWD (508809) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-508832_DIANA-ConID-AEPW-6 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a.Apply single-phase fault on DIANA (508832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from DIANA (508832) 345.0 kV bus to PIRKEY (508563) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from DIANA (508832) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from DIANA (508832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-508832_DIANA-ConID-AEPW-7 | Single Phase Fault with Stuck Breaker on DIANA (508832) 345.0 kV bus a.Apply single-phase fault on DIANA (508832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from DIANA (508832) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from DIANA (508832) 345.0 kV bus to SW (507760) 345.0 kV bus CKT 1 b. 3. Clear fault from DIANA (508832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-508841_WILKES-ConID-AEPW-5 | Single Phase Fault with Stuck Breaker on WILKES (508841) 345.0 kV bus a.Apply single-phase fault on WILKES (508841) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from WILKES (508841) 345.0 kV bus to LONGWD (508809) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from WILKES (508841) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 b. 3. Clear fault from WILKES (508841) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-509807_ONETA--7-ConID-AEPW-82 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a.Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Open branch from ONETA--7 (509807) 345.0 kV bus to R.S.S.-7 (509782) 345.0 kV bus CKT 1 b.Run for 10.0 cycles and trip the following elements: b. 2. Open branch from ONETA--7 (509807) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 b. 3. Clear fault from ONETA--7 (509807) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512635_KERR-ConID-GRDA-68 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a.Apply single-phase fault on KERR (512635) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from KERR (512635) b. 3. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512635_KERR-ConID-GRDA-69 | Single Phase Fault with Stuck Breaker on KERR (512635) 161.0 kV bus a.Apply single-phase fault on KERR (512635) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Clear fault from KERR (512635) b. 3. Open branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 2 b. 4. Disconnect SALNCRK5 (512805) 161.0 kV bus b. 5. Disconnect SALINA (512686) 161.0 kV bus b. 6. Drop generator from SALINA_U1 (512608 ID 1) 13.399999618530273 kV bus b. 7. Drop generator from SALINA_U2 (512609 ID 2) 13.399999618530273 kV bus b. 8. Drop generator from SALINA_U3 (512610 ID 3) 13.399999618530273 kV bus b. 9. Drop generator from SALINA_U4 (512611 ID 4) 13.399999618530273 kV bus b. 10. Drop generator from SALINA_U5 (512612 ID 5) 13.399999618530273 kV bus b. 11. Drop generator from SALINA_U6 (512613 ID 6) 13.399999618530273 kV bus b. 12. Drop load from SALINA_U1 (512608 ID PS) 13.399999618530273 kV bus b. 13. Drop load from SALINA_U2 (512609 ID PS) 13.399999618530273 kV bus b. 14. Drop load from SALINA_U3 (512610 ID PS) 13.399999618530273 kV bus b. 15. Drop load from SALINA_U4 (512611 ID PS) 13.399999618530273 kV bus b. 16. Drop load from SALINA_U5 (512612 ID PS) 13.399999618530273 kV bus b. 17. Drop load from SALINA_U6 (512613 ID PS) 13.399999618530273 kV bus b. 18. Disconnect SALINA_U1 (512608) 13.399999618530273 kV bus b. 19. Disconnect SALINA_U2 (512609) 13.399999618530273 kV bus b. 20. Disconnect SALINA_U3 (512610) 13.399999618530273 kV bus b. 21. Disconnect SALINA_U4 (512611) 13.399999618530273 kV bus b. 22. Disconnect SALINA_U5 (512612) 13.399999618530273 kV bus b. 23. Disconnect SALINA_U6 (512613) 13.399999618530273 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-58 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from 5CHOTEAU1 (300069) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-59 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-60 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from DRYGULCH5 (512629) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-61 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER2 (512837) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-62 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Disconnect MAITER1 (512836) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-63 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from 5CHOTEAU1 (300069) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from MAID (512648) 161.0 kV bus to GERALDGAY5 (512760) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-64 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from CATSAGR5 (512638) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-65 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from KERR (512635) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512648_MAID-ConID-GRDA-66 | Single Phase Fault with Stuck Breaker on MAID (512648) 161.0 kV bus a.Apply single-phase fault on MAID (512648) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from MAID (512648) b. 3. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-46 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA1 (512821) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-47 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from 7SPORTSMAN (300740) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA1 (512821) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-48 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA1 (512821) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512650_GRDA1-ConID-GRDA-49 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a.Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512650) b. 3. Disconnect GRDA17-1 (512688) 22.799999237060547 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512654_PENSA-ConID-GRDA-71 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Disconnect PENSA (512841) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512654_PENSA-ConID-GRDA-72 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Disconnect PENSA (512841) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512654_PENSA-ConID-GRDA-73 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from DRYGULCH5 (512629) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Open branch from PENSA (512654) 161.0 kV bus to KETCHUM5 (512669) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512654_PENSA-ConID-GRDA-74 | Single Phase Fault with Stuck Breaker on PENSA (512654) 161.0 kV bus a.Apply single-phase fault on PENSA (512654) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to PENSA (512654) 161.0 kV bus CKT 1 b. 2. Clear fault from PENSA (512654) b. 3. Drop generator from PENSA_U4 (512605 ID 4) 13.2 kV bus b. 4. Drop generator from PENSA_U5 (512607 ID 5) 13.2 kV bus b. 5. Drop generator from PENSA_U6 (512606 ID 6) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512656_GRDA1-ConID-GRDA-53 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a.Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CHOUTEAUCRK5 (513570) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512656) b. 3. Disconnect WAGNOR (512700) 161.0 kV bus b. 4. Disconnect WAGNOR1 (512818) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512656_GRDA1-ConID-GRDA-54 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a.Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from MAID (512648) 161.0 kV bus to GRDA1 (512656) 161.0 kV bus CKT 1 b. 2. Clear fault from GRDA1 (512656) b. 3. Open branch from GRDA1 (512656) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512669_KETCHUM5-ConID-GRDA-70 | Single Phase Fault with Stuck Breaker on KETCHUM5 (512669) 161.0 kV bus a.Apply single-phase fault on KETCHUM5 (512669) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Disconnect AFTON (512632) 161.0 kV bus b. 2. Clear fault from KETCHUM5 (512669) b. 3. Open branch from PENSA (512654) 161.0 kV bus to KETCHUM5 (512669) 161.0 kV bus CKT 1 b. 4. Drop load from KETCHUM5 (512669 ID 1) 161.0 kV bus b. 5. Disconnect KETCHUM5 (512669) 161.0 kV bus b. 6. Disconnect AFTON1 (512845) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512694_CLEVLND7-ConID-GRDA-55 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345.0 kV bus a.Apply single-phase fault on CLEVLND7 (512694) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 b. 2. Clear fault from CLEVLND7 (512694) b. 3. Open branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512694_CLEVLND7-ConID-GRDA-56 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345.0 kV bus a.Apply single-phase fault on CLEVLND7 (512694) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from T.NO.--7 (509852) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 b. 2. Clear fault from CLEVLND7 (512694) b. 3. Disconnect CLEVLND1 (512817) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512694_CLEVLND7-ConID-GRDA-57 | Single Phase Fault with Stuck Breaker on CLEVLND7 (512694) 345.0 kV bus a.Apply single-phase fault on CLEVLND7 (512694) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from CLEVLND7 (512694) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 b. 2. Clear fault from CLEVLND7 (512694) b. 3. Disconnect CLEVLND1 (512817) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512750_TONECE7-ConID-GRDA-77 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345.0 kV bus a.Apply single-phase fault on TONECE7 (512750) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Clear fault from TONECE7 (512750) b. 3. Open branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512750_TONECE7-ConID-GRDA-78 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345.0 kV bus a.Apply single-phase fault on TONECE7 (512750) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Clear fault from TONECE7 (512750) b. 3. Disconnect TONECE1 (512752) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512751_TONECE5-ConID-GRDA-76 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a.Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from SILMCTY5 (512643) 161.0 kV bus to TONECE5 (512751) 161.0 kV bus CKT 1 b. 2. Clear fault from TONECE5 (512751) b. 3. Disconnect TONNEC1 (512754) 13.2 kV bus b. 4. Drop load from SSLINC2 (512745 ID 1) 69.0 kV bus b. 5. Drop load from SSNORT2 (512746 ID 1) 69.0 kV bus b. 6. Disconnect ARKLIN2 (512728) 69.0 kV bus b. 7. Disconnect SSLINC2 (512745) 69.0 kV bus b. 8. Disconnect SSNORT2 (512746) 69.0 kV bus b. 9. Disconnect SSNEWN2 (512747) 69.0 kV bus b. 10. Disconnect TONECESTR2 (512756) 69.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512805_SALNCRK5-ConID-GRDA-75 | Single Phase Fault with Stuck Breaker on SALNCRK5 (512805) 161.0 kV bus a.Apply single-phase fault on SALNCRK5 (512805) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from KERR (512635) 161.0 kV bus to SALNCRK5 (512805) 161.0 kV bus CKT 1 b. 2. Clear fault from SALNCRK5 (512805) b. 3. Disconnect SALINA (512686) 161.0 kV bus b. 4. Drop generator from SALINA_U1 (512608 ID 1) 13.399999618530273 kV bus b. 5. Drop generator from SALINA_U2 (512609 ID 2) 13.399999618530273 kV bus b. 6. Drop generator from SALINA_U3 (512610 ID 3) 13.399999618530273 kV bus b. 7. Drop generator from SALINA_U4 (512611 ID 4) 13.399999618530273 kV bus b. 8. Drop generator from SALINA_U5 (512612 ID 5) 13.399999618530273 kV bus b. 9. Drop generator from SALINA_U6 (512613 ID 6) 13.399999618530273 kV bus b. 10. Drop load from SALINA_U1 (512608 ID PS) 13.399999618530273 kV bus b. 11. Drop load from SALINA_U2 (512609 ID PS) 13.399999618530273 kV bus b. 12. Drop load from SALINA_U3 (512610 ID PS) 13.399999618530273 kV bus b. 13. Drop load from SALINA_U4 (512611 ID PS) 13.399999618530273 kV bus b. 14. Drop load from SALINA_U5 (512612 ID PS) 13.399999618530273 kV bus b. 15. Drop load from SALINA_U6 (512613 ID PS) 13.399999618530273 kV bus b. 16. Disconnect SALINA_U1 (512608) 13.399999618530273 kV bus b. 17. Disconnect SALINA_U2 (512609) 13.399999618530273 kV bus b. 18. Disconnect SALINA_U3 (512610) 13.399999618530273 kV bus b. 19. Disconnect SALINA_U4 (512611) 13.399999618530273 kV bus b. 20. Disconnect SALINA_U5 (512612) 13.399999618530273 kV bus b. 21. Disconnect SALINA_U6 (512613) 13.399999618530273 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512865_GREC-ConID-GRDA-50 | Single Phase Fault with Stuck Breaker on GREC (512865) 345.0 kV bus a.Apply single-phase fault on GREC (512865) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 b. 2. Clear fault from GREC (512865) b. 3. Disconnect GRECSTG_1 (512615) 21.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-512865_GREC-ConID-GRDA-51 | Single Phase Fault with Stuck Breaker on GREC (512865) 345.0 kV bus a.Apply single-phase fault on GREC (512865) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 b. 2. Clear fault from GREC (512865) b. 3. Disconnect GRECCTG_1 (512614) 20.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-513596_IGLOOV-ConID-GRDA-52 | Single Phase Fault with Stuck Breaker on IGLOOV (513596) 345.0 kV bus a.Apply single-phase fault on IGLOOV (513596) 345.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from T.NO.--7 (509852) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 b. 2. Clear fault from IGLOOV (513596) b. 3. Disconnect IGLOTER1 (513592) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-514803_SOONER-ConID-OKGE-29 | Single Phase Fault with Stuck Breaker on SOONER (514803) 345.0 kV bus a.Apply single-phase fault on SOONER (514803) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect SOONER (515760) 13.8 kV bus b. 2. Open branch from G15-066T (560056) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 b. 3. Clear fault from SOONER (514803) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-514809_JOHNCO-ConID-OKGE-21 | Single Phase Fault with Stuck Breaker on JOHNCO (514809) 345.0 kV bus a.Apply single-phase fault on JOHNCO (514809) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 b. 2. Open branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 b. 3. Clear fault from JOHNCO (514809) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-515045_SEMINOL7-ConID-OKGE-28 | Single Phase Fault with Stuck Breaker on SEMINOL7 (515045) 345.0 kV bus a.Apply single-phase fault on SEMINOL7 (515045) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 b. 2. Disconnect SEMINO21 (515757) 14.399999618530273 kV bus b. 3. Clear fault from SEMINOL7 (515045) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-515136_SUNNYSD7-ConID-OKGE-18 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345.0 kV bus a.Apply single-phase fault on SUNNYSD7 (515136) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect SUNYSD (515405) 13.8 kV bus b. 2. Open branch from SUNNYSD7 (515136) 345.0 kV bus to G17-075-TAP (560088) 345.0 kV bus CKT 1 b. 3. Clear fault from SUNNYSD7 (515136) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-515339_VBI-ConID-OKGE-32 | Single Phase Fault with Stuck Breaker on VBI (515339) 161.0 kV bus a.Apply single-phase fault on VBI (515339) 161.0 kV bus b.Run for 23.52 cycles and trip the following elements: b. 1. Open branch from VAN (505522) 161.0 kV bus to VBI (515339) 161.0 kV bus CKT Z1 b.Run for 2.1 cycles and trip the following elements: b. 2. Open branch from OAKPARK5 (515315) 161.0 kV bus to GERBRTP5 (515326) 161.0 kV bus CKT 1 b.Run for 1.2 cycles and trip the following elements: b. 3. Open branch from MASSARD5 (515343) 161.0 kV bus to WHITESD5 (515341) 161.0 kV bus CKT 1 b.Run for 1.5 cycles and trip the following elements: b. 4. Open branch from HELBERG5 (515327) 161.0 kV bus to PUDDIN (515346) 161.0 kV bus CKT 1 b.Run for 3.9 cycles and trip the following elements: b. 5. Open branch from BRANCH (515316) 161.0 kV bus to GRNDPRT5 (515524) 161.0 kV bus CKT 1 b.Run for 11.28 cycles and trip the following elements: b. 6. Close branch from VAN (505522) 161.0 kV bus to VBI (515339) 161.0 kV bus CKT Z1 b.Run for 2.1 cycles and trip the following elements: b. 7. Close branch from OAKPARK5 (515315) 161.0 kV bus to GERBRTP5 (515326) 161.0 kV bus CKT 1 b.Run for 1.2 cycles and trip the following elements: b. 8. Close branch from MASSARD5 (515343) 161.0 kV bus to WHITESD5 (515341) 161.0 kV bus CKT 1 b.Run for 1.5 cycles and trip the following elements: b. 9. Close branch from HELBERG5 (515327) 161.0 kV bus to PUDDIN (515346) 161.0 kV bus CKT 1 b.Run for 3.9 cycles and trip the following elements: b. 10. Close branch from BRANCH (515316) 161.0 kV bus to GRNDPRT5 (515524) 161.0 kV bus CKT 1 b.Run for 1.62 cycles and trip the following elements: b. 11. Open branch from ROLANRD2 (515257) 69.0 kV bus to ROLANTP2 (515277) 69.0 kV bus CKT 1 b.Run for 9.18 cycles and trip the following elements: b. 12. Open branch from TAHLQH (512655) 161.0 kV bus to HWY59TP5 (515527) 161.0 kV bus CKT 1 b.Run for 4.02 cycles and trip the following elements: b. 13. Open branch from VAN (505522) 161.0 kV bus to VBI (515339) 161.0 kV bus CKT Z1 b.Run for 4.2 cycles and trip the following elements: b. 14. Open branch from OAKPARK5 (515315) 161.0 kV bus to GERBRTP5 (515326) 161.0 kV bus CKT 1 b.Run for 2.4 cycles and trip the following elements: b. 15. Open branch from MASSARD5 (515343) 161.0 kV bus to WHITESD5 (515341) 161.0 kV bus CKT 1 b.Run for 0.18 cycles and trip the following elements: b. 16. Close branch from ROLANRD2 (515257) 69.0 kV bus to ROLANTP2 (515277) 69.0 kV bus CKT 1 b.Run for 2.82 cycles and trip the following elements: b. 17. Open branch from HELBERG5 (515327) 161.0 kV bus to PUDDIN (515346) 161.0 kV bus CKT 1 b.Run for 6.36 cycles and trip the following elements: b. 18. Close branch from TAHLQH (512655) 161.0 kV bus to HWY59TP5 (515527) 161.0 kV bus CKT 1 b.Run for 1.44 cycles and trip the following elements: b. 19. Open branch from BRANCH (515316) 161.0 kV bus to GRNDPRT5 (515524) 161.0 kV bus CKT 1 b.Run for 19.38 cycles and trip the following elements: b. 20. Disconnect VBI (515769) 13.8 kV bus b.Run for 23.82 cycles and trip the following elements: b. 21. Open branch from ROLANRD2 (515257) 69.0 kV bus to ROLANTP2 (515277) 69.0 kV bus CKT 1 b.Run for 18.36 cycles and trip the following elements: b. 22. Open branch from TAHLQH (512655) 161.0 kV bus to HWY59TP5 (515527) 161.0 kV bus CKT 1 b. 23. Clear fault from VBI (515339) b. 24. Drop load from HWY59 (504191 ID A1) 161.0 kV bus b. 25. Drop load from GRANDPR5 (504192 ID A1) 161.0 kV bus b. 26. Drop load from SIMMONS5 (515332 ID 1) 161.0 kV bus b. 27. Drop load from SIMMONS5 (515332 ID A1) 161.0 kV bus b. 28. Drop load from DYER (515333 ID A1) 161.0 kV bus b. 29. Drop load from ALMA (515334 ID 1) 161.0 kV bus b. 30. Drop load from RUDY (515337 ID A1) 161.0 kV bus b. 31. Drop load from OAKGROV5 (515340 ID A1) 161.0 kV bus b. 32. Drop load from WHITESD5 (515341 ID 1) 161.0 kV bus b. 33. Drop load from PUDDIN (515346 ID A1) 161.0 kV bus b. 34. Drop load from NITROUS5 (515350 ID 1) 161.0 kV bus b. 35. Drop load from GERBER (515351 ID 1) 161.0 kV bus b. 36. Drop load from TWNBRDG5 (515360 ID 1) 161.0 kV bus b. 37. Drop load from ADABELL5 (515406 ID 1) 161.0 kV bus b. 38. Disconnect HWY59 (504191) 161.0 kV bus b. 39. Disconnect GRANDPR5 (504192) 161.0 kV bus b. 40. Disconnect GERBRTP5 (515326) 161.0 kV bus b. 41. Disconnect NITROTP5 (515329) 161.0 kV bus b. 42. Disconnect SIMMONS5 (515332) 161.0 kV bus b. 43. Disconnect DYER (515333) 161.0 kV bus b. 44. Disconnect ALMA (515334) 161.0 kV bus b. 45. Disconnect RUDY (515337) 161.0 kV bus b. 46. Disconnect OAKGROV5 (515340) 161.0 kV bus b. 47. Disconnect WHITESD5 (515341) 161.0 kV bus b. 48. Disconnect PUDDIN (515346) 161.0 kV bus b. 49. Disconnect NALCOTP5 (515348) 161.0 kV bus b. 50. Disconnect NITROUS5 (515350) 161.0 kV bus b. 51. Disconnect GERBER (515351) 161.0 kV bus b. 52. Disconnect TWNBRDG5 (515360) 161.0 kV bus b. 53. Disconnect ADABELL5 (515406) 161.0 kV bus b. 54. Disconnect GRNDPRT5 (515524) 161.0 kV bus b. 55. Disconnect HWY59TP5 (515527) 161.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-515458_BORDER-ConID-OKGE-31 | Single Phase Fault with Stuck Breaker on BORDER (515458) 345.0 kV bus a.Apply single-phase fault on BORDER (515458) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from WWDBORDT (755000) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from BORDER (515458) b. 4. Disconnect BORDER (515458) 345.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-515554_BVRCNTY7-ConID-OKGE-16 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345.0 kV bus a.Apply single-phase fault on BVRCNTY7 (515554) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 1 b. 2. Open branch from BVRCNTY7 (515554) 345.0 kV bus to BADGER (515677) 345.0 kV bus CKT 2 b. 3. Clear fault from BVRCNTY7 (515554) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-515576_RANCHRD7-ConID-OKGE-25 | Single Phase Fault with Stuck Breaker on RANCHRD7 (515576) 345.0 kV bus a.Apply single-phase fault on RANCHRD7 (515576) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from SOONER (514803) 345.0 kV bus to RANCHRD7 (515576) 345.0 kV bus CKT 1 b. 2. Open branch from RANCHRD7 (515576) 345.0 kV bus to FRNTWND7 (515688) 345.0 kV bus CKT 1 b. 3. Clear fault from RANCHRD7 (515576) b. 4. Drop generator from FRNTWDG1 (515691 ID 1) 0.65 kV bus b. 5. Drop load from FRNTWD11 (515689 ID S1) 34.5 kV bus b. 6. Disconnect FRNTWND7 (515688) 345.0 kV bus b. 7. Disconnect FRNTWD11 (515689) 34.5 kV bus b. 8. Disconnect FRNTWDC1 (515690) 34.5 kV bus b. 9. Disconnect FRNTWDG1 (515691) 0.65 kV bus b. 10. Disconnect FRNTWDT1 (515692) 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-515621_OPENSKY7-ConID-OKGE-23 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345.0 kV bus a.Apply single-phase fault on OPENSKY7 (515621) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 b. 2. Open branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 b. 3. Clear fault from OPENSKY7 (515621) b. 4. Drop generator from KAYWNDG1 (515651 ID 1) 0.69 kV bus b. 5. Drop generator from KAYWNDG2 (515652 ID 1) 0.69 kV bus b. 6. Drop load from KAYWND11 (515622 ID S1) 34.5 kV bus b. 7. Drop load from KAYWND12 (515623 ID S1) 34.5 kV bus b. 8. Disconnect KAYWIND7 (514825) 345.0 kV bus b. 9. Disconnect KAYWNDT1 (515619) 12.5 kV bus b. 10. Disconnect KAYWNDT2 (515620) 12.5 kV bus b. 11. Disconnect OPENSKY7 (515621) 345.0 kV bus b. 12. Disconnect KAYWND11 (515622) 34.5 kV bus b. 13. Disconnect KAYWND12 (515623) 34.5 kV bus b. 14. Disconnect KAYWNDG1 (515651) 0.69 kV bus b. 15. Disconnect KAYWNDG2 (515652) 0.69 kV bus b. 16. Disconnect KAYWNDC1 (515653) 34.5 kV bus b. 17. Disconnect KAYWNDC2 (515654) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-515785_WINDFRM4-ConID-OKGE-17 | Single Phase Fault with Stuck Breaker on WINDFRM4 (515785) 138.0 kV bus a.Apply single-phase fault on WINDFRM4 (515785) 138.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from WINDFRM4 (515785) 138.0 kV bus to MOORLND4 (520999) 138.0 kV bus CKT 1 b. 2. Open branch from WOODWRD4 (514785) 138.0 kV bus to WINDFRM4 (515785) 138.0 kV bus CKT 1 b. 3. Clear fault from WINDFRM4 (515785) b. 4. Drop generator from FPLWNDG1 (515895 ID 1) 0.69 kV bus b. 5. Drop load from FPLWND11 (515787 ID S1) 34.5 kV bus b. 6. Disconnect WINDFRM4 (515785) 138.0 kV bus b. 7. Disconnect FPLWIND4 (515786) 138.0 kV bus b. 8. Disconnect FPLWND11 (515787) 34.5 kV bus b. 9. Disconnect FLPWND21 (515790) 13.8 kV bus b. 10. Disconnect FPLWNDG1 (515895) 0.69 kV bus b. 11. Disconnect FPLWNDC1 (515896) 34.5 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-515800_GRACMNT7-ConID-OKGE-22 | Single Phase Fault with Stuck Breaker on GRACMNT7 (515800) 345.0 kV bus a.Apply single-phase fault on GRACMNT7 (515800) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from LES (587744) None kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 2. Open branch from MINCO (514801) 345.0 kV bus to GRACMNT7 (515800) 345.0 kV bus CKT 1 b. 3. Clear fault from GRACMNT7 (515800) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-520430_NOELSW-ConID-WFEC-59 | Single Phase Fault with Stuck Breaker on NOELSW (520430) 138.0 kV bus a.Apply single-phase fault on NOELSW (520430) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from DRIFTWD4 (521200) 138.0 kV bus to CHRKCTY4 (520431) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from ROSEVLY4 (520436) 138.0 kV bus to NOELSW (520430) 138.0 kV bus CKT 1 b. 3. Open branch from NOELSW (520430) 138.0 kV bus to SALTPLN4 (520437) 138.0 kV bus CKT 1 b. 4. Clear fault from NOELSW (520430) b. 5. Drop load from CHRKCTY4 (520431 ID 1) 138.0 kV bus b. 6. Drop load from SALTPLN4 (520437 ID 1) 138.0 kV bus b. 7. Drop load from SALTPLN4 (520437 ID 2) 138.0 kV bus b. 8. Disconnect CHRKCTY4 (520431) 138.0 kV bus b. 9. Disconnect SALTPLN4 (520437) 138.0 kV bus b. 10. Drop load from ROSEVLY4 (520436 ID 1) 138.0 kV bus b. 11. Drop load from AVARD (520601 ID 1) 138.0 kV bus b. 12. Disconnect ROSEVLY4 (520436) 138.0 kV bus b. 13. Disconnect AVARD (520601) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-520814_ANADARK4-ConID-WFEC-51 | Single Phase Fault with Stuck Breaker on ANADARK4 (520814) 138.0 kV bus a.Apply single-phase fault on ANADARK4 (520814) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from SUNSHIN4 (521059) 138.0 kV bus to BRIDGCR4 (520501) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from GRACMNT4 (515802) 138.0 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 b. 3. Open branch from ANADRK5 (520812) 13.8 kV bus to ANADARK4 (520814) 138.0 kV bus CKT 1 b. 4. Open branch from ANADARK4 (520814) 138.0 kV bus to POCASET4 (521031) 138.0 kV bus CKT 1 b. 5. Clear fault from ANADARK4 (520814) b. 6. Drop generator from ANADRK5 (520812 ID 1) 13.8 kV bus b. 7. Drop load from ANADRK5 (520812 ID F1) 13.8 kV bus b. 8. Drop load from ANADRK5 (520812 ID V1) 13.8 kV bus b. 9. Disconnect ANADRK5 (520812) 13.8 kV bus b. 10. Drop load from TUTTLE (520496 ID 1) 138.0 kV bus b. 11. Drop load from BRIDGCR4 (520501 ID 1) 138.0 kV bus b. 12. Drop load from POCASET4 (521031 ID 1) 138.0 kV bus b. 13. Disconnect TUTTLE (520496) 138.0 kV bus b. 14. Disconnect BRIDGCR4 (520501) 138.0 kV bus b. 15. Disconnect POCASET4 (521031) 138.0 kV bus b. 16. Disconnect TUTLETP4 (521072) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-520920_FTSUPLY4-ConID-WFEC-55 | Single Phase Fault with Stuck Breaker on FTSUPLY4 (520920) 138.0 kV bus a.Apply single-phase fault on FTSUPLY4 (520920) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from SLEEPBR4 (520922) 138.0 kV bus to FTSUPLY4 (520920) 138.0 kV bus CKT 1 b. 2. Drop generator from SLP (521145 ID 1) 0.6000000238418579 kV bus b. 3. Disconnect SLEEPBR4 (520922) 138.0 kV bus b. 4. Disconnect SLP (521141) 34.5 kV bus b. 5. Disconnect SLP (521144) 34.5 kV bus b. 6. Disconnect SLP (521145) 0.6000000238418579 kV bus b. 7. Disconnect SLP (521151) 9.949999809265137 kV bus b.Run for 9.0 cycles and trip the following elements: b. 8. Open branch from MOORLND4 (520999) 138.0 kV bus to IODINE (520957) 138.0 kV bus CKT 1 b. 9. Clear fault from FTSUPLY4 (520920) b. 10. Open branch from FTSUPLY4 (520920) 138.0 kV bus to IODINE (520957) 138.0 kV bus CKT 1 b. 11. Drop load from IODINE (520957 ID 1) 138.0 kV bus b. 12. Disconnect IODINE (520957) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-521016_OKEENE-ConID-WFEC-60 | Single Phase Fault with Stuck Breaker on OKEENE (521016) 138.0 kV bus a.Apply single-phase fault on OKEENE (521016) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from DOVERSW4 (520882) 138.0 kV bus to OKEENE (521016) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from MOORLND4 (520999) 138.0 kV bus to PIC4 (520425) 138.0 kV bus CKT 1 b. 3. Clear fault from OKEENE (521016) b. 4. Drop load from PIC4 (520425 ID 1) 138.0 kV bus b. 5. Drop load from CEDRDAL4 (520507 ID 1) 138.0 kV bus b. 6. Disconnect PIC4 (520425) 138.0 kV bus b. 7. Disconnect CDRDLTP4 (520848) 138.0 kV bus b. 8. Disconnect CEDRDAL4 (520507) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-521089_WASHITA4-ConID-WFEC-65 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138.0 kV bus a.Apply single-phase fault on WASHITA4 (521089) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from CLINTJC4 (511485) 138.0 kV bus to CLINTON4 (520856) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 1 b. 3. Open branch from WASHITA4 (521089) 138.0 kV bus to ONEY (521017) 138.0 kV bus CKT 1 b. 4. Clear fault from WASHITA4 (521089) b. 5. Drop load from HINTON (520468 ID 1) 138.0 kV bus b. 6. Drop load from DEERCR (520503 ID 1) 138.0 kV bus b. 7. Drop load from CLINTON4 (520856 ID 1) 138.0 kV bus b. 8. Drop load from HYDRO (520950 ID 1) 138.0 kV bus b. 9. Drop load from NIJECT (521010 ID 1) 138.0 kV bus b. 10. Drop load from NIJECT (521010 ID 2) 138.0 kV bus b. 11. Drop load from ONEY (521017 ID 1) 138.0 kV bus b. 12. Drop load from SICKLES4 (521050 ID 1) 138.0 kV bus b. 13. Drop load from WEATHFD4 (521092 ID 1) 138.0 kV bus b. 14. Disconnect HINTON (520468) 138.0 kV bus b. 15. Disconnect DEERCR (520503) 138.0 kV bus b. 16. Disconnect BINGERJ4 (520827) 138.0 kV bus b. 17. Disconnect CLINTON4 (520856) 138.0 kV bus b. 18. Disconnect HYDRO (520950) 138.0 kV bus b. 19. Disconnect NIJECT (521010) 138.0 kV bus b. 20. Disconnect ONEY (521017) 138.0 kV bus b. 21. Disconnect SICKLES4 (521050) 138.0 kV bus b. 22. Disconnect WEATHFD4 (521092) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-521089_WASHITA4-ConID-WFEC-66 | Single Phase Fault with Stuck Breaker on WASHITA4 (521089) 138.0 kV bus a.Apply single-phase fault on WASHITA4 (521089) 138.0 kV bus b.Run for 6.0 cycles and trip the following elements: b. 1. Open branch from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 1 b.Run for 9.0 cycles and trip the following elements: b. 2. Open branch from GRACMNT4 (515802) 138.0 kV bus to WASHITA4 (521089) 138.0 kV bus CKT 2 b. 3. Clear fault from WASHITA4 (521089) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-523777_WHEELER-ConID-SPS-140 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230.0 kV bus a.Apply single-phase fault on WHEELER (523777) 230.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from WHEELER (523777) 230.0 kV bus to SWEETWT6 (511541) 230.0 kV bus CKT &1 b. 2. Disconnect WHEELER (523777) 230.0 kV bus b. 3. Disconnect WHEELER_TR1113.200 (523774) 13.2 kV bus b. 4. Clear fault from WHEELER (523777) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-523777_WHEELER-ConID-SPS-143 | Single Phase Fault with Stuck Breaker on WHEELER (523777) 230.0 kV bus a.Apply single-phase fault on WHEELER (523777) 230.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect WHEELER_TR1113.200 (523774) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Disconnect WHEELER (523777) 230.0 kV bus b. 3. Disconnect WHEELER_TR1113.200 (523774) 13.2 kV bus b. 4. Clear fault from WHEELER (523777) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-132 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR1 (525824) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from BORDER (515458) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-138 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-139 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 21.0 cycles and trip the following elements: b. 1. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 2. Disconnect TUCO_TR1 (525824) 13.2 kV bus b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-525832_TUCO_INT-ConID-SPS-141 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345.0 kV bus a.Apply single-phase fault on TUCO_INT (525832) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect TUCO_TR2 (525825) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from TUCO_INT (525832) 345.0 kV bus to BORDER (515458) 345.0 kV bus CKT 1 b. 3. Clear fault from TUCO_INT (525832) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-129 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 3. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-130 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 5.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 11.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b.Run for 5.0 cycles and trip the following elements: b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 6. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 7. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-526936_YOAKUM_345-ConID-SPS-131 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345.0 kV bus a.Apply single-phase fault on YOAKUM_345 (526936) 345.0 kV bus b.Run for 16.0 cycles and trip the following elements: b. 1. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b.Run for 5.0 cycles and trip the following elements: b. 2. Open branch from YOAKUM_345 (526936) 345.0 kV bus to TUCO_INT (525832) 345.0 kV bus CKT 1 b. 3. Open branch from YOAKUM_345 (526936) 345.0 kV bus to HOBBS_INT (527896) 345.0 kV bus CKT 1 b. 4. Disconnect YOAKUM_TR1 (526937) 13.2 kV bus b. 5. Disconnect YOAKUM_345 (526936) 345.0 kV bus b. 6. Clear fault from YOAKUM_345 (526936) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-532791_BENTON-ConID-Evergy-105 | Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 4.75 cycles and trip the following elements: b. 1. Open branch from BENTON (532791) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 b. 2. Clear fault from BENTON (532791) Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 12.0 cycles and trip the following elements: b. 3. Open branch from BENTON (532791) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 4. Clear fault from BENTON (532791) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-532791_BENTON-ConID-Evergy-106 | Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 4.75 cycles and trip the following elements: b. 1. Open branch from BENTON (532791) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 2. Clear fault from BENTON (532791) Single Phase Fault with Stuck Breaker on BENTON (532791) 345.0 kV bus a.Apply single-phase fault on BENTON (532791) 345.0 kV bus b.Run for 12.0 cycles and trip the following elements: b. 3. Open branch from BENTON (532791) 345.0 kV bus to WICHITA7 (532796) 345.0 kV bus CKT 1 b. 4. Clear fault from BENTON (532791) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-532794_ROSEHIL7-ConID-Evergy-116 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from ROSEHIL7 (532794) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 2. Clear fault from ROSEHIL7 (532794) Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 13.0 cycles and trip the following elements: b. 3. Disconnect ROSEH3 (532831) 13.8 kV bus b. 4. Clear fault from ROSEHIL7 (532794) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-532794_ROSEHIL7-ConID-Evergy-152 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Disconnect ROSEH3 (532831) 13.8 kV bus b. 2. Clear fault from ROSEHIL7 (532794) Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345.0 kV bus a.Apply single-phase fault on ROSEHIL7 (532794) 345.0 kV bus b.Run for 13.0 cycles and trip the following elements: b. 3. Open branch from ROSEHIL7 (532794) 345.0 kV bus to WOLFCRK7 (532797) 345.0 kV bus CKT 1 b. 4. Clear fault from ROSEHIL7 (532794) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-121 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 4. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-122 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 4. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-123 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Open branch from WOLFCRK7 (532797) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 b. 4. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-532797_WOLFCRK7-ConID-Evergy-124 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 3.75 cycles and trip the following elements: b. 1. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 2. Clear fault from WOLFCRK7 (532797) Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345.0 kV bus a.Apply single-phase fault on WOLFCRK7 (532797) 345.0 kV bus b.Run for 6.75 cycles and trip the following elements: b. 3. Disconnect WOLFCRK1 (532962) 17.0 kV bus b. 4. Open branch from WOLFCRK7 (532797) 345.0 kV bus to BENTON (532791) 345.0 kV bus CKT 1 b. 5. Clear fault from WOLFCRK7 (532797) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-542965_WGRDNR7-ConID-Evergy-150 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345.0 kV bus a.Apply single-phase fault on W.GRDNR7 (542965) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from W.GRDNR7 (542965) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 b. 2. Open branch from STILWEL7 (542968) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 b. 3. Clear fault from W.GRDNR7 (542965) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-542968_STILWEL7-ConID-Evergy-148 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345.0 kV bus a.Apply single-phase fault on STILWEL7 (542968) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from PECULR (541198) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 2. Open branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 3. Clear fault from STILWEL7 (542968) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-140 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 b. 2. Open branch from LACYGNE7 (542981) 345.0 kV bus to WAVERLY7 (532799) 345.0 kV bus CKT 1 b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-141 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 2. Disconnect LAC (542955) 22.0 kV bus b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-142 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to WAVERLY7 (532799) 345.0 kV bus CKT 1 b. 2. Disconnect LAC (542955) 22.0 kV bus b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-542981_LACYGNE7-ConID-Evergy-143 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a.Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b.Run for 11.0 cycles and trip the following elements: b. 1. Open branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 b. 2. Disconnect LAC (542956) 24.0 kV bus b. 3. Clear fault from LACYGNE7 (542981) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25S | Transfer | P4_TO-547469_RIV4525-ConID-EMDE-34 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161.0 kV bus a.Apply single-phase fault on RIV4525 (547469) 161.0 kV bus b.Run for 7.0 cycles and trip the following elements: b. 1. Open branch from RIV4525 (547469) 161.0 kV bus to NEOSHO (532937) 161.0 kV bus CKT 1 b.Run for 86.0 cycles and trip the following elements: b. 4. Open branch from BAX488 (547729) 161.0 kV bus to HOC404 (547487) 161.0 kV bus CKT 1 b. 5. Clear fault from RIV4525 (547469) | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512753_TONNEC2-512745_SSLINC2_Ckt1 | 3 Phase fault on TONNEC2 (512753) 69.0 kV a. Apply fault on TONNEC2 (512753) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONNEC2 (512753) 69.0 bus to TONECESTR2 (512756) 69.0 bus CKT 1 b. 2. Trip branch from TONECESTR2 (512756) 69.0 bus to ARKLIN2 (512728) 69.0 bus CKT 1 b. 3. Trip branch from ARKLIN2 (512728) 69.0 bus to SSNEWN2 (512747) 69.0 bus CKT 1 b. 4. Trip branch from SSNEWN2 (512747) 69.0 bus to SSNORT2 (512746) 69.0 bus CKT 1 b. 5. Drop load from bus SSNORT2 (512746) 69.0 kV bus b. 6. Drop load from bus SSLINC2 (512745) 69.0 kV bus b. 7. Trip branch from SSNORT2 (512746) 69.0 bus to SSLINC2 (512745) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONNEC2 (512753) 69.0 bus to TONECESTR2 (512756) 69.0 bus CKT 1 c. 2. Reclose branch from TONECESTR2 (512756) 69.0 bus to ARKLIN2 (512728) 69.0 bus CKT 1 c. 3. Reclose branch from ARKLIN2 (512728) 69.0 bus to SSNEWN2 (512747) 69.0 bus CKT 1 c. 4. Reclose branch from SSNEWN2 (512747) 69.0 bus to SSNORT2 (512746) 69.0 bus CKT 1 c. 5. Reclose branch from SSNORT2 (512746) 69.0 bus to SSLINC2 (512745) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONNEC2 (512753) 69.0 bus to TONECESTR2 (512756) 69.0 bus CKT 1 d. 2. Trip branch from TONECESTR2 (512756) 69.0 bus to ARKLIN2 (512728) 69.0 bus CKT 1 d. 3. Trip branch from ARKLIN2 (512728) 69.0 bus to SSNEWN2 (512747) 69.0 bus CKT 1 d. 4. Trip branch from SSNEWN2 (512747) 69.0 bus to SSNORT2 (512746) 69.0 bus CKT 1 d. 5. Trip branch from SSNORT2 (512746) 69.0 bus to SSLINC2 (512745) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512753_TONNEC2-512751_TONECE5_3Winding | 3 Phase fault on TONNEC2 (512753) 69.0 kV a. Apply fault on TONNEC2 (512753) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONNEC1 (512754) to trip transformer at TONNEC1 13.200 (512754) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512751_TONECE5-512643_SILMCTY5_Ckt1 | 3 Phase fault on TONECE5 (512751) 161.0 kV a. Apply fault on TONECE5 (512751) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512751_TONECE5-512750_TONECE7_3Winding | 3 Phase fault on TONECE5 (512751) 161.0 kV a. Apply fault on TONECE5 (512751) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONECE1 (512752) to trip transformer at TONECE1 13.200 (512752) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512751_TONECE5-512753_TONNEC2_3Winding | 3 Phase fault on TONECE5 (512751) 161.0 kV a. Apply fault on TONECE5 (512751) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONNEC1 (512754) to trip transformer at TONNEC1 13.200 (512754) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512750_TONECE7-512650_GRDA1_Ckt1 | 3 Phase fault on TONECE7 (512750) 345.0 kV a. Apply fault on TONECE7 (512750) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512750_TONECE7-506935_FLINTCR7_Ckt1 | 3 Phase fault on TONECE7 (512750) 345.0 kV a. Apply fault on TONECE7 (512750) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512750_TONECE7-512751_TONECE5_3Winding | 3 Phase fault on TONECE7 (512750) 345.0 kV a. Apply fault on TONECE7 (512750) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TONECE1 (512752) to trip transformer at TONECE1 13.200 (512752) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506935_FLINTCR7-506929_ECNTRTN5_3Winding | 3 Phase fault on FLINTCR7 (506935) 345.0 kV a. Apply fault on FLINTCR7 (506935) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345.0 bus to SHIPERD7 (506979) 345.0 bus CKT 1 b. 2. Disconnect bus at SHIPERD1 (506981) to trip transformer at SHIPERD1 13.8 kV bus b. 3. Trip branch from SHIPERD5 (506980) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 b. 4. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 5. Trip branch from CENTRTN5 (506952) 161.0 bus to ECNTRTN5 (506929) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR7 (506935) 345.0 bus to SHIPERD7 (506979) 345.0 bus CKT 1 c. 2. Reclose branch from SHIPERD5 (506980) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 c. 3. Reclose branch from CENTRTN5 (506952) 161.0 bus to ECNTRTN5 (506929) 161.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR7 (506935) 345.0 bus to SHIPERD7 (506979) 345.0 bus CKT 1 d. 2. Trip branch from SHIPERD5 (506980) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 d. 3. Trip branch from CENTRTN5 (506952) 161.0 bus to ECNTRTN5 (506929) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506935_FLINTCR7-549984_BROOKLINE_Ckt1 | 3 Phase fault on FLINTCR7 (506935) 345.0 kV a. Apply fault on FLINTCR7 (506935) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR7 (506935) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506935_FLINTCR7-506934_FLINTCR5_3Winding | 3 Phase fault on FLINTCR7 (506935) 345.0 kV a. Apply fault on FLINTCR7 (506935) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at FLINT2-1 (506920) to trip transformer at FLINT2-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512643_SILMCTY5-506948_SILOAM_Ckt1 | 3 Phase fault on SILMCTY5 (512643) 161.0 kV a. Apply fault on SILMCTY5 (512643) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512643_SILMCTY5-512714_KANSATP5_Ckt1 | 3 Phase fault on SILMCTY5 (512643) 161.0 kV a. Apply fault on SILMCTY5 (512643) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 b. 2. Drop load from bus SILSPWW5 (512642) 161.0 kV bus b. 3. Trip branch from SILSPWW5 (512642) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY5 (512643) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 c. 2. Reclose branch from SILSPWW5 (512642) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY5 (512643) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 d. 2. Trip branch from SILSPWW5 (512642) 161.0 bus to KANSATP5 (512714) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512643_SILMCTY5-512820_SILMCTY2_3Winding | 3 Phase fault on SILMCTY5 (512643) 161.0 kV a. Apply fault on SILMCTY5 (512643) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SLMCTY2 (512850) to trip transformer at SLMCTY2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips GEN-2018-064 (763002) | Protection disabled with no impact to stability.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512650_GRDA1-300740_7SPORTSMAN_Ckt1 | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512650_GRDA1-512865_GREC_Ckt1 | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to GREC (512865) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512650_GRDA1-512656_GRDA1_3Winding | 3 Phase fault on GRDA1 (512650) 345.0 kV a. Apply fault on GRDA1 (512650) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at GRDA1 (512821) to trip transformer at GRDA1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_549984_BROOKLINE-300045_7MORGAN_Ckt1 | 3 Phase fault on BROOKLINE (549984) 345.0 kV a. Apply fault on BROOKLINE (549984) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_549984_BROOKLINE-549969_BROOKLINE_3Winding | 3 Phase fault on BROOKLINE (549984) 345.0 kV a. Apply fault on BROOKLINE (549984) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at BRKLNE (549989) to trip transformer at BRKLNE XF2 113.200 (549989) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506934_FLINTCR5-506990_GREENHOUSE_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 b. 2. Drop load from bus GENTRY (504201) 161.0 kV bus b. 3. Trip branch from GENTRY (504201) 161.0 bus to BEN279_5 (506960) 161.0 bus CKT 1 b. 4. Drop load from bus BEN279_5 (506960) 161.0 kV bus b. 5. Drop load from bus GREENHOUSE (506990) 161.0 kV bus b. 6. Trip branch from BEN279_5 (506960) 161.0 bus to GREENHOUSE (506990) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 c. 2. Reclose branch from GENTRY (504201) 161.0 bus to BEN279_5 (506960) 161.0 bus CKT 1 c. 3. Reclose branch from BEN279_5 (506960) 161.0 bus to GREENHOUSE (506990) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to GENTRY (504201) 161.0 bus CKT 1 d. 2. Trip branch from GENTRY (504201) 161.0 bus to BEN279_5 (506960) 161.0 bus CKT 1 d. 3. Trip branch from BEN279_5 (506960) 161.0 bus to GREENHOUSE (506990) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506934_FLINTCR5-506957_TONTITN5_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506934_FLINTCR5-547484_DEC392_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to DEC392 (547484) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 kV bus to DEC392 (547484) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to DEC392 (547484) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506934_FLINTCR5-504202_SILOAMSP_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SILOAMSP (504202) 161.0 kV bus b. 2. Trip branch from FLINTCR5 (506934) 161.0 bus to SILOAMSP (504202) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 bus to SILOAMSP (504202) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 bus to SILOAMSP (504202) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506934_FLINTCR5-506935_FLINTCR7_3Winding | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at FLINT2-1 (506920) to trip transformer at FLINT2-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506934_FLINTCR5-506948_SILOAM_Ckt1 | 3 Phase fault on FLINTCR5 (506934) 161.0 kV a. Apply fault on FLINTCR5 (506934) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FLINTCR5 (506934) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FLINTCR5 (506934) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506948_SILOAM-506944_CHAMSPR5_Ckt1 | 3 Phase fault on SILOAM (506948) 161.0 kV a. Apply fault on SILOAM (506948) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506948_SILOAM-506936_GREENLD2_3Winding | 3 Phase fault on SILOAM (506948) 161.0 kV a. Apply fault on SILOAM (506948) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SILOAM-1 (506917) to trip transformer at SILOAM-1 13.200 (506917) 13.2 kV bus b. 2. Drop switching device from bus SILOAM (506973) 69.0 kV bus b. 3. Trip branch from SILOAM (506973) 69.0 bus to LINCOLN2 (506972) 69.0 bus CKT 1 b. 4. Drop load from bus LINCOLN2 (506972) 69.0 kV bus b. 5. Trip branch from LINCOLN2 (506972) 69.0 bus to PRGROVE2 (506941) 69.0 bus CKT 1 b. 6. Drop load from bus PRGROVE2 (506941) 69.0 kV bus b. 7. Trip branch from PRGROVE2 (506941) 69.0 bus to GREENLD2 (506936) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILOAM (506973) 69.0 bus to LINCOLN2 (506972) 69.0 bus CKT 1 c. 2. Reclose branch from LINCOLN2 (506972) 69.0 bus to PRGROVE2 (506941) 69.0 bus CKT 1 c. 3. Reclose branch from PRGROVE2 (506941) 69.0 bus to GREENLD2 (506936) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILOAM (506973) 69.0 bus to LINCOLN2 (506972) 69.0 bus CKT 1 d. 2. Trip branch from LINCOLN2 (506972) 69.0 bus to PRGROVE2 (506941) 69.0 bus CKT 1 d. 3. Trip branch from PRGROVE2 (506941) 69.0 bus to GREENLD2 (506936) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512820_SILMCTY2-512730_SSSWES2_Ckt1 | 3 Phase fault on SILMCTY2 (512820) 69.0 kV a. Apply fault on SILMCTY2 (512820) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SSSWES2 (512730) 69.0 kV bus b. 2. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWES2 (512730) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY2 (512820) 69.0 bus to SSSWES2 (512730) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWES2 (512730) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512820_SILMCTY2-512643_SILMCTY5_3Winding | 3 Phase fault on SILMCTY2 (512820) 69.0 kV a. Apply fault on SILMCTY2 (512820) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at SLMCTY2 (512850) to trip transformer at SLMCTY2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512820_SILMCTY2-512744_SSMOSS2_Ckt1 | 3 Phase fault on SILMCTY2 (512820) 69.0 kV a. Apply fault on SILMCTY2 (512820) 69.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWTP2 (512737) 69.0 bus CKT 1 b. 2. Drop load from bus SSMOSS2 (512744) 69.0 kV bus b. 3. Trip branch from SSSWTP2 (512737) 69.0 bus to SSMOSS2 (512744) 69.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SILMCTY2 (512820) 69.0 bus to SSSWTP2 (512737) 69.0 bus CKT 1 c. 2. Reclose branch from SSSWTP2 (512737) 69.0 bus to SSMOSS2 (512744) 69.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SILMCTY2 (512820) 69.0 bus to SSSWTP2 (512737) 69.0 bus CKT 1 d. 2. Trip branch from SSSWTP2 (512737) 69.0 bus to SSMOSS2 (512744) 69.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_300740_7SPORTSMAN-300741_5SPORTSMAN_Ckt1 | 3 Phase fault on 7SPORTSMAN (300740) 345.0 kV a. Apply fault on 7SPORTSMAN (300740) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_300740_7SPORTSMAN-300741_5SPORTSMAN_Ckt2 | 3 Phase fault on 7SPORTSMAN (300740) 345.0 kV a. Apply fault on 7SPORTSMAN (300740) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SPORTSMAN (300740) 345.0 bus to 5SPORTSMAN (300741) 345.0 bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_300740_7SPORTSMAN-300739_7BLACKBERRY_Ckt1 | 3 Phase fault on 7SPORTSMAN (300740) 345.0 kV a. Apply fault on 7SPORTSMAN (300740) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7SPORTSMAN (300740) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7SPORTSMAN (300740) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512865_GREC-513596_IGLOOV_Ckt1 | 3 Phase fault on GREC (512865) 345.0 kV a. Apply fault on GREC (512865) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GREC (512865) 345.0 kV bus to IGLOOV (513596) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512656_GRDA1-512742_WMAIN_Ckt1 | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus WMAIN (512742) 161.0 kV bus b. 2. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from GRDA1 (512656) 161.0 bus to WMAIN (512742) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512656_GRDA1-512650_GRDA1_3Winding | 3 Phase fault on GRDA1 (512656) 161.0 kV a. Apply fault on GRDA1 (512656) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at GRDA1 (512821) to trip transformer at GRDA1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_300045_7MORGAN-300949_7JASPER_Ckt1 | 3 Phase fault on 7MORGAN (300045) 345.0 kV a. Apply fault on 7MORGAN (300045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_549969_BROOKLINE-505492_SPRGFLD5_Ckt1 | 3 Phase fault on BROOKLINE (549969) 161.0 kV a. Apply fault on BROOKLINE (549969) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_549969_BROOKLINE-549955_JUNCTION_Ckt1 | 3 Phase fault on BROOKLINE (549969) 161.0 kV a. Apply fault on BROOKLINE (549969) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506957_TONTITN5-504010_ELMSPRGS_Ckt1 | 3 Phase fault on TONTITN5 (506957) 161.0 kV a. Apply fault on TONTITN5 (506957) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506957_TONTITN5-506945_CHAMSPR7_3Winding | 3 Phase fault on TONTITN5 (506957) 161.0 kV a. Apply fault on TONTITN5 (506957) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at TONTITN1 (506958) to trip transformer at TONTITN1 13.8 kV bus b. 2. Trip branch from TONTITN7 (506959) 345.0 bus to CHAMSPR7 (506945) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from TONTITN7 (506959) 345.0 bus to CHAMSPR7 (506945) 345.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from TONTITN7 (506959) 345.0 bus to CHAMSPR7 (506945) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506944_CHAMSPR5-506992_WEDINGTON_Ckt1 | 3 Phase fault on CHAMSPR5 (506944) 161.0 kV a. Apply fault on CHAMSPR5 (506944) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506944_CHAMSPR5-506945_CHAMSPR7_3Winding | 3 Phase fault on CHAMSPR5 (506944) 161.0 kV a. Apply fault on CHAMSPR5 (506944) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at CHAMSPR1 (506919) to trip transformer at CHAMSPR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512714_KANSATP5-512635_KERR_Ckt1 | 3 Phase fault on KANSATP5 (512714) 161.0 kV a. Apply fault on KANSATP5 (512714) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 b. 2. Drop load from bus 412SUB (512637) 161.0 kV bus b. 3. Trip branch from 412SUB (512637) 161.0 bus to KERR (512635) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KANSATP5 (512714) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 c. 2. Reclose branch from 412SUB (512637) 161.0 bus to KERR (512635) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KANSATP5 (512714) 161.0 bus to 412SUB (512637) 161.0 bus CKT 1 d. 2. Trip branch from 412SUB (512637) 161.0 bus to KERR (512635) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512714_KANSATP5-512643_SILMCTY5_Ckt1 | 3 Phase fault on KANSATP5 (512714) 161.0 kV a. Apply fault on KANSATP5 (512714) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 b. 2. Drop load from bus SILSPWW5 (512642) 161.0 kV bus b. 3. Trip branch from SILSPWW5 (512642) 161.0 bus to SILMCTY5 (512643) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KANSATP5 (512714) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 c. 2. Reclose branch from SILSPWW5 (512642) 161.0 bus to SILMCTY5 (512643) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KANSATP5 (512714) 161.0 bus to SILSPWW5 (512642) 161.0 bus CKT 1 d. 2. Trip branch from SILSPWW5 (512642) 161.0 bus to SILMCTY5 (512643) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512714_KANSATP5-512715_KANSAS_3Winding | 3 Phase fault on KANSATP5 (512714) 161.0 kV a. Apply fault on KANSATP5 (512714) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161.0 bus to KANSAS (512716) 161.0 bus CKT 1 b. 2. Disconnect bus at KANSAS1 (512736) to trip transformer at KANSAS1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from KANSATP5 (512714) 161.0 bus to KANSAS (512716) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from KANSATP5 (512714) 161.0 bus to KANSAS (512716) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506929_ECNTRTN5-506935_FLINTCR7_3Winding | 3 Phase fault on ECNTRTN5 (506929) 161.0 kV a. Apply fault on ECNTRTN5 (506929) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN5 (506929) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 b. 2. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 3. Trip branch from CENTRTN5 (506952) 161.0 bus to SHIPERD5 (506980) 161.0 bus CKT 1 b. 4. Disconnect bus at SHIPERD1 (506981) to trip transformer at SHIPERD1 13.8 kV bus b. 5. Drop load from bus ECNTRTN5 (506929) 161.0 kV bus b. 6. Drop load from bus ECNTRTN5 (506929) 161.0 kV bus b. 7. Trip branch from SHIPERD7 (506979) 345.0 bus to FLINTCR7 (506935) 345.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ECNTRTN5 (506929) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 c. 2. Reclose branch from CENTRTN5 (506952) 161.0 bus to SHIPERD5 (506980) 161.0 bus CKT 1 c. 3. Reclose branch from SHIPERD7 (506979) 345.0 bus to FLINTCR7 (506935) 345.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ECNTRTN5 (506929) 161.0 bus to CENTRTN5 (506952) 161.0 bus CKT 1 d. 2. Trip branch from CENTRTN5 (506952) 161.0 bus to SHIPERD5 (506980) 161.0 bus CKT 1 d. 3. Trip branch from SHIPERD7 (506979) 345.0 bus to FLINTCR7 (506935) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506929_ECNTRTN5-506963_BENT_SL5_Ckt1 | 3 Phase fault on ECNTRTN5 (506929) 161.0 kV a. Apply fault on ECNTRTN5 (506929) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus BENT_SL5 (506963) 161.0 kV bus b. 2. Trip branch from ECNTRTN5 (506929) 161.0 bus to BENT_SL5 (506963) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ECNTRTN5 (506929) 161.0 bus to BENT_SL5 (506963) 161.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ECNTRTN5 (506929) 161.0 bus to BENT_SL5 (506963) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_513596_IGLOOV-513591_HERRON_3Winding | 3 Phase fault on IGLOOV (513596) 345.0 kV a. Apply fault on IGLOOV (513596) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at IGLOTER2 (513594) to trip transformer at IGLOTER2 1 13.200 (513594) 13.2 kV bus b. 2. Trip branch from IGLOOV2 (513595) 161.0 bus to HERRON (513591) 161.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from IGLOOV2 (513595) 161.0 bus to HERRON (513591) 161.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from IGLOOV2 (513595) 161.0 bus to HERRON (513591) 161.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_513596_IGLOOV-509852_TNO--7_Ckt1 | 3 Phase fault on IGLOOV (513596) 345.0 kV a. Apply fault on IGLOOV (513596) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV (513596) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from IGLOOV (513596) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from IGLOOV (513596) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506945_CHAMSPR7-509745_CLARKSV7_Ckt1 | 3 Phase fault on CHAMSPR7 (506945) 345.0 kV a. Apply fault on CHAMSPR7 (506945) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHAMSPR7 (506945) 345.0 kV bus to CLARKSV7 (509745) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506945_CHAMSPR7-506957_TONTITN5_3Winding | 3 Phase fault on CHAMSPR7 (506945) 345.0 kV a. Apply fault on CHAMSPR7 (506945) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR7 (506945) 345.0 bus to TONTITN7 (506959) 345.0 bus CKT 1 b. 2. Disconnect bus at TONTITN1 (506958) to trip transformer at TONTITN1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from CHAMSPR7 (506945) 345.0 bus to TONTITN7 (506959) 345.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from CHAMSPR7 (506945) 345.0 bus to TONTITN7 (506959) 345.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_506945_CHAMSPR7-506944_CHAMSPR5_3Winding | 3 Phase fault on CHAMSPR7 (506945) 345.0 kV a. Apply fault on CHAMSPR7 (506945) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at CHAMSPR1 (506919) to trip transformer at CHAMSPR1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512751_TONECE5 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a. Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TONECE5 (512751) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 b. 2. Disconnect TONECE1 (512752) 13.2 kV bus to trip transformer at TONECE1 13.200 (512752) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512750_TONECE7 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345.0 kV bus a. Apply single-phase fault on TONECE7 (512750) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345.0 kV bus to GRDA1 (512650) 345.0 kV bus CKT 1 b. 2. Trip branch from TONECE7 (512750) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-506935_FLINTCR7 | Single Phase Fault with Stuck Breaker on FLINTCR7 (506935) 345.0 kV bus a. Apply single-phase fault on FLINTCR7 (506935) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Trip branch from FLINTCR7 (506935) 345.0 kV bus to SHIPERD7 (506979) 345.0 kV bus CKT 1 b. 3. Disconnect SHIPERD1 (506981) 13.8 kV bus to trip transformer at SHIPERD1 13.8 kV bus b. 4. Trip branch from SHIPERD5 (506980) 161.0 kV bus to CENTRTN5 (506952) 161.0 kV bus CKT 1 b. 5. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 6. Trip branch from CENTRTN5 (506952) 161.0 kV bus to ECNTRTN5 (506929) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512643_SILMCTY5 | Single Phase Fault with Stuck Breaker on SILMCTY5 (512643) 161.0 kV bus a. Apply single-phase fault on SILMCTY5 (512643) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILOAM (506948) 161.0 kV bus CKT 1 b. 2. Trip branch from SILMCTY5 (512643) 161.0 kV bus to SILSPWW5 (512642) 161.0 kV bus CKT 1 b. 3. Drop load from bus SILSPWW5 (512642) 161.0 kV bus b. 4. Trip branch from SILSPWW5 (512642) 161.0 kV bus to KANSATP5 (512714) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512650_GRDA1 | Single Phase Fault with Stuck Breaker on GRDA1 (512650) 345.0 kV bus a. Apply single-phase fault on GRDA1 (512650) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512650) 345.0 kV bus to TONECE7 (512750) 345.0 kV bus CKT 1 b. 2. Trip branch from GRDA1 (512650) 345.0 kV bus to 7SPORTSMAN (300740) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-549984_BROOKLINE | Single Phase Fault with Stuck Breaker on BROOKLINE (549984) 345.0 kV bus a. Apply single-phase fault on BROOKLINE (549984) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549984) 345.0 kV bus to 7MORGAN (300045) 345.0 kV bus CKT 1 b. 2. Disconnect BRKLNE (549988) 13.2 kV bus to trip transformer at BRKLNE XF1 113.200 (549988) 13.2 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-506934_FLINTCR5 | Single Phase Fault with Stuck Breaker on FLINTCR5 (506934) 161.0 kV bus a. Apply single-phase fault on FLINTCR5 (506934) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Drop load from bus GENTRY (504201) 161.0 kV bus b. 2. Trip branch from FLINTCR5 (506934) 161.0 kV bus to GENTRY (504201) 161.0 kV bus CKT 1 b. 3. Trip branch from FLINTCR5 (506934) 161.0 kV bus to TONTITN5 (506957) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-506948_SILOAM | Single Phase Fault with Stuck Breaker on SILOAM (506948) 161.0 kV bus a. Apply single-phase fault on SILOAM (506948) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM (506948) 161.0 kV bus to CHAMSPR5 (506944) 161.0 kV bus CKT 1 b. 2. Trip branch from SILOAM (506948) 161.0 kV bus to SILMCTY5 (512643) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-512656_GRDA1 | Single Phase Fault with Stuck Breaker on GRDA1 (512656) 161.0 kV bus a. Apply single-phase fault on GRDA1 (512656) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 (512656) 161.0 kV bus to WMAIN (512742) 161.0 kV bus CKT 1 b. 2. Drop load from bus WMAIN (512742) 161.0 kV bus b. 3. Trip branch from WMAIN (512742) 161.0 kV bus to NWMAID5 (512757) 161.0 kV bus CKT 1 b. 4. Drop load from bus NWMAID5 (512757) 161.0 kV bus b. 5. Trip branch from NWMAID5 (512757) 161.0 kV bus to GERALDGAY5 (512760) 161.0 kV bus CKT 1 b. 6. Drop load from bus GERALDGAY5 (512760) 161.0 kV bus b. 7. Trip branch from GERALDGAY5 (512760) 161.0 kV bus to MAID (512648) 161.0 kV bus CKT 1 b. 8. Disconnect GRDA2 (512826) 13.8 kV bus to trip transformer at GRDA2 1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-300045_7MORGAN | Single Phase Fault with Stuck Breaker on 7MORGAN (300045) 345.0 kV bus a. Apply single-phase fault on 7MORGAN (300045) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345.0 kV bus to 7JASPER (300949) 345.0 kV bus CKT 1 b. 2. Trip branch from 7MORGAN (300045) 345.0 kV bus to BROOKLINE (549984) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-549969_BROOKLINE | Single Phase Fault with Stuck Breaker on BROOKLINE (549969) 161.0 kV bus a. Apply single-phase fault on BROOKLINE (549969) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE (549969) 161.0 kV bus to SPRGFLD5 (505492) 161.0 kV bus CKT 1 b. 2. Trip branch from BROOKLINE (549969) 161.0 kV bus to JUNCTION (549955) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-506957_TONTITN5 | Single Phase Fault with Stuck Breaker on TONTITN5 (506957) 161.0 kV bus a. Apply single-phase fault on TONTITN5 (506957) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161.0 kV bus to ELMSPRGS (504010) 161.0 kV bus CKT 1 b. 2. Disconnect TONTITN1 (506958) 13.8 kV bus to trip transformer at TONTITN1 13.8 kV bus b. 3. Trip branch from TONTITN7 (506959) 345.0 kV bus to CHAMSPR7 (506945) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-506944_CHAMSPR5 | Single Phase Fault with Stuck Breaker on CHAMSPR5 (506944) 161.0 kV bus a. Apply single-phase fault on CHAMSPR5 (506944) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR5 (506944) 161.0 kV bus to WEDINGTON (506992) 161.0 kV bus CKT 1 b. 2. Disconnect CHAMSPR1 (506919) 13.8 kV bus to trip transformer at CHAMSPR1 13.8 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-514803_SOONER | Single Phase Fault with Stuck Breaker on SOONER (514803) 345.0 kV bus a. Apply single-phase fault on SOONER (514803) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 b. 2. Trip branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-506929_ECNTRTN5 | Single Phase Fault with Stuck Breaker on ECNTRTN5 (506929) 161.0 kV bus a. Apply single-phase fault on ECNTRTN5 (506929) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN5 (506929) 161.0 kV bus to CENTRTN5 (506952) 161.0 kV bus CKT 1 b. 2. Drop load from bus CENTRTN5 (506952) 161.0 kV bus b. 3. Trip branch from CENTRTN5 (506952) 161.0 kV bus to SHIPERD5 (506980) 161.0 kV bus CKT 1 b. 4. Disconnect SHIPERD1 (506981) 13.8 kV bus to trip transformer at SHIPERD1 13.8 kV bus b. 5. Trip branch from SHIPERD7 (506979) 345.0 kV bus to FLINTCR7 (506935) 345.0 kV bus CKT 1 b. 6. Drop load from bus BENT_SL5 (506963) 161.0 kV bus b. 7. Trip branch from ECNTRTN5 (506929) 161.0 kV bus to BENT_SL5 (506963) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515576_RANCHRD7-515621_OPENSKY7_Ckt1 | 3 Phase fault on RANCHRD7 (515576) 345.0 kV a. Apply fault on RANCHRD7 (515576) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to OPENSKY7 (515621) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515576_RANCHRD7-514803_SOONER_Ckt1 | 3 Phase fault on RANCHRD7 (515576) 345.0 kV a. Apply fault on RANCHRD7 (515576) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from RANCHRD7 (515576) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from RANCHRD7 (515576) 345.0 kV bus to SOONER (514803) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514803_SOONER-560056_G15-066T_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to G15-066T (560056) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514803_SOONER-509755_WEKIWA-7_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to WEKIWA-7 (509755) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514803_SOONER-516010_PINTAIL7_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to PINTAIL7 (516010) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to PINTAIL7 (516010) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to PINTAIL7 (516010) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514803_SOONER-514802_SOONER_3Winding | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SOONER (515760) to trip transformer at SOONER 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514803_SOONER-587804_G16-119-TAP_Ckt1 | 3 Phase fault on SOONER (514803) 345.0 kV a. Apply fault on SOONER (514803) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514803) 345.0 kV bus to G16-119-TAP (587804) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514803) 345.0 kV bus to G16-119-TAP (587804) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514803) 345.0 kV bus to G16-119-TAP (587804) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515621_OPENSKY7-560053_G15-052T_Ckt1 | 3 Phase fault on OPENSKY7 (515621) 345.0 kV a. Apply fault on OPENSKY7 (515621) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from OPENSKY7 (515621) 345.0 kV bus to G15-052T (560053) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509755_WEKIWA-7-509757_WEKIWA-4_3Winding | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at WEKIW1-1 (509879) to trip transformer at WEKIW1-1 34.500 (509879) 34.5 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509755_WEKIWA-7-509870_SAPLPRD7_Ckt1 | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to SAPLPRD7 (509870) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509755_WEKIWA-7-509852_TNO--7_Ckt1 | 3 Phase fault on WEKIWA-7 (509755) 345.0 kV a. Apply fault on WEKIWA-7 (509755) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from WEKIWA-7 (509755) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_560056_G15-066T-512694_CLEVLND7_Ckt1 | 3 Phase fault on G15-066T (560056) 345.0 kV a. Apply fault on G15-066T (560056) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-066T (560056) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G15-066T (560056) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G15-066T (560056) 345.0 kV bus to CLEVLND7 (512694) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514802_SOONER-514798_SNRPMPT4_Ckt1 | 3 Phase fault on SOONER (514802) 138.0 kV a. Apply fault on SOONER (514802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514802_SOONER-514704_MILLERT4_Ckt1 | 3 Phase fault on SOONER (514802) 138.0 kV a. Apply fault on SOONER (514802) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_560053_G15-052T-532794_ROSEHIL7_Ckt1 | 3 Phase fault on G15-052T (560053) 345.0 kV a. Apply fault on G15-052T (560053) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-052T (560053) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G15-052T (560053) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G15-052T (560053) 345.0 kV bus to ROSEHIL7 (532794) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-514802_SOONER | Single Phase Fault with Stuck Breaker on SOONER (514802) 138.0 kV bus a. Apply single-phase fault on SOONER (514802) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SOONER (514802) 138.0 kV bus to SNRPMPT4 (514798) 138.0 kV bus CKT 1 b. 2. Trip branch from SOONER (514802) 138.0 kV bus to MILLERT4 (514704) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_763113_G18-079-TAP-512734_FARML_Ckt1 | 3 Phase fault on G18-079-TAP (763113) 138.0 kV a. Apply fault on G18-079-TAP (763113) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G18-079-TAP (763113) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G18-079-TAP (763113) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_763113_G18-079-TAP-510380_DELWARE7_3Winding | 3 Phase fault on G18-079-TAP (763113) 138.0 kV a. Apply fault on G18-079-TAP (763113) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138.0 bus to DELWARE4 (510379) 138.0 bus CKT 1 b. 2. Disconnect bus at DELAWAR1 (510370) to trip transformer at DELAWAR1 13.8 kV bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from G18-079-TAP (763113) 138.0 bus to DELWARE4 (510379) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from G18-079-TAP (763113) 138.0 bus to DELWARE4 (510379) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_512734_FARML-510378_SCOFCTY4_Ckt1 | 3 Phase fault on FARML (512734) 138.0 kV a. Apply fault on FARML (512734) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FARML (512734) 138.0 kV bus to SCOFCTY4 (510378) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from FARML (512734) 138.0 kV bus to SCOFCTY4 (510378) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from FARML (512734) 138.0 kV bus to SCOFCTY4 (510378) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510380_DELWARE7-510406_NES-7_Ckt1 | 3 Phase fault on DELWARE7 (510380) 345.0 kV a. Apply fault on DELWARE7 (510380) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510380_DELWARE7-532793_NEOSHO_Ckt1 | 3 Phase fault on DELWARE7 (510380) 345.0 kV a. Apply fault on DELWARE7 (510380) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510380_DELWARE7-763113_G18-079-TAP_3Winding | 3 Phase fault on DELWARE7 (510380) 345.0 kV a. Apply fault on DELWARE7 (510380) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at DELAWAR1 (510370) to trip transformer at DELAWAR1 13.8 kV bus b. 2. Trip branch from DELWARE4 (510379) 138.0 bus to G18-079-TAP (763113) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from DELWARE4 (510379) 138.0 bus to G18-079-TAP (763113) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from DELWARE4 (510379) 138.0 bus to G18-079-TAP (763113) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510378_SCOFCTY4-510422_COFFEYT4_Ckt1 | 3 Phase fault on SCOFCTY4 (510378) 138.0 kV a. Apply fault on SCOFCTY4 (510378) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510378_SCOFCTY4-510420_SCOFFEYV4_Ckt1 | 3 Phase fault on SCOFCTY4 (510378) 138.0 kV a. Apply fault on SCOFCTY4 (510378) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus SCOFFEYV4 (510420) 138.0 kV bus b. 2. Trip branch from SCOFCTY4 (510378) 138.0 bus to SCOFFEYV4 (510420) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SCOFCTY4 (510378) 138.0 bus to SCOFFEYV4 (510420) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SCOFCTY4 (510378) 138.0 bus to SCOFFEYV4 (510420) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510406_NES-7-509852_TNO--7_Ckt1 | 3 Phase fault on N.E.S.-7 (510406) 345.0 kV a. Apply fault on N.E.S.-7 (510406) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510406_NES-7-509807_ONETA--7_Ckt1 | 3 Phase fault on N.E.S.-7 (510406) 345.0 kV a. Apply fault on N.E.S.-7 (510406) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from N.E.S.-7 (510406) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to ONETA--7 (509807) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_532793_NEOSHO-532937_NEOSHO_3Winding | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532825) to trip transformer at N345 2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_532793_NEOSHO-542981_LACYGNE7_Ckt1 | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_532793_NEOSHO-533021_NEOSHO_3Winding | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532824) to trip transformer at N345 1 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_532793_NEOSHO-532777_G17-009-TAP_Ckt1 | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to G17-009-TAP (532777) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532793) 345.0 kV bus to G17-009-TAP (532777) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to G17-009-TAP (532777) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_532793_NEOSHO-300739_7BLACKBERRY_Ckt1 | 3 Phase fault on NEOSHO (532793) 345.0 kV a. Apply fault on NEOSHO (532793) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532793) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532793) 345.0 kV bus to 7BLACKBERRY (300739) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510422_COFFEYT4-533002_DEARING4_Ckt1 | 3 Phase fault on COFFEYT4 (510422) 138.0 kV a. Apply fault on COFFEYT4 (510422) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138.0 kV bus to DEARING4 (533002) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from COFFEYT4 (510422) 138.0 kV bus to DEARING4 (533002) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from COFFEYT4 (510422) 138.0 kV bus to DEARING4 (533002) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510422_COFFEYT4-510391_BV-SE--4_Ckt1 | 3 Phase fault on COFFEYT4 (510422) 138.0 kV a. Apply fault on COFFEYT4 (510422) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138.0 bus to NBVILLE4 (510386) 138.0 bus CKT 1 b. 2. Drop load from bus NBVILLE4 (510386) 138.0 kV bus b. 3. Trip branch from NBVILLE4 (510386) 138.0 bus to BV-SE--4 (510391) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from COFFEYT4 (510422) 138.0 bus to NBVILLE4 (510386) 138.0 bus CKT 1 c. 2. Reclose branch from NBVILLE4 (510386) 138.0 bus to BV-SE--4 (510391) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from COFFEYT4 (510422) 138.0 bus to NBVILLE4 (510386) 138.0 bus CKT 1 d. 2. Trip branch from NBVILLE4 (510386) 138.0 bus to BV-SE--4 (510391) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509807_ONETA--7-509836_OEC_Ckt2 | 3 Phase fault on ONETA--7 (509807) 345.0 kV a. Apply fault on ONETA--7 (509807) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509807_ONETA--7-509836_OEC_Ckt1 | 3 Phase fault on ONETA--7 (509807) 345.0 kV a. Apply fault on ONETA--7 (509807) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_509852_TNO--7-509895_TNO2-4_3Winding | 3 Phase fault on T.NO.--7 (509852) 345.0 kV a. Apply fault on T.NO.--7 (509852) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at TNO2-1 (509894) to trip transformer at TNO2-1 34.500 (509894) 34.5 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Tripping issues with G10-055 generator (560391) observed in PQ cases and not caused by CQ generators | No mitigation required.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_542981_LACYGNE7-542968_STILWEL7_Ckt1 | 3 Phase fault on LACYGNE7 (542981) 345.0 kV a. Apply fault on LACYGNE7 (542981) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_542981_LACYGNE7-542965_WGRDNR7_Ckt1 | 3 Phase fault on LACYGNE7 (542981) 345.0 kV a. Apply fault on LACYGNE7 (542981) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_533021_NEOSHO-532793_NEOSHO_3Winding | 3 Phase fault on NEOSHO (533021) 138.0 kV a. Apply fault on NEOSHO (533021) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532824) to trip transformer at N345 1 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_533021_NEOSHO-533022_NEOSHON4_CktZ1 | 3 Phase fault on NEOSHO (533021) 138.0 kV a. Apply fault on NEOSHO (533021) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_532937_NEOSHO-532793_NEOSHO_3Winding | 3 Phase fault on NEOSHO (532937) 161.0 kV a. Apply fault on NEOSHO (532937) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at N345 (532825) to trip transformer at N345 2 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_532937_NEOSHO-547469_RIV4525_Ckt1 | 3 Phase fault on NEOSHO (532937) 161.0 kV a. Apply fault on NEOSHO (532937) 161.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_533020_NEOSHOS4-532937_NEOSHO_3Winding | 3 Phase fault on NEOSHOS4 (533020) 138.0 kV a. Apply fault on NEOSHOS4 (533020) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEOSH5 (532959) to trip transformer at NEOSH5 1 13.200 (532959) 13.2 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_533020_NEOSHOS4-533003_LIBERTY4_Ckt1 | 3 Phase fault on NEOSHOS4 (533020) 138.0 kV a. Apply fault on NEOSHOS4 (533020) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS4 (533020) 138.0 bus to TV1MNDV4 (533008) 138.0 bus CKT 1 b. 2. Drop load from bus TV1MNDV4 (533008) 138.0 kV bus b. 3. Trip branch from TV1MNDV4 (533008) 138.0 bus to LIBERTY4 (533003) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHOS4 (533020) 138.0 bus to TV1MNDV4 (533008) 138.0 bus CKT 1 c. 2. Reclose branch from TV1MNDV4 (533008) 138.0 bus to LIBERTY4 (533003) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHOS4 (533020) 138.0 bus to TV1MNDV4 (533008) 138.0 bus CKT 1 d. 2. Trip branch from TV1MNDV4 (533008) 138.0 bus to LIBERTY4 (533003) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_533020_NEOSHOS4-533021_NEOSHO_CktZ1 | 3 Phase fault on NEOSHOS4 (533020) 138.0 kV a. Apply fault on NEOSHOS4 (533020) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS4 (533020) 138.0 kV bus to NEOSHO (533021) 138.0 kV bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHOS4 (533020) 138.0 kV bus to NEOSHO (533021) 138.0 kV bus CKT Z1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHOS4 (533020) 138.0 kV bus to NEOSHO (533021) 138.0 kV bus CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_533022_NEOSHON4-588664_G17-022-TAP_Ckt1 | 3 Phase fault on NEOSHON4 (533022) 138.0 kV a. Apply fault on NEOSHON4 (533022) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHON4 (533022) 138.0 bus to NEPARSN4 (533005) 138.0 bus CKT 1 b. 2. Drop load from bus NEPARSN4 (533005) 138.0 kV bus b. 3. Drop load from bus NEPARSN4 (533005) 138.0 kV bus b. 4. Drop load from bus NEPARSN4 (533005) 138.0 kV bus b. 5. Drop switching device from bus NEPARSN4 (533005) 138.0 kV bus b. 6. Trip branch from NEPARSN4 (533005) 138.0 bus to G17-022-TAP (588664) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from NEOSHON4 (533022) 138.0 bus to NEPARSN4 (533005) 138.0 bus CKT 1 c. 2. Reclose branch from NEPARSN4 (533005) 138.0 bus to G17-022-TAP (588664) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from NEOSHON4 (533022) 138.0 bus to NEPARSN4 (533005) 138.0 bus CKT 1 d. 2. Trip branch from NEPARSN4 (533005) 138.0 bus to G17-022-TAP (588664) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_533022_NEOSHON4-533768_NEOSHON2_3Winding | 3 Phase fault on NEOSHON4 (533022) 138.0 kV a. Apply fault on NEOSHON4 (533022) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at NEC (532711) to trip transformer at NEC U3 12.000 (532711) 12.0 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-510380_DELWARE7 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345.0 kV bus a. Apply single-phase fault on DELWARE7 (510380) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 b. 2. Trip branch from DELWARE7 (510380) 345.0 kV bus to NEOSHO (532793) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-510378_SCOFCTY4 | Single Phase Fault with Stuck Breaker on SCOFCTY4 (510378) 138.0 kV bus a. Apply single-phase fault on SCOFCTY4 (510378) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to FARML (512734) 138.0 kV bus CKT 1 b. 2. Trip branch from SCOFCTY4 (510378) 138.0 kV bus to COFFEYT4 (510422) 138.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-510406_NES-7 | Single Phase Fault with Stuck Breaker on N.E.S.-7 (510406) 345.0 kV bus a. Apply single-phase fault on N.E.S.-7 (510406) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to DELWARE7 (510380) 345.0 kV bus CKT 1 b. 2. Trip branch from N.E.S.-7 (510406) 345.0 kV bus to T.NO.--7 (509852) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-532793_NEOSHO | Single Phase Fault with Stuck Breaker on NEOSHO (532793) 345.0 kV bus a. Apply single-phase fault on NEOSHO (532793) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect N345 (532825) 13.8 kV bus to trip transformer at N345 2 1 13.8 kV bus b. 2. Trip branch from NEOSHO (532793) 345.0 kV bus to LACYGNE7 (542981) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-509807_ONETA--7 | Single Phase Fault with Stuck Breaker on ONETA--7 (509807) 345.0 kV bus a. Apply single-phase fault on ONETA--7 (509807) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 2 b. 2. Trip branch from ONETA--7 (509807) 345.0 kV bus to OEC (509836) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-509852_TNO--7 | Single Phase Fault with Stuck Breaker on T.NO.--7 (509852) 345.0 kV bus a. Apply single-phase fault on T.NO.--7 (509852) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect TNO2-1 (509894) 34.5 kV bus to trip transformer at TNO2-1 34.500 (509894) 34.5 kV bus b. 2. Trip branch from T.NO.--7 (509852) 345.0 kV bus to N.E.S.-7 (510406) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-542981_LACYGNE7 | Single Phase Fault with Stuck Breaker on LACYGNE7 (542981) 345.0 kV bus a. Apply single-phase fault on LACYGNE7 (542981) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345.0 kV bus to STILWEL7 (542968) 345.0 kV bus CKT 1 b. 2. Trip branch from LACYGNE7 (542981) 345.0 kV bus to W.GRDNR7 (542965) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-533021_NEOSHO | Single Phase Fault with Stuck Breaker on NEOSHO (533021) 138.0 kV bus a. Apply single-phase fault on NEOSHO (533021) 138.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect N345 (532824) 13.8 kV bus to trip transformer at N345 1 1 13.8 kV bus b. 2. Trip branch from NEOSHO (533021) 138.0 kV bus to NEOSHON4 (533022) 138.0 kV bus CKT Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-532937_NEOSHO | Single Phase Fault with Stuck Breaker on NEOSHO (532937) 161.0 kV bus a. Apply single-phase fault on NEOSHO (532937) 161.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Disconnect N345 (532825) 13.8 kV bus to trip transformer at N345 2 1 13.8 kV bus b. 2. Trip branch from NEOSHO (532937) 161.0 kV bus to RIV4525 (547469) 161.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510907_PITTSB-7-514809_JOHNCO_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510907_PITTSB-7-515045_SEMINOL7_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510907_PITTSB-7-515422_C-RIVER7_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to C-RIVER7 (515422) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510907_PITTSB-7-510911_VALIANT7_Ckt1 | 3 Phase fault on PITTSB-7 (510907) 345.0 kV a. Apply fault on PITTSB-7 (510907) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to VALIANT7 (510911) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510911_VALIANT7-508298_LYDIA_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to LYDIA (508298) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510911_VALIANT7-510918_VALIANT4_3Winding | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at VALN3-1 (510939) to trip transformer at VALN3-1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510911_VALIANT7-521157_HUGO_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to HUGO (521157) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510911_VALIANT7-508072_NWTXARK7_Ckt1 | 3 Phase fault on VALIANT7 (510911) 345.0 kV a. Apply fault on VALIANT7 (510911) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT7 (510911) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT7 (510911) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514809_JOHNCO-514808_JOHNCO_3Winding | 3 Phase fault on JOHNCO (514809) 345.0 kV a. Apply fault on JOHNCO (514809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at JOHNCO11 (514810) to trip transformer at JOHNCO11 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P4_HOL-510907_PITTSB-7 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345.0 kV bus a. Apply single-phase fault on PITTSB-7 (510907) 345.0 kV bus b. Clear fault after 16 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345.0 kV bus to JOHNCO (514809) 345.0 kV bus CKT 1 b. 2. Trip branch from PITTSB-7 (510907) 345.0 kV bus to SEMINOL7 (515045) 345.0 kV bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514809_JOHNCO-515136_SUNNYSD7_Ckt1 | 3 Phase fault on JOHNCO (514809) 345.0 kV a. Apply fault on JOHNCO (514809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to SUNNYSD7 (515136) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514809_JOHNCO-516006_DMNDSPG7_Ckt1 | 3 Phase fault on JOHNCO (514809) 345.0 kV a. Apply fault on JOHNCO (514809) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to DMNDSPG7 (516006) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514809) 345.0 kV bus to DMNDSPG7 (516006) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514809) 345.0 kV bus to DMNDSPG7 (516006) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515045_SEMINOL7-514934_DRAPER_Ckt1 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515045_SEMINOL7-514934_DRAPER_Ckt2 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 2 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515045_SEMINOL7-515044_SEMINOL4_Ckt3 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 bus to SEMINOL4 (515044) 345.0 bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 bus to SEMINOL4 (515044) 345.0 bus CKT 3 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 bus to SEMINOL4 (515044) 345.0 bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515045_SEMINOL7-515044_SEMINOL4_3Winding | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SEMINO11 (515756) to trip transformer at SEMINO11 14.400 (515756) 14.399999618530273 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515045_SEMINOL7-514934_DRAPER_Ckt3 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 3 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to DRAPER (514934) 345.0 kV bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515045_SEMINOL7-588839_FIREWHL-TAP_Ckt1 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515045_SEMINOL7-514908_ARCADIA7_Ckt1 | 3 Phase fault on SEMINOL7 (515045) 345.0 kV a. Apply fault on SEMINOL7 (515045) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to ARCADIA7 (514908) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SEMINOL7 (515045) 345.0 kV bus to ARCADIA7 (514908) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SEMINOL7 (515045) 345.0 kV bus to ARCADIA7 (514908) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515422_C-RIVER7-510951_TALAWANDA_3Winding | 3 Phase fault on C-RIVER7 (515422) 345.0 kV a. Apply fault on C-RIVER7 (515422) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at C-RIVER1 (510947) to trip transformer at C-RIVER1 13.8 kV bus b. 2. Trip branch from C-RIVER4 (510946) 138.0 bus to TALAWANDA (510951) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from C-RIVER4 (510946) 138.0 bus to TALAWANDA (510951) 138.0 bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from C-RIVER4 (510946) 138.0 bus to TALAWANDA (510951) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515422_C-RIVER7-588839_FIREWHL-TAP_Ckt1 | 3 Phase fault on C-RIVER7 (515422) 345.0 kV a. Apply fault on C-RIVER7 (515422) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from C-RIVER7 (515422) 345.0 kV bus to FIREWHL-TAP (588839) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508298_LYDIA-508359_WELSH_Ckt1 | 3 Phase fault on LYDIA (508298) 345.0 kV a. Apply fault on LYDIA (508298) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LYDIA (508298) 345.0 kV bus to WELSH (508359) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_508298_LYDIA-508072_NWTXARK7_Ckt1 | 3 Phase fault on LYDIA (508298) 345.0 kV a. Apply fault on LYDIA (508298) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA (508298) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from LYDIA (508298) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from LYDIA (508298) 345.0 kV bus to NWTXARK7 (508072) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510918_VALIANT4-510866_V-WEYCO4_Ckt1 | 3 Phase fault on VALIANT4 (510918) 138.0 kV a. Apply fault on VALIANT4 (510918) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Drop load from bus V-WEYCO4 (510866) 138.0 kV bus b. 2. Drop switching device from bus V-WEYCO4 (510866) 138.0 kV bus b. 3. Trip branch from VALIANT4 (510918) 138.0 bus to V-WEYCO4 (510866) 138.0 bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT4 (510918) 138.0 bus to V-WEYCO4 (510866) 138.0 bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT4 (510918) 138.0 bus to V-WEYCO4 (510866) 138.0 bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_510918_VALIANT4-520948_HUGO_Ckt1 | 3 Phase fault on VALIANT4 (510918) 138.0 kV a. Apply fault on VALIANT4 (510918) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from VALIANT4 (510918) 138.0 kV bus to HUGO (520948) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515136_SUNNYSD7-511568_TERRYRD7_Ckt1 | 3 Phase fault on SUNNYSD7 (515136) 345.0 kV a. Apply fault on SUNNYSD7 (515136) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 d. Leave fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from SUNNYSD7 (515136) 345.0 kV bus to TERRYRD7 (511568) 345.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_515136_SUNNYSD7-515135_SUNNYSD4_3Winding | 3 Phase fault on SUNNYSD7 (515136) 345.0 kV a. Apply fault on SUNNYSD7 (515136) 345.0 kV b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Disconnect bus at SUNYSD (515405) to trip transformer at SUNYSD 1 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514808_JOHNCO-514809_JOHNCO_3Winding | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Disconnect bus at JOHNCO11 (514810) to trip transformer at JOHNCO11 13.8 kV bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514808_JOHNCO-515120_RUSSET-4_Ckt1 | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to RUSSET-4 (515120) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.
04 SOUTHEAST | DISIS-2018-002 / DISIS-2019-001 | 25W | Transfer | P1_514808_JOHNCO-515150_CANEYCK4_Ckt1 | 3 Phase fault on JOHNCO (514808) 138.0 kV a. Apply fault on JOHNCO (514808) 138.0 kV b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the fault: c. 1. Reclose branch from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 d. Leave fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault: d. 1. Trip branch from JOHNCO (514808) 138.0 kV bus to CANEYCK4 (515150) 138.0 kV bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Damping and Tripping issues observed with CQ GEN-2018-115. Adjusting the dynamic model parameters for the rate of change of reactive current (Iqr) to -20/+20 and deadband output limits (emax/emin) -99/+99 resolves the tripping and damping issues. | Model tuned to not trip during fault conditions. No additional system issues observed.