DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526332 [JONES_2 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.9629 | 0.1899 | 89.8676 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526332 [JONES_2 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.9629 | 0.1887 | 88.7047 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526332 [JONES_2 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.9629 | 7.154 | 7054.0285 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526332 [JONES_2 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.9629 | 7.1067 | 7006.706 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 15.8727 | 15772.6901 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 17.508 | 17407.9694 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 19.0853 | 18985.2856 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 18.201 | 18100.9995 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 19.9536 | 19853.6242 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 20.1053 | 20005.2936 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 20.1684 | 20068.3903 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 19.528 | 19428.0459 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 27.8794 | 1.8377 | 1737.711 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 21.1199 | 45.4808 | 45380.8083 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 21.1199 | 6.0528 | 5952.803 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 21.1199 | 1.7861 | 1686.0667 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 21.1199 | 6.0528 | 5952.7948 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 18.8998 | 11.2641 | 11164.1096 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 10.0395 | 4.856 | 4755.9963 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 10.0395 | 4.856 | 4755.9963 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.9672 | 0.1899 | 89.8666 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.9672 | 0.1887 | 88.7029 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.9672 | 7.1195 | 7019.4873 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.9672 | 7.0723 | 6972.2848 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 15.8729 | 15772.9125 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 17.5082 | 17408.2331 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 19.0856 | 18985.5972 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 18.2013 | 18101.2946 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 19.954 | 19853.9779 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 20.1056 | 20005.6479 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 20.1687 | 20068.7428 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 12.3246 | 19.5284 | 19428.3871 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 27.8782 | 1.8377 | 1737.7288 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 21.1183 | 45.4816 | 45381.5647 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 21.1183 | 6.0535 | 5953.4515 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 21.1183 | 1.7862 | 1686.1638 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 21.1183 | 6.0534 | 5953.4433 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 18.8616 | 11.3004 | 11200.4434 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 10.0392 | 4.8561 | 4756.1 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 10.0392 | 4.8561 | 4756.1 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.9663 | 0.1899 | 89.8671 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.9663 | 0.1887 | 88.7034 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.9663 | 7.1206 | 7020.5606 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.9663 | 7.0733 | 6973.3313 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 12.1901 | 15.7976 | 15697.5509 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 12.1901 | 17.4267 | 17326.7433 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 12.1901 | 18.9907 | 18890.6748 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 12.1901 | 18.1302 | 18030.2298 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 12.1901 | 19.8574 | 19757.442 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 12.1901 | 19.9983 | 19898.3021 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 12.1901 | 20.0623 | 19962.3106 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 12.1901 | 19.4843 | 19384.2577 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 27.9177 | 1.8346 | 1734.5907 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 21.1885 | 45.4242 | 45324.2282 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 21.1885 | 5.8558 | 5755.7848 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 21.1885 | 1.7566 | 1656.5961 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 21.1885 | 5.8558 | 5755.7761 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 20.5773 | 10.0312 | 9931.1601 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 10.053 | 4.8328 | 4732.8291 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 10.053 | 4.8328 | 4732.8291 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 4.9907 | 0.1899 | 89.8576 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 4.9907 | 0.1887 | 88.6909 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 4.9907 | 6.9979 | 6897.9411 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 4.9907 | 6.9514 | 6851.447 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 12.1453 | 15.7899 | 15689.852 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 12.1453 | 17.4222 | 17322.206 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 12.1453 | 18.9855 | 18885.5257 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 12.1453 | 18.1331 | 18033.1365 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 12.1453 | 19.8605 | 19760.513 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 12.1453 | 19.9925 | 19892.4953 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 12.1453 | 20.0566 | 19956.5978 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 12.1453 | 19.4876 | 19387.6117 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 27.9176 | 1.835 | 1734.9553 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 16.6029 | 46.7246 | 46624.5691 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 16.6029 | 5.8078 | 5707.8012 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 16.6029 | 1.7565 | 1656.5248 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 16.6029 | 5.8078 | 5707.7928 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 20.5214 | 10.0729 | 9972.9419 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 10.051 | 4.8372 | 4737.1859 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 10.051 | 4.8372 | 4737.1859 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 4.0847 | 0.1913 | 91.2633 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 4.0847 | 0.1901 | 90.0762 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 4.0847 | 7.3036 | 7203.5761 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 4.0847 | 7.2434 | 7143.4301 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 12.3744 | 15.8868 | 15786.8257 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 12.3744 | 17.524 | 17423.9663 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 12.3744 | 19.1037 | 19003.6757 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 12.3744 | 18.2218 | 18121.846 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 12.3744 | 19.9748 | 19874.8237 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 12.3744 | 20.1261 | 20026.0575 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 12.3744 | 20.1889 | 20088.9003 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 12.3744 | 19.5519 | 19451.8831 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 27.9256 | 1.8378 | 1737.8255 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 21.1839 | 45.514 | 45413.9582 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 21.1839 | 6.3549 | 6254.9032 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 21.1839 | 1.837 | 1737.0377 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 21.1839 | 6.3549 | 6254.8929 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 20.544 | 10.08 | 9979.9724 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 10.0525 | 4.8574 | 4757.3949 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 10.0525 | 4.8574 | 4757.3949 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 5.0163 | 0.1898 | 89.8305 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 5.0163 | 0.1887 | 88.67 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 5.0163 | 7.1758 | 7075.8125 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 5.0163 | 7.13 | 7029.9518 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 10.934 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 10.934 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 10.934 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 10.934 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 10.934 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 10.934 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 10.934 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 10.934 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 26.6063 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 18.32 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 18.32 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 18.32 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 18.32 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 19.6842 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 9.554 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 9.554 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 4.531 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 4.531 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 4.531 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 4.531 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 12.1862 | 15.7944 | 15694.4036 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 12.1862 | 17.4246 | 17324.5679 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 12.1862 | 18.9881 | 18888.1363 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 12.1862 | 18.1308 | 18030.839 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 12.1862 | 19.8577 | 19757.7226 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 12.1862 | 19.9954 | 19895.4307 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 12.1862 | 20.0595 | 19959.4622 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 12.1862 | 19.4849 | 19384.9422 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 27.8926 | 1.8341 | 1734.1349 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 21.0253 | 45.4516 | 45351.6067 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 21.0253 | 5.6573 | 5557.2665 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 21.0253 | 1.7296 | 1629.5652 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 21.0253 | 5.6573 | 5557.2587 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 20.5433 | 10.0721 | 9972.0576 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 10.0437 | 4.8352 | 4735.1538 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 10.0437 | 4.8352 | 4735.1538 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 4.9855 | 0.1899 | 89.87 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 4.9855 | 0.1887 | 88.7027 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 4.9855 | 6.9851 | 6885.0717 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 4.9855 | 6.9385 | 6838.5017 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 12.1862 | 15.7944 | 15694.4036 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 12.1862 | 17.4246 | 17324.5679 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 12.1862 | 18.9881 | 18888.1363 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 12.1862 | 18.1308 | 18030.839 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 12.1862 | 19.8577 | 19757.7226 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 12.1862 | 19.9954 | 19895.4307 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 12.1862 | 20.0595 | 19959.4622 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 12.1862 | 19.4849 | 19384.9422 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 27.8926 | 1.8341 | 1734.1349 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 21.0253 | 45.4516 | 45351.6067 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 21.0253 | 5.6573 | 5557.2665 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 21.0253 | 1.7296 | 1629.5652 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 21.0253 | 5.6573 | 5557.2587 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 20.5433 | 10.0721 | 9972.0576 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 10.0437 | 4.8352 | 4735.1538 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 10.0437 | 4.8352 | 4735.1538 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 4.9855 | 0.1899 | 89.87 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 4.9855 | 0.1887 | 88.7027 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 4.9855 | 6.9851 | 6885.0717 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 4.9855 | 6.9385 | 6838.5017 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 12.1862 | 15.7977 | 15697.7173 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 12.1862 | 17.427 | 17327.0327 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 12.1862 | 18.991 | 18891.0489 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 12.1862 | 18.1305 | 18030.5012 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 12.1862 | 19.858 | 19757.9508 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 12.1862 | 19.9987 | 19898.7325 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 12.1862 | 20.0627 | 19962.7457 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 12.1862 | 19.4846 | 19384.583 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 27.8922 | 1.8344 | 1734.3503 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 20.3554 | 45.7794 | 45679.3748 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 20.3554 | 5.9767 | 5876.6552 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 20.3554 | 1.7738 | 1673.7879 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 20.3554 | 5.9766 | 5876.6459 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 20.5331 | 10.0762 | 9976.1961 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 10.0426 | 4.837 | 4736.9549 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 10.0426 | 4.837 | 4736.9549 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 4.9599 | 0.1899 | 89.8814 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 4.9599 | 0.1887 | 88.7145 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 4.9599 | 7.0146 | 6914.5517 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 4.9599 | 6.9675 | 6867.5254 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 12.1877 | 15.7958 | 15695.7776 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 12.1877 | 17.4255 | 17325.509 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 12.1877 | 18.9892 | 18889.235 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 12.1877 | 18.1306 | 18030.5532 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 12.1877 | 19.8576 | 19757.567 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 12.1877 | 19.9967 | 19896.6747 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 12.1877 | 20.0607 | 19960.6925 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 12.1877 | 19.4846 | 19384.6188 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 27.9149 | 1.8342 | 1734.1682 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 21.054 | 45.3542 | 45254.1902 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 21.054 | 5.7627 | 5662.6561 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 21.054 | 1.744 | 1644.0253 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 21.054 | 5.7626 | 5662.649 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 20.5416 | 10.0724 | 9972.3872 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 10.0453 | 4.8262 | 4726.2181 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 10.0453 | 4.8262 | 4726.2181 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 4.9835 | 0.1899 | 89.8711 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 4.9835 | 0.1887 | 88.7038 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 4.9835 | 6.9749 | 6874.8626 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 4.9835 | 6.9286 | 6828.5751 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1854 | 15.7938 | 15693.8485 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1854 | 17.4242 | 17324.2075 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1854 | 18.9877 | 18887.7227 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1854 | 18.131 | 18030.9879 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1854 | 19.8578 | 19757.8437 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1854 | 19.995 | 19894.9632 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1854 | 20.059 | 19958.9994 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1854 | 19.4851 | 19385.1122 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 27.9174 | 1.8341 | 1734.1403 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 21.1473 | 45.3442 | 45244.1651 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 21.1473 | 5.6928 | 5592.7724 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 21.1473 | 1.7342 | 1634.1922 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 21.1473 | 5.6928 | 5592.7645 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 20.5426 | 10.0721 | 9972.135 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 10.0524 | 4.8302 | 4730.1769 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 10.0524 | 4.8302 | 4730.1769 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.9879 | 0.1899 | 89.8646 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.9879 | 0.1887 | 88.6975 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.9879 | 6.9793 | 6879.3259 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.9879 | 6.933 | 6833.0007 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 12.1854 | 15.7938 | 15693.8485 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 12.1854 | 17.4242 | 17324.2075 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 12.1854 | 18.9877 | 18887.7227 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 12.1854 | 18.131 | 18030.9879 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 12.1854 | 19.8578 | 19757.8437 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 12.1854 | 19.995 | 19894.9632 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 12.1854 | 20.059 | 19958.9994 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 12.1854 | 19.4851 | 19385.1122 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 27.9174 | 1.8341 | 1734.1403 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 21.1473 | 45.3442 | 45244.1651 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 21.1473 | 5.6928 | 5592.7724 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 21.1473 | 1.7342 | 1634.1922 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 21.1473 | 5.6928 | 5592.7645 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 20.5426 | 10.0721 | 9972.135 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 10.0524 | 4.8302 | 4730.1769 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 10.0524 | 4.8302 | 4730.1769 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 4.9879 | 0.1899 | 89.8646 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 4.9879 | 0.1887 | 88.6975 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 4.9879 | 6.9793 | 6879.3259 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 4.9879 | 6.933 | 6833.0007 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1903 | 15.7979 | 15697.8763 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1903 | 17.4269 | 17326.9459 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1903 | 18.9909 | 18890.9074 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1903 | 18.1301 | 18030.1256 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1903 | 19.8573 | 19757.3399 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1903 | 19.9986 | 19898.5646 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1903 | 20.0626 | 19962.5676 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 12.1903 | 19.4841 | 19384.1362 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 27.9162 | 1.8344 | 1734.432 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 21.1549 | 45.4299 | 45329.8795 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 21.1549 | 5.8672 | 5767.2395 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 21.1549 | 1.7583 | 1658.3174 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 21.1549 | 5.8672 | 5767.2315 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 20.5417 | 10.0731 | 9973.1045 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 10.0481 | 4.8307 | 4730.6965 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 10.0481 | 4.8307 | 4730.6965 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.9887 | 0.1899 | 89.8607 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.9887 | 0.1887 | 88.6939 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.9887 | 6.9948 | 6894.8221 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.9887 | 6.9484 | 6848.3528 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 10.2509 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 10.2509 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 10.2509 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 10.2509 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 10.2509 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 10.2509 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 10.2509 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 10.2509 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 28.3995 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 22.5778 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 22.5778 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 22.5778 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 22.5778 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 21.1746 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 10.8811 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 10.8811 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 5.4417 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 5.4417 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 5.4417 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 5.4417 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 12.3034 | 15.8545 | 15754.4659 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 12.3034 | 17.4867 | 17386.7257 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 12.3034 | 19.0604 | 18960.4025 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 12.3034 | 18.1758 | 18075.7845 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 12.3034 | 19.9252 | 19825.1902 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 12.3034 | 20.0771 | 19977.1208 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 12.3034 | 20.1404 | 20040.4207 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 12.3034 | 19.499 | 19399.0443 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 27.9219 | 1.8365 | 1736.52 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 21.1907 | 1.9753 | 1875.3042 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 21.1907 | 7.0535 | 6953.474 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 20.5431 | 10.0833 | 9983.3412 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 10.0527 | 4.8476 | 4747.6393 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 10.0527 | 4.8476 | 4747.6393 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 5.0042 | 0.1899 | 89.8903 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 5.0042 | 0.1887 | 88.7264 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 5.0042 | 7.1222 | 7022.2253 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 5.0042 | 7.075 | 6975.0432 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 12.3034 | 15.8545 | 15754.4659 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 12.3034 | 17.4867 | 17386.7257 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 12.3034 | 19.0604 | 18960.4025 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 12.3034 | 18.1758 | 18075.7845 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 12.3034 | 19.9252 | 19825.1902 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 12.3034 | 20.0771 | 19977.1208 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 12.3034 | 20.1404 | 20040.4207 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 12.3034 | 19.499 | 19399.0443 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 27.9219 | 1.8365 | 1736.52 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 21.1907 | 46.0704 | 45970.415 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 21.1907 | 7.0535 | 6953.4519 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 20.5431 | 10.0833 | 9983.3412 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 10.0527 | 4.8476 | 4747.6393 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 10.0527 | 4.8476 | 4747.6393 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 5.0042 | 0.1899 | 89.8903 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 5.0042 | 0.1887 | 88.7264 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 5.0042 | 7.1222 | 7022.2255 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 5.0042 | 7.075 | 6975.0433 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 10.6229 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 10.6229 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 10.6229 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 10.6229 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 10.6229 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 10.6229 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 10.6229 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 10.6229 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 29.096 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 22.7823 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 22.7823 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 22.7823 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 22.7823 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 22.4011 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 11.034 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 11.034 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 5.5513 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 5.5513 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 5.5513 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 5.5513 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 12.0681 | 15.8066 | 15706.6022 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 12.0681 | 17.4406 | 17340.5597 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 12.0681 | 19.0082 | 18908.1732 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 12.0681 | 18.1421 | 18042.1155 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 12.0681 | 19.8796 | 19779.5703 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 12.0681 | 20.0182 | 19918.2474 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 12.0681 | 20.0826 | 19982.5667 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 12.0681 | 19.4984 | 19398.4484 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 27.9171 | 1.8344 | 1734.4307 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 21.1876 | 45.4234 | 45323.3807 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 21.1876 | 5.8532 | 5753.1669 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 21.1876 | 1.7562 | 1656.2227 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 21.1876 | 5.8532 | 5753.1579 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 20.5418 | 10.0733 | 9973.3462 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 10.053 | 4.8324 | 4732.4465 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 10.053 | 4.8324 | 4732.4465 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 4.99 | 0.1899 | 89.8587 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 4.99 | 0.1887 | 88.692 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 4.99 | 6.9973 | 6897.2859 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 4.99 | 6.9508 | 6850.8074 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.1573 | 15.8017 | 15701.6938 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.1573 | 17.4331 | 17333.1324 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.1573 | 18.9988 | 18898.8166 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.1573 | 18.1357 | 18035.6581 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.1573 | 19.8678 | 19767.7628 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.1573 | 20.0076 | 19907.6268 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.1573 | 20.0718 | 19971.769 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 12.1573 | 19.4908 | 19390.7804 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 27.9167 | 1.8344 | 1734.4355 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 21.1872 | 45.4235 | 45323.5131 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 21.1872 | 5.8541 | 5754.0805 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 21.1872 | 1.7564 | 1656.3543 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 21.1872 | 5.8541 | 5754.0722 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 20.5414 | 10.0733 | 9973.2663 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 10.0528 | 4.8326 | 4732.562 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 10.0528 | 4.8326 | 4732.562 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 4.9898 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 4.9898 | 0.1887 | 88.692 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 4.9898 | 6.9964 | 6896.3515 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 4.9898 | 6.9499 | 6849.8708 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 12.1792 | 15.7936 | 15693.6027 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 12.1792 | 17.4224 | 17322.394 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 12.1792 | 18.9852 | 18885.2479 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 12.1792 | 18.1282 | 18028.2426 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 12.1792 | 19.8529 | 19752.8895 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 12.1792 | 19.9921 | 19892.0712 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 12.1792 | 20.056 | 19956.0418 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 12.1792 | 19.4818 | 19381.8026 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 27.9169 | 1.8344 | 1734.4325 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 21.1878 | 45.4234 | 45323.3763 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 21.1878 | 5.8539 | 5753.9337 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 21.1878 | 1.7563 | 1656.3342 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 21.1878 | 5.8539 | 5753.925 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 20.542 | 10.0731 | 9973.0718 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 10.0529 | 4.8325 | 4732.529 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 10.0529 | 4.8325 | 4732.529 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 4.9902 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 4.9902 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 4.9902 | 6.9963 | 6896.3197 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 4.9902 | 6.9498 | 6849.8469 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 12.1773 | 15.7904 | 15690.3632 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 12.1773 | 17.4187 | 17318.725 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 12.1773 | 18.9807 | 18880.6695 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 12.1773 | 18.1264 | 18026.4006 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 12.1773 | 19.8488 | 19748.8494 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 12.1773 | 19.9868 | 19886.8255 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 12.1773 | 20.0508 | 19950.7591 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 12.1773 | 19.4795 | 19379.5464 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 27.9169 | 1.8344 | 1734.4299 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 21.1878 | 45.4233 | 45323.3413 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 21.1878 | 5.8538 | 5753.7539 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 21.1878 | 1.7563 | 1656.3089 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 21.1878 | 5.8537 | 5753.7452 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 20.542 | 10.073 | 9973.0415 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 10.0529 | 4.8325 | 4732.5092 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 10.0529 | 4.8325 | 4732.5092 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 4.9902 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 4.9902 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 4.9902 | 6.9963 | 6896.2825 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 4.9902 | 6.9498 | 6849.8114 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 12.0636 | 15.8026 | 15702.559 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 12.0636 | 17.4352 | 17335.2421 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 12.0636 | 19.0014 | 18901.4402 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 12.0636 | 18.1386 | 18038.555 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 12.0636 | 19.8723 | 19772.2899 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 12.0636 | 20.0105 | 19910.508 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 12.0636 | 20.0747 | 19974.7489 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 12.0636 | 19.4941 | 19394.1181 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 27.9172 | 1.8344 | 1734.4284 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 21.1876 | 45.4233 | 45323.3074 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 21.1876 | 5.8528 | 5752.7965 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 21.1876 | 1.7562 | 1656.1694 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 21.1876 | 5.8528 | 5752.7875 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 20.5418 | 10.0733 | 9973.2972 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 10.053 | 4.8324 | 4732.4066 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 10.053 | 4.8324 | 4732.4066 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 4.99 | 0.1899 | 89.8587 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 4.99 | 0.1887 | 88.6921 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 4.99 | 6.9975 | 6897.4589 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 4.99 | 6.951 | 6850.9852 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 12.1161 | 15.7981 | 15698.1176 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 12.1161 | 17.4289 | 17328.8507 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 12.1161 | 18.9934 | 18893.3883 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 12.1161 | 18.1334 | 18033.3923 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 12.1161 | 19.8626 | 19762.6019 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 12.1161 | 20.0013 | 19901.344 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 12.1161 | 20.0654 | 19965.4471 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 12.1161 | 19.488 | 19387.9551 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 27.9165 | 1.8344 | 1734.4338 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 21.1868 | 45.4235 | 45323.4687 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 21.1868 | 5.8539 | 5753.8553 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 21.1868 | 1.7563 | 1656.3222 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 21.1868 | 5.8538 | 5753.8473 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 20.5408 | 10.0733 | 9973.2521 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 10.0528 | 4.8325 | 4732.533 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 10.0528 | 4.8325 | 4732.533 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 4.9896 | 0.1899 | 89.8588 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 4.9896 | 0.1887 | 88.6921 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 4.9896 | 6.9965 | 6896.496 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 4.9896 | 6.95 | 6850.0191 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 12.1743 | 15.7957 | 15695.7281 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 12.1743 | 17.4245 | 17324.5413 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 12.1743 | 18.9879 | 18887.8899 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 12.1743 | 18.129 | 18029.0182 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 12.1743 | 19.8548 | 19754.7535 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 12.1743 | 19.9951 | 19895.0856 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 12.1743 | 20.0591 | 19959.07 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 12.1743 | 19.4828 | 19382.7572 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 27.9167 | 1.8344 | 1734.4358 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 21.1874 | 45.4234 | 45323.4223 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 21.1874 | 5.8541 | 5754.13 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 21.1874 | 1.7564 | 1656.362 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 21.1874 | 5.8541 | 5754.1213 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 20.5416 | 10.0731 | 9973.1067 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 10.0529 | 4.8326 | 4732.5521 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 10.0529 | 4.8326 | 4732.5521 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 4.99 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 4.99 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 4.99 | 6.9963 | 6896.3408 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 4.99 | 6.9499 | 6849.8666 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 12.1724 | 15.7951 | 15695.1254 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 12.1724 | 17.424 | 17324.0114 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 12.1724 | 18.9872 | 18887.246 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 12.1724 | 18.1289 | 18028.9462 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 12.1724 | 19.8545 | 19754.4649 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 12.1724 | 19.9943 | 19894.3491 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 12.1724 | 20.0583 | 19958.3357 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 12.1724 | 19.4827 | 19382.6593 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 27.9168 | 1.8344 | 1734.435 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 21.1875 | 45.4234 | 45323.4065 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 21.1875 | 5.8541 | 5754.0551 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 21.1875 | 1.7564 | 1656.3511 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 21.1875 | 5.854 | 5754.0465 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 20.5416 | 10.0731 | 9973.1015 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 10.0529 | 4.8325 | 4732.5478 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 10.0529 | 4.8325 | 4732.5478 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 4.99 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 4.99 | 0.1887 | 88.692 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 4.99 | 6.9963 | 6896.3079 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 4.99 | 6.9498 | 6849.8344 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 2.3684 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 2.3684 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 2.3684 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 2.3684 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 2.3684 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 2.3684 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 2.3684 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 2.3684 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 27.5661 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 21.4072 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 21.4072 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 21.4072 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 21.4072 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 20.4538 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 10.5568 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 10.5568 | 0 | 0 | 0 | 0 | PASS | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 5.034 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 5.034 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 5.034 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 766291 [G20-009-TAP 345.00] CKT 1 | 5.034 | 0 | 0 | 0 | 0 | FAIL | FAIL
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.0851 | 15.8792 | 15779.1963 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.0851 | 17.5545 | 17454.5378 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.0851 | 19.1842 | 19084.234 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.0851 | 18.3258 | 18225.7985 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.0851 | 20.1163 | 20016.2552 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.0851 | 20.2565 | 20156.5396 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.0851 | 20.3146 | 20214.6387 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 11.0851 | 19.7054 | 19605.441 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 27.8488 | 1.8299 | 1729.9122 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 20.9715 | 45.4356 | 45335.5671 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 20.9715 | 5.497 | 5396.9748 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 20.9715 | 1.7089 | 1608.8662 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 20.9715 | 5.497 | 5396.9685 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 20.1916 | 10.2329 | 10132.8757 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 10.0313 | 4.7898 | 4689.7565 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 10.0313 | 4.7898 | 4689.7565 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 4.8175 | 0.19 | 90.0449 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 4.8175 | 0.1889 | 88.8844 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 4.8175 | 7.3698 | 7269.7948 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 4.8175 | 7.3204 | 7220.4265 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 12.1709 | 15.7831 | 15683.1152 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 12.1709 | 17.4154 | 17315.4357 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 12.1709 | 18.9793 | 18879.3131 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 12.1709 | 18.1334 | 18033.4112 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 12.1709 | 19.8594 | 19759.3861 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 12.1709 | 19.9888 | 19888.7996 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 12.1709 | 20.0496 | 19949.584 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 12.1709 | 19.4879 | 19387.8604 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 27.9105 | 1.834 | 1733.9878 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 21.1856 | 45.419 | 45319.0455 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 21.1856 | 5.8323 | 5732.3289 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 21.1856 | 1.7532 | 1653.2434 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 21.1856 | 5.8323 | 5732.3209 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 20.5406 | 10.0713 | 9971.3329 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 10.0237 | 4.8449 | 4744.9497 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 10.0237 | 4.8449 | 4744.9497 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 4.9882 | 0.1899 | 89.861 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 4.9882 | 0.1887 | 88.6939 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 4.9882 | 6.9832 | 6883.1893 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 4.9882 | 6.9367 | 6836.689 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 12.1896 | 15.7974 | 15697.4395 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 12.1896 | 17.4267 | 17326.6564 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 12.1896 | 18.9906 | 18890.571 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 12.1896 | 18.1302 | 18030.2341 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 12.1896 | 19.8574 | 19757.4201 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 12.1896 | 19.9982 | 19898.1841 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 12.1896 | 20.0622 | 19962.1917 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 12.1896 | 19.4843 | 19384.2601 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 27.9168 | 1.8345 | 1734.5082 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 21.1876 | 45.4234 | 45323.4352 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 21.1876 | 5.8542 | 5754.1847 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 21.1876 | 1.7564 | 1656.3689 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 21.1876 | 5.8542 | 5754.1757 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 20.5417 | 10.0732 | 9973.2017 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 10.039 | 4.8214 | 4721.3898 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 10.039 | 4.8214 | 4721.3898 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 4.9901 | 0.1899 | 89.8585 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 4.9901 | 6.9963 | 6896.324 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 4.9901 | 6.9498 | 6849.8476 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 12.19 | 15.7976 | 15697.5989 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 12.19 | 17.4268 | 17326.7598 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 12.19 | 18.9907 | 18890.6917 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 12.19 | 18.1302 | 18030.194 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 12.19 | 19.8574 | 19757.3887 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 12.19 | 19.9983 | 19898.3183 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 12.19 | 20.0623 | 19962.326 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 12.19 | 19.4842 | 19384.214 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 27.9181 | 1.8344 | 1734.4189 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 21.1881 | 45.4232 | 45323.2255 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 21.1881 | 5.8544 | 5754.4466 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 21.1881 | 1.7564 | 1656.409 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 21.1881 | 5.8544 | 5754.4382 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 20.542 | 10.0729 | 9972.8506 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 10.0472 | 4.8136 | 4713.5716 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 10.0472 | 4.8136 | 4713.5716 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 4.9902 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 4.9902 | 0.1887 | 88.692 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 4.9902 | 6.9964 | 6896.3841 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 4.9902 | 6.9499 | 6849.9135 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 12.1898 | 15.7975 | 15697.4867 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 12.1898 | 17.4267 | 17326.6881 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 12.1898 | 18.9906 | 18890.6081 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 12.1898 | 18.1302 | 18030.2242 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 12.1898 | 19.8574 | 19757.4141 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 12.1898 | 19.9982 | 19898.2255 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 12.1898 | 20.0622 | 19962.2329 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 12.1898 | 19.4842 | 19384.2487 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 27.9171 | 1.8346 | 1734.5537 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 21.1876 | 45.4235 | 45323.4647 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 21.1876 | 5.8543 | 5754.3156 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 21.1876 | 1.7564 | 1656.3885 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 21.1876 | 5.8543 | 5754.3077 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 20.5418 | 10.0732 | 9973.1995 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 10.037 | 4.8239 | 4723.9448 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 10.037 | 4.8239 | 4723.9448 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 4.9901 | 6.9964 | 6896.3765 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 4.9901 | 6.9499 | 6849.901 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1899 | 15.7976 | 15697.5618 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1899 | 17.4267 | 17326.7376 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1899 | 18.9907 | 18890.6653 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1899 | 18.1302 | 18030.2039 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1899 | 19.8574 | 19757.3984 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1899 | 19.9983 | 19898.2892 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1899 | 20.0623 | 19962.2969 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1899 | 19.4842 | 19384.2264 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 27.9193 | 1.8344 | 1734.4224 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 21.1882 | 45.4231 | 45323.1487 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 21.1882 | 5.8543 | 5754.3364 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 21.1882 | 1.7564 | 1656.3922 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 21.1882 | 5.8543 | 5754.3284 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 20.5422 | 10.0731 | 9973.1367 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 9.7188 | 4.6927 | 4592.6643 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 9.7188 | 4.6927 | 4592.6643 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.9903 | 0.1899 | 89.8585 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.9903 | 0.1887 | 88.6918 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.9903 | 6.9962 | 6896.1807 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.9903 | 6.9497 | 6849.7072 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 12.1899 | 15.7976 | 15697.5526 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 12.1899 | 17.4267 | 17326.7312 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 12.1899 | 18.9907 | 18890.6576 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 12.1899 | 18.1302 | 18030.2074 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 12.1899 | 19.8574 | 19757.4003 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 12.1899 | 19.9983 | 19898.2814 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 12.1899 | 20.0623 | 19962.2896 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 12.1899 | 19.4842 | 19384.2298 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 27.9171 | 1.8343 | 1734.2656 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 21.1877 | 45.4233 | 45323.344 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 21.1877 | 5.8542 | 5754.2431 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 21.1877 | 1.7564 | 1656.3788 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 21.1877 | 5.8542 | 5754.2348 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 20.5419 | 10.0731 | 9973.0979 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 10.0328 | 4.8454 | 4745.4193 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 10.0328 | 4.8454 | 4745.4193 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 4.9902 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 4.9902 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 4.9902 | 6.9963 | 6896.3054 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 4.9902 | 6.9498 | 6849.8318 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 12.1897 | 15.7974 | 15697.4098 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 12.1897 | 17.4266 | 17326.636 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 12.1897 | 18.9905 | 18890.5469 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 12.1897 | 18.1302 | 18030.2409 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 12.1897 | 19.8574 | 19757.424 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 12.1897 | 19.9982 | 19898.1568 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 12.1897 | 20.0622 | 19962.1645 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 12.1897 | 19.4843 | 19384.2679 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 27.9158 | 1.8343 | 1734.2757 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 21.1874 | 45.4234 | 45323.383 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 21.1874 | 5.854 | 5753.9915 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 21.1874 | 1.7563 | 1656.3419 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 21.1874 | 5.854 | 5753.9829 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 20.5416 | 10.0732 | 9973.1633 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 9.9601 | 4.8519 | 4751.948 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 9.9601 | 4.8519 | 4751.948 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 4.9901 | 6.9962 | 6896.1733 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 4.9901 | 6.9497 | 6849.6975 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 12.1904 | 15.7979 | 15697.8817 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 12.1904 | 17.427 | 17326.9576 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 12.1904 | 18.9909 | 18890.9229 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 12.1904 | 18.1301 | 18030.1432 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 12.1904 | 19.8574 | 19757.3709 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 12.1904 | 19.9986 | 19898.58 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 12.1904 | 20.0626 | 19962.5857 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 12.1904 | 19.4842 | 19384.1573 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 27.9172 | 1.8335 | 1733.4571 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 21.1876 | 45.4228 | 45322.8311 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 21.1876 | 5.8536 | 5753.6493 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 21.1876 | 1.7563 | 1656.2954 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 21.1876 | 5.8536 | 5753.642 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 20.5423 | 10.0737 | 9973.7177 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 9.7176 | 4.7968 | 4696.7508 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 9.7176 | 4.7968 | 4696.7508 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 4.9902 | 0.1899 | 89.8585 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 4.9902 | 0.1887 | 88.6918 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 4.9902 | 6.9958 | 6895.8107 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 4.9902 | 6.9493 | 6849.3303 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 15.7979 | 15697.875 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 17.4269 | 17326.9457 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 18.9909 | 18890.9064 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 18.1301 | 18030.1317 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 19.8573 | 19757.3472 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 19.9986 | 19898.5609 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 20.0626 | 19962.5664 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 19.4841 | 19384.1434 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 27.839 | 1.835 | 1734.9914 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 21.154 | 45.4349 | 45334.8525 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 21.154 | 5.8704 | 5770.4301 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 21.154 | 1.7587 | 1658.6897 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 21.154 | 5.8704 | 5770.4224 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 20.538 | 10.0734 | 9973.425 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 8.6714 | 4.8227 | 4722.6559 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 8.6714 | 4.8227 | 4722.6559 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.991 | 0.1899 | 89.8579 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.991 | 0.1887 | 88.6914 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.991 | 7.0014 | 6901.4184 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.991 | 6.955 | 6854.9762 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 12.1933 | 15.8003 | 15700.2665 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 12.1933 | 17.4287 | 17328.6514 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 12.1933 | 18.9929 | 18892.9081 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 12.1933 | 18.1298 | 18029.758 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 12.1933 | 19.8573 | 19757.2909 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 12.1933 | 20.0008 | 19900.8286 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 12.1933 | 20.0648 | 19964.8175 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 12.1933 | 19.4837 | 19383.7302 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 27.9189 | 1.8351 | 1735.1223 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 21.1883 | 45.4493 | 45349.2822 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 21.1883 | 5.8642 | 5764.1507 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 21.1883 | 1.7577 | 1657.7125 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 21.1883 | 5.8641 | 5764.1427 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 20.5421 | 10.0776 | 9977.6447 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 10.067 | 4.9098 | 4809.7516 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 10.067 | 4.9098 | 4809.7516 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 4.9905 | 0.1899 | 89.8597 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 4.9905 | 0.1887 | 88.6931 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 4.9905 | 7.004 | 6903.9851 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 4.9905 | 6.9573 | 6857.3459 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 12.1897 | 15.7974 | 15697.4073 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 12.1897 | 17.4266 | 17326.6348 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 12.1897 | 18.9905 | 18890.546 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 12.1897 | 18.1302 | 18030.2417 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 12.1897 | 19.8574 | 19757.4259 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 12.1897 | 19.9982 | 19898.1554 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 12.1897 | 20.0622 | 19962.1633 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 12.1897 | 19.4843 | 19384.2698 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 27.9144 | 1.833 | 1733.0099 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 21.1879 | 45.4229 | 45322.9032 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 21.1879 | 5.8526 | 5752.5844 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 21.1879 | 1.7561 | 1656.141 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 21.1879 | 5.8526 | 5752.5761 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 20.5421 | 10.0733 | 9973.2976 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 10.0392 | 4.7804 | 4680.4083 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 10.0392 | 4.7804 | 4680.4083 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 4.9901 | 6.9956 | 6895.586 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 4.9901 | 6.9491 | 6849.1084 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 15.7977 | 15697.7446 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 17.4269 | 17326.857 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 18.9908 | 18890.8033 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 18.1302 | 18030.1564 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 19.8574 | 19757.3604 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 19.9984 | 19898.4449 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 20.0625 | 19962.451 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 12.1902 | 19.4842 | 19384.1725 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 27.9115 | 1.8343 | 1734.2764 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 21.1865 | 45.4239 | 45323.8982 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 21.1865 | 5.8552 | 5755.1848 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 21.1865 | 1.7565 | 1656.5112 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 21.1865 | 5.8552 | 5755.1757 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 20.542 | 10.0724 | 9972.3714 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 6.6674 | 5.6634 | 5563.4443 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 6.6674 | 5.6634 | 5563.4443 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.9903 | 0.1899 | 89.859 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.9903 | 0.1887 | 88.6923 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.9903 | 6.9956 | 6895.6225 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.9903 | 6.9492 | 6849.1606 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 12.1897 | 15.7974 | 15697.4441 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 12.1897 | 17.4267 | 17326.6584 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 12.1897 | 18.9906 | 18890.5725 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 12.1897 | 18.1302 | 18030.2316 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 12.1897 | 19.8574 | 19757.4166 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 12.1897 | 19.9982 | 19898.186 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 12.1897 | 20.0622 | 19962.1935 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 12.1897 | 19.4843 | 19384.2579 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 27.9169 | 1.8344 | 1734.4267 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 21.1876 | 45.4234 | 45323.4272 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 21.1876 | 5.8542 | 5754.2295 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 21.1876 | 1.7564 | 1656.3761 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 21.1876 | 5.8542 | 5754.2219 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 20.5418 | 10.0731 | 9973.1079 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 10.0537 | 4.828 | 4727.9751 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 10.0537 | 4.828 | 4727.9751 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 4.9901 | 6.9963 | 6896.3268 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 4.9901 | 6.9499 | 6849.8519 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 12.1897 | 15.7974 | 15697.434 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 12.1897 | 17.4267 | 17326.6515 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 12.1897 | 18.9906 | 18890.5646 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 12.1897 | 18.1302 | 18030.2337 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 12.1897 | 19.8574 | 19757.4179 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 12.1897 | 19.9982 | 19898.1767 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 12.1897 | 20.0622 | 19962.1843 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 12.1897 | 19.4843 | 19384.2596 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 27.9169 | 1.8344 | 1734.4202 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 21.1877 | 45.4234 | 45323.4138 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 21.1877 | 5.8542 | 5754.2124 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 21.1877 | 1.7564 | 1656.3737 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 21.1877 | 5.8542 | 5754.2047 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 20.5418 | 10.0731 | 9973.1008 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 10.0542 | 4.8253 | 4725.2948 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 10.0542 | 4.8253 | 4725.2948 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 4.9901 | 0.1899 | 89.8585 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 4.9901 | 6.9963 | 6896.312 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 4.9901 | 6.9498 | 6849.8372 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 12.1896 | 15.7974 | 15697.4104 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 12.1896 | 17.4266 | 17326.6362 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 12.1896 | 18.9905 | 18890.5474 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 12.1896 | 18.1302 | 18030.2396 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 12.1896 | 19.8574 | 19757.4223 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 12.1896 | 19.9982 | 19898.1575 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 12.1896 | 20.0622 | 19962.1651 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 12.1896 | 19.4843 | 19384.2661 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 27.9166 | 1.8345 | 1734.4561 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 21.1875 | 45.4235 | 45323.4564 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 21.1875 | 5.8542 | 5754.1804 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 21.1875 | 1.7564 | 1656.3682 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 21.1875 | 5.8542 | 5754.172 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 20.5417 | 10.0731 | 9973.1267 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 10.0512 | 4.8413 | 4741.3303 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 10.0512 | 4.8413 | 4741.3303 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 4.9901 | 6.9963 | 6896.3216 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 4.9901 | 6.9498 | 6849.8463 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 12.1896 | 15.7974 | 15697.4109 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 12.1896 | 17.4266 | 17326.6366 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 12.1896 | 18.9905 | 18890.5478 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 12.1896 | 18.1302 | 18030.2394 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 12.1896 | 19.8574 | 19757.4223 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 12.1896 | 19.9982 | 19898.1564 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 12.1896 | 20.0622 | 19962.1652 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 12.1896 | 19.4843 | 19384.2661 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 27.9165 | 1.8345 | 1734.4603 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 21.1875 | 45.4235 | 45323.4613 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 21.1875 | 5.8542 | 5754.1843 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 21.1875 | 1.7564 | 1656.3688 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 21.1875 | 5.8542 | 5754.1763 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 20.5417 | 10.0731 | 9973.1312 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 10.0508 | 4.8431 | 4743.1359 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 10.0508 | 4.8431 | 4743.1359 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 4.9901 | 0.1899 | 89.8585 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 4.9901 | 6.9963 | 6896.325 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 4.9901 | 6.9499 | 6849.8504 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 12.19 | 15.7977 | 15697.7368 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 12.19 | 17.4268 | 17326.826 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 12.19 | 18.9908 | 18890.7616 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 12.19 | 18.1301 | 18030.1166 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 12.19 | 19.8573 | 19757.2875 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 12.19 | 19.9984 | 19898.3969 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 12.19 | 20.0624 | 19962.4028 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 12.19 | 19.4841 | 19384.124 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 27.8934 | 1.8371 | 1737.0689 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 21.1892 | 45.4228 | 45322.8413 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 21.1892 | 5.8556 | 5755.6441 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 21.1892 | 1.7566 | 1656.5843 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 21.1892 | 5.8556 | 5755.6358 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 20.5381 | 10.0681 | 9968.1078 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 9.6842 | 4.8116 | 4711.6416 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 9.6842 | 4.8116 | 4711.6416 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 4.9903 | 0.1899 | 89.8595 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 4.9903 | 0.1887 | 88.6928 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 4.9903 | 6.9967 | 6896.7141 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 4.9903 | 6.9503 | 6850.2853 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 12.1888 | 15.7967 | 15696.6753 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 12.1888 | 17.4261 | 17326.128 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 12.1888 | 18.99 | 18889.955 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 12.1888 | 18.1304 | 18030.3849 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 12.1888 | 19.8575 | 19757.4926 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 12.1888 | 19.9975 | 19897.4852 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 12.1888 | 20.0615 | 19961.5005 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 12.1888 | 19.4844 | 19384.4294 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 27.7926 | 1.8318 | 1731.8113 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 21.187 | 45.4228 | 45322.8142 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 21.187 | 5.8509 | 5750.9094 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 21.187 | 1.7559 | 1655.9023 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 21.187 | 5.8509 | 5750.9018 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 20.5409 | 10.0711 | 9971.1387 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 10.0465 | 4.8304 | 4730.3621 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 10.0465 | 4.8304 | 4730.3621 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 4.9899 | 0.1899 | 89.8595 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 4.9899 | 0.1887 | 88.6928 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 4.9899 | 6.9946 | 6894.5552 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 4.9899 | 6.9481 | 6848.0866 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 12.1897 | 15.7984 | 15698.3565 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 12.1897 | 17.4274 | 17327.3654 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 12.1897 | 18.9914 | 18891.4144 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 12.1897 | 18.1302 | 18030.1887 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 12.1897 | 19.8576 | 19757.566 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 12.1897 | 19.9991 | 19899.1396 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 12.1897 | 20.0631 | 19963.1441 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 12.1897 | 19.4842 | 19384.2183 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 27.8094 | 1.8317 | 1731.6641 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 21.1875 | 45.4237 | 45323.7404 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 21.1875 | 5.855 | 5754.9986 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 21.1875 | 1.7565 | 1656.4854 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 21.1875 | 5.855 | 5754.9913 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 20.5264 | 10.0782 | 9978.1899 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 10.0395 | 4.8263 | 4726.2942 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 10.0395 | 4.8263 | 4726.2942 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 4.9889 | 0.1899 | 89.8592 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 4.9889 | 0.1887 | 88.6926 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 4.9889 | 6.9979 | 6897.9282 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 4.9889 | 6.9514 | 6851.4035 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1891 | 15.7983 | 15698.3452 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1891 | 17.4274 | 17327.3776 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1891 | 18.9914 | 18891.4321 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1891 | 18.1302 | 18030.2267 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1891 | 19.8576 | 19757.6277 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1891 | 19.9992 | 19899.1596 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1891 | 20.0632 | 19963.165 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1891 | 19.4843 | 19384.2631 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 27.8281 | 1.8317 | 1731.6937 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 21.1874 | 45.4238 | 45323.792 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 21.1874 | 5.8553 | 5755.3238 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 21.1874 | 1.7565 | 1656.5325 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 21.1874 | 5.8553 | 5755.3158 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 20.5084 | 10.0768 | 9976.8001 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 10.0407 | 4.8263 | 4726.2759 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 10.0407 | 4.8263 | 4726.2759 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 4.9878 | 0.1899 | 89.8605 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 4.9878 | 0.1887 | 88.6938 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 4.9878 | 6.9985 | 6898.4794 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 4.9878 | 6.9519 | 6851.9437 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 12.1897 | 15.7974 | 15697.4285 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 12.1897 | 17.4266 | 17326.6471 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 12.1897 | 18.9906 | 18890.5608 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 12.1897 | 18.1302 | 18030.2359 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 12.1897 | 19.8574 | 19757.42 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 12.1897 | 19.9982 | 19898.171 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 12.1897 | 20.0622 | 19962.1801 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 12.1897 | 19.4843 | 19384.2619 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 27.9168 | 1.8344 | 1734.4365 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 21.1876 | 45.4234 | 45323.437 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 21.1876 | 5.8542 | 5754.2187 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 21.1876 | 1.7564 | 1656.3746 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 21.1876 | 5.8542 | 5754.211 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 20.5418 | 10.0731 | 9973.1128 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 10.0529 | 4.8326 | 4732.5614 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 10.0529 | 4.8326 | 4732.5614 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 4.9901 | 6.9963 | 6896.318 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 4.9901 | 6.9498 | 6849.8437 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 12.1897 | 15.7974 | 15697.4284 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 12.1897 | 17.4266 | 17326.6471 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 12.1897 | 18.9906 | 18890.5608 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 12.1897 | 18.1302 | 18030.2359 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 12.1897 | 19.8574 | 19757.42 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 12.1897 | 19.9982 | 19898.1709 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 12.1897 | 20.0622 | 19962.1801 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 12.1897 | 19.4843 | 19384.2619 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 27.9168 | 1.8344 | 1734.4365 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 21.1876 | 45.4234 | 45323.437 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 21.1876 | 5.8542 | 5754.2187 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 21.1876 | 1.7564 | 1656.3746 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 21.1876 | 5.8542 | 5754.211 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 20.5418 | 10.0731 | 9973.1128 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 10.0529 | 4.8326 | 4732.5614 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 10.0529 | 4.8326 | 4732.5614 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 4.9901 | 6.9963 | 6896.318 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 4.9901 | 6.9498 | 6849.8437 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 12.1897 | 15.7974 | 15697.4285 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 12.1897 | 17.4266 | 17326.6472 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 12.1897 | 18.9906 | 18890.5608 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 12.1897 | 18.1302 | 18030.2359 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 12.1897 | 19.8574 | 19757.42 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 12.1897 | 19.9982 | 19898.171 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 12.1897 | 20.0622 | 19962.1801 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 12.1897 | 19.4843 | 19384.2619 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 27.9168 | 1.8344 | 1734.4365 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 21.1876 | 45.4234 | 45323.437 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 21.1876 | 5.8542 | 5754.2187 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 21.1876 | 1.7564 | 1656.3746 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 21.1876 | 5.8542 | 5754.2107 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 20.5418 | 10.0731 | 9973.1128 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 10.0529 | 4.8326 | 4732.5615 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 10.0529 | 4.8326 | 4732.5615 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 4.9901 | 6.9963 | 6896.318 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 4.9901 | 6.9498 | 6849.8437 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 12.1905 | 15.7989 | 15698.9199 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 12.1905 | 17.4278 | 17327.7808 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 12.1905 | 18.9919 | 18891.903 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 12.1905 | 18.1301 | 18030.1231 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 12.1905 | 19.8576 | 19757.593 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 12.1905 | 19.9997 | 19899.6952 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 12.1905 | 20.0637 | 19963.6966 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 12.1905 | 19.4841 | 19384.1479 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 27.6018 | 1.8598 | 1759.7853 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 21.1876 | 45.4242 | 45324.1936 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 21.1876 | 5.8582 | 5758.2204 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 21.1876 | 1.757 | 1656.9517 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 21.1876 | 5.8582 | 5758.2114 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 20.5214 | 10.0856 | 9985.5569 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 10.0425 | 4.8752 | 4775.223 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 10.0425 | 4.8752 | 4775.223 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 4.9887 | 0.1899 | 89.8581 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 4.9887 | 0.1887 | 88.6915 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 4.9887 | 7.001 | 6901.0196 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 4.9887 | 6.9545 | 6854.464 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 12.1821 | 15.795 | 15695.02 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 12.1821 | 17.4253 | 17325.2815 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 12.1821 | 18.989 | 18889.0256 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 12.1821 | 18.1312 | 18031.2261 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 12.1821 | 19.8585 | 19758.539 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 12.1821 | 19.9964 | 19896.445 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 12.1821 | 20.0605 | 19960.4859 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 12.1821 | 19.4854 | 19385.4121 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 27.8406 | 1.8348 | 1734.8091 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 21.1889 | 45.4194 | 45319.405 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 21.1889 | 5.8311 | 5731.0912 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 21.1889 | 1.7531 | 1653.0531 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 21.1889 | 5.8311 | 5731.0836 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 20.5204 | 10.0779 | 9977.9304 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 10.0204 | 4.8281 | 4728.141 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 10.0204 | 4.8281 | 4728.141 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 4.9853 | 0.1899 | 89.8616 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 4.9853 | 0.1887 | 88.6944 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 4.9853 | 6.9838 | 6883.8192 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 4.9853 | 6.9372 | 6837.2045 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 12.325 | 15.8689 | 15768.8502 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 12.325 | 17.5034 | 17403.3758 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 12.325 | 19.0798 | 18979.8181 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 12.325 | 18.196 | 18095.9982 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 12.325 | 19.9474 | 19847.4207 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 12.325 | 20.0991 | 19999.0882 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 12.325 | 20.1622 | 20062.2039 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 12.325 | 19.5223 | 19422.2575 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 27.51 | 1.8428 | 1742.8128 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 21.0812 | 45.4936 | 45393.6169 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 21.0812 | 6.0378 | 5937.778 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 21.0812 | 1.7836 | 1683.6233 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 21.0812 | 6.0378 | 5937.7688 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 20.4571 | 10.1108 | 10010.7819 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 9.8975 | 4.8935 | 4793.4686 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 9.8975 | 4.8935 | 4793.4686 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 4.9782 | 0.1899 | 89.8571 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 4.9782 | 0.1887 | 88.6934 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 4.9782 | 7.1056 | 7005.6302 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 4.9782 | 7.0589 | 6958.8659 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 12.1858 | 15.7959 | 15695.877 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 12.1858 | 17.4258 | 17325.8094 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 12.1858 | 18.9896 | 18889.6306 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 12.1858 | 18.1309 | 18030.9463 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 12.1858 | 19.8583 | 19758.2683 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 12.1858 | 19.9971 | 19897.1275 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 12.1858 | 20.0612 | 19961.1583 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 12.1858 | 19.4851 | 19385.09 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 27.8549 | 1.8317 | 1731.6855 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 21.1461 | 45.4568 | 45356.828 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 21.1461 | 5.8322 | 5732.1886 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 21.1461 | 1.7531 | 1653.0919 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 21.1461 | 5.8322 | 5732.181 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 20.3065 | 10.2435 | 10143.4662 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 9.996 | 4.8372 | 4737.2333 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 9.996 | 4.8372 | 4737.2333 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 4.9728 | 0.1899 | 89.8703 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 4.9728 | 0.1887 | 88.7033 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 4.9728 | 7.0158 | 6915.8135 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 4.9728 | 6.9684 | 6868.3903 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 12.1726 | 15.7844 | 15684.4391 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 12.1726 | 17.4169 | 17316.9366 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 12.1726 | 18.9802 | 18880.2341 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 12.1726 | 18.1329 | 18032.9423 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 12.1726 | 19.8589 | 19758.91 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 12.1726 | 19.9883 | 19888.3066 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 12.1726 | 20.0506 | 19950.6061 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 12.1726 | 19.4873 | 19387.3187 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 27.8238 | 1.8344 | 1734.4116 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 21.1821 | 45.414 | 45314.0172 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 21.1821 | 5.8029 | 5702.9012 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 21.1821 | 1.7491 | 1649.0583 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 21.1821 | 5.8029 | 5702.8938 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 20.5333 | 10.0697 | 9969.7053 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 10.0456 | 4.8194 | 4719.3969 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 10.0456 | 4.8194 | 4719.3969 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 4.9857 | 0.1899 | 89.864 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 4.9857 | 0.1887 | 88.6966 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 4.9857 | 6.9767 | 6876.7301 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 4.9857 | 6.9302 | 6830.2213 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 12.1892 | 15.7971 | 15697.1009 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 12.1892 | 17.4264 | 17326.4409 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 12.1892 | 18.9903 | 18890.3237 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 12.1892 | 18.1303 | 18030.3325 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 12.1892 | 19.8575 | 19757.5075 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 12.1892 | 19.9979 | 19897.9055 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 12.1892 | 20.0619 | 19961.9162 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 12.1892 | 19.4844 | 19384.3734 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 8.3225 | 2.9949 | 2894.9447 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 21.1897 | 45.4221 | 45322.0872 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 21.1897 | 5.8434 | 5743.4464 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 21.1897 | 1.7548 | 1654.8165 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 21.1897 | 5.8434 | 5743.4382 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 20.5317 | 10.0831 | 9983.1301 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 10.0499 | 4.8165 | 4716.525 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 10.0499 | 4.8165 | 4716.525 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 4.9895 | 0.1899 | 89.8582 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 4.9895 | 0.1887 | 88.6914 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 4.9895 | 6.9946 | 6894.6356 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 4.9895 | 6.9481 | 6848.0955 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.121 | 15.745 | 15645.034 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.121 | 17.3715 | 17271.5482 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.121 | 18.9409 | 18840.8516 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.121 | 18.1416 | 18041.6376 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.121 | 19.8642 | 19764.1665 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.121 | 19.9935 | 19893.5454 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.121 | 20.0469 | 19946.8725 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.121 | 19.4972 | 19397.1657 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 27.7289 | 1.8322 | 1732.1678 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 21.1858 | 45.3945 | 45294.5499 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 21.1858 | 5.6548 | 5554.8127 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 21.1858 | 1.7289 | 1628.8739 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 21.1858 | 5.6548 | 5554.8053 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.5347 | 10.0675 | 9967.4601 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 9.986 | 4.7953 | 4695.2702 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 9.986 | 4.7953 | 4695.2702 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 4.9795 | 0.1899 | 89.8691 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 4.9795 | 0.1887 | 88.7001 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 4.9795 | 6.9267 | 6826.6787 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 4.9795 | 6.88 | 6779.984 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 12.2475 | 15.8292 | 15729.2063 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 12.2475 | 17.4576 | 17357.6096 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 12.2475 | 19.0265 | 18926.5475 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 12.2475 | 18.1326 | 18032.5641 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 12.2475 | 19.8864 | 19786.3796 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 12.2475 | 20.0388 | 19938.8448 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 12.2475 | 20.1025 | 20002.4885 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 12.2475 | 19.474 | 19373.982 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 27.8673 | 1.8358 | 1735.7752 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 21.1668 | 45.4427 | 45342.7183 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 21.1668 | 5.9257 | 5825.7363 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 21.1668 | 1.7668 | 1666.8008 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 21.1668 | 5.9257 | 5825.7284 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 20.5335 | 10.0783 | 9978.2778 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 10.0322 | 4.8468 | 4746.7846 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 10.0322 | 4.8468 | 4746.7846 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 4.9916 | 0.1899 | 89.8553 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 4.9916 | 0.1887 | 88.6899 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 4.9916 | 7.0378 | 6937.7826 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 4.9916 | 6.9913 | 6891.34 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 12.1912 | 15.7986 | 15698.6117 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 12.1912 | 17.4275 | 17327.4984 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 12.1912 | 18.9916 | 18891.5628 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 12.1912 | 18.1301 | 18030.0562 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 12.1912 | 19.8574 | 19757.4067 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 12.1912 | 19.9993 | 19899.3084 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 12.1912 | 20.0633 | 19963.3067 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 12.1912 | 19.4841 | 19384.0645 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 20.964 | 2.0718 | 1971.7993 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 21.1897 | 45.4226 | 45322.6226 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 21.1897 | 5.8316 | 5731.6049 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 21.1897 | 1.7531 | 1653.1022 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 21.1897 | 5.8316 | 5731.5967 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 20.5331 | 10.0885 | 9988.4912 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 10.0463 | 4.798 | 4697.9865 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 10.0463 | 4.798 | 4697.9865 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 4.9891 | 0.1899 | 89.8581 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 4.9891 | 0.1887 | 88.6912 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 4.9891 | 6.9934 | 6893.3565 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 4.9891 | 6.9467 | 6846.7443 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 12.18 | 15.79 | 15690.0264 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 12.18 | 17.4216 | 17321.6403 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 12.18 | 18.9847 | 18884.7395 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 12.18 | 18.1319 | 18031.8672 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 12.18 | 19.8584 | 19758.4211 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 12.18 | 19.9916 | 19891.5892 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 12.18 | 20.0557 | 19955.6592 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 12.18 | 19.4861 | 19386.1107 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 27.9089 | 1.8492 | 1749.1678 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 21.1865 | 45.4211 | 45321.138 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 21.1865 | 5.8443 | 5744.3473 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 21.1865 | 1.755 | 1654.9614 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 21.1865 | 5.8443 | 5744.3397 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 20.5407 | 10.0713 | 9971.3277 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 10.0514 | 4.8329 | 4732.9278 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 10.0514 | 4.8329 | 4732.9278 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 4.9891 | 0.1899 | 89.8599 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 4.9891 | 0.1887 | 88.693 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 4.9891 | 6.9898 | 6889.8224 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 4.9891 | 6.9433 | 6843.3453 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 12.1854 | 15.7942 | 15694.1738 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 12.1854 | 17.4244 | 17324.445 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 12.1854 | 18.988 | 18887.9961 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 12.1854 | 18.131 | 18030.9566 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 12.1854 | 19.8579 | 19757.8612 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 12.1854 | 19.9953 | 19895.2694 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 12.1854 | 20.0593 | 19959.3077 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 12.1854 | 19.4851 | 19385.0784 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 27.9137 | 1.8387 | 1738.6667 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 21.1876 | 45.4223 | 45322.3278 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 21.1876 | 5.8497 | 5749.6605 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 21.1876 | 1.7557 | 1655.725 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 21.1876 | 5.8497 | 5749.6522 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 20.5416 | 10.0722 | 9972.205 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 10.0526 | 4.8323 | 4732.2713 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 10.0526 | 4.8323 | 4732.2713 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 4.9899 | 0.1899 | 89.8592 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 4.9899 | 0.1887 | 88.6924 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 4.9899 | 6.9933 | 6893.2874 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 4.9899 | 6.9468 | 6846.813 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 12.18 | 15.7901 | 15690.0546 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 12.18 | 17.4217 | 17321.6602 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 12.18 | 18.9848 | 18884.7628 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 12.18 | 18.1319 | 18031.8624 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 12.18 | 19.8584 | 19758.4199 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 12.18 | 19.9916 | 19891.6158 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 12.18 | 20.0557 | 19955.6857 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 12.18 | 19.4861 | 19386.1054 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 27.9087 | 1.8533 | 1753.3305 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 21.1862 | 45.4213 | 45321.3186 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 21.1862 | 5.8449 | 5744.904 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 21.1862 | 1.755 | 1655.0412 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 21.1862 | 5.8449 | 5744.8958 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 20.5404 | 10.0714 | 9971.4257 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 10.0511 | 4.8337 | 4733.666 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 10.0511 | 4.8337 | 4733.666 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 4.9891 | 0.1899 | 89.8599 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 4.9891 | 0.1887 | 88.693 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 4.9891 | 6.99 | 6890.0233 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 4.9891 | 6.9435 | 6843.5459 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 12.1844 | 15.7934 | 15693.3868 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 12.1844 | 17.4239 | 17323.9124 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 12.1844 | 18.9874 | 18887.3772 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 12.1844 | 18.1311 | 18031.1318 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 12.1844 | 19.858 | 19757.9706 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 12.1844 | 19.9946 | 19894.5691 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 12.1844 | 20.0586 | 19958.6131 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 12.1844 | 19.4853 | 19385.2768 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 27.9132 | 1.842 | 1741.9512 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 21.1876 | 45.4221 | 45322.1496 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 21.1876 | 5.8488 | 5748.8377 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 21.1876 | 1.7556 | 1655.6083 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 21.1876 | 5.8488 | 5748.8301 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 20.5416 | 10.072 | 9972.0345 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 10.0525 | 4.8326 | 4732.6049 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 10.0525 | 4.8326 | 4732.6049 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 4.9899 | 0.1899 | 89.8593 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 4.9899 | 0.1887 | 88.6925 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 4.9899 | 6.9926 | 6892.6497 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 4.9899 | 6.9462 | 6846.1738 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1782 | 15.7934 | 15693.3511 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1782 | 17.424 | 17323.9691 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1782 | 18.9875 | 18887.4588 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1782 | 18.1313 | 18031.2862 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1782 | 19.8582 | 19758.2114 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1782 | 19.9947 | 19894.6627 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1782 | 20.0587 | 19958.7095 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 12.1782 | 19.4855 | 19385.4563 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 27.885 | 1.8332 | 1733.1515 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 21.1813 | 45.4215 | 45321.492 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 21.1813 | 5.8464 | 5746.4052 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 21.1813 | 1.7553 | 1655.2627 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 21.1813 | 5.8464 | 5746.3976 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 20.4192 | 10.0237 | 9923.6941 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 10.047 | 4.8307 | 4730.7374 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 10.047 | 4.8307 | 4730.7374 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 4.9787 | 0.1899 | 89.8742 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 4.9787 | 0.1887 | 88.7073 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 4.9787 | 6.9976 | 6897.5538 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 4.9787 | 6.9511 | 6851.0834 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 12.1866 | 15.7972 | 15697.2072 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 12.1866 | 17.4266 | 17326.6353 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 12.1866 | 18.9906 | 18890.5716 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 12.1866 | 18.1305 | 18030.5304 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 12.1866 | 19.8579 | 19757.8655 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 12.1866 | 19.9982 | 19898.1867 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 12.1866 | 20.0622 | 19962.204 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 12.1866 | 19.4846 | 19384.6092 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 27.9151 | 1.8341 | 1734.074 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 21.1844 | 45.4238 | 45323.7538 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 21.1844 | 5.8551 | 5755.0893 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 21.1844 | 1.7565 | 1656.5079 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 21.1844 | 5.8551 | 5755.0803 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 20.5437 | 10.0664 | 9966.3583 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 10.0528 | 4.8317 | 4731.6614 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 10.0528 | 4.8317 | 4731.6614 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 4.9861 | 0.1899 | 89.8659 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 4.9861 | 0.1887 | 88.6992 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 4.9861 | 7.0009 | 6900.946 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 4.9861 | 6.9544 | 6854.3986 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 12.1874 | 15.7981 | 15698.1415 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 12.1874 | 17.4272 | 17327.1918 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 12.1874 | 18.9912 | 18891.205 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 12.1874 | 18.1302 | 18030.1932 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 12.1874 | 19.8575 | 19757.5125 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 12.1874 | 19.9989 | 19898.8999 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 12.1874 | 20.0629 | 19962.9068 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 12.1874 | 19.4842 | 19384.2187 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 27.9158 | 1.8343 | 1734.2909 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 21.1869 | 45.4234 | 45323.3617 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 21.1869 | 5.8549 | 5754.8726 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 21.1869 | 1.7565 | 1656.4691 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 21.1869 | 5.8549 | 5754.8645 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 20.5393 | 10.1085 | 10008.4732 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 10.052 | 4.8333 | 4733.2852 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 10.052 | 4.8333 | 4733.2852 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 4.9872 | 0.1899 | 89.8617 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 4.9872 | 0.1887 | 88.6951 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 4.9872 | 6.9998 | 6899.8497 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 4.9872 | 6.9534 | 6853.4031 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 12.1793 | 15.7897 | 15689.6911 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 12.1793 | 17.4213 | 17321.3497 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 12.1793 | 18.9844 | 18884.3866 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 12.1793 | 18.1318 | 18031.8309 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 12.1793 | 19.8583 | 19758.2717 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 12.1793 | 19.9912 | 19891.1878 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 12.1793 | 20.0553 | 19955.2582 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 12.1793 | 19.4861 | 19386.0617 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 27.916 | 1.8344 | 1734.407 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 21.1863 | 45.4209 | 45320.8704 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 21.1863 | 5.8452 | 5745.1608 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 21.1863 | 1.7551 | 1655.081 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 21.1863 | 5.8452 | 5745.1535 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 20.5373 | 10.0604 | 9960.3752 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 10.0525 | 4.8319 | 4731.9031 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 10.0525 | 4.8319 | 4731.9031 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 4.989 | 0.1899 | 89.861 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 4.989 | 0.1887 | 88.6942 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 4.989 | 6.9911 | 6891.0755 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 4.989 | 6.9447 | 6844.6717 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 12.1827 | 15.7974 | 15697.3572 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 12.1827 | 17.4264 | 17326.4341 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 12.1827 | 18.9903 | 18890.2736 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 12.1827 | 18.13 | 18029.9813 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 12.1827 | 19.8569 | 19756.9266 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 12.1827 | 19.9978 | 19897.8346 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 12.1827 | 20.0618 | 19961.8357 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 12.1827 | 19.4839 | 19383.9498 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 27.9145 | 1.8337 | 1733.7287 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 21.1793 | 45.4221 | 45322.0514 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 21.1793 | 5.8609 | 5760.8801 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 21.1793 | 1.7574 | 1657.3612 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 21.1793 | 5.8609 | 5760.8728 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 20.5043 | 10.111 | 10011.0292 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 10.0529 | 4.8311 | 4731.06 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 10.0529 | 4.8311 | 4731.06 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 4.98 | 0.1899 | 89.8767 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 4.98 | 0.1887 | 88.71 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 4.98 | 6.9973 | 6897.2716 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 4.98 | 6.9511 | 6851.1078 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 12.1828 | 15.7975 | 15697.5319 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 12.1828 | 17.4265 | 17326.5404 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 12.1828 | 18.9904 | 18890.3934 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 12.1828 | 18.1299 | 18029.9267 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 12.1828 | 19.8569 | 19756.8703 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 12.1828 | 19.998 | 19897.9668 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 12.1828 | 20.062 | 19961.9672 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 12.1828 | 19.4839 | 19383.8868 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 27.9148 | 1.8337 | 1733.683 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 21.1791 | 45.422 | 45322.0258 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 21.1791 | 5.8617 | 5761.6989 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 21.1791 | 1.7575 | 1657.4847 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 21.1791 | 5.8617 | 5761.6899 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 20.5023 | 10.1137 | 10013.6637 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 10.053 | 4.831 | 4730.9832 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 10.053 | 4.831 | 4730.9832 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 4.9795 | 0.1899 | 89.8779 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 4.9795 | 0.1887 | 88.7112 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 4.9795 | 6.9974 | 6897.4239 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 4.9795 | 6.9513 | 6851.2823 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 12.1898 | 15.7974 | 15697.4168 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 12.1898 | 17.4266 | 17326.637 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 12.1898 | 18.9905 | 18890.5467 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 12.1898 | 18.1302 | 18030.234 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 12.1898 | 19.8574 | 19757.4124 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 12.1898 | 19.9982 | 19898.1562 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 12.1898 | 20.0622 | 19962.1642 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 12.1898 | 19.4843 | 19384.2596 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 27.9167 | 1.8344 | 1734.4099 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 21.1877 | 45.4233 | 45323.3387 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 21.1877 | 5.8539 | 5753.8818 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 21.1877 | 1.7563 | 1656.3272 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 21.1877 | 5.8539 | 5753.8739 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 20.542 | 10.0726 | 9972.6139 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 10.0529 | 4.8325 | 4732.5079 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 10.0529 | 4.8325 | 4732.5079 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 4.9901 | 6.9959 | 6895.9215 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 4.9901 | 6.9494 | 6849.4475 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 12.1898 | 15.7974 | 15697.4165 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 12.1898 | 17.4266 | 17326.6368 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 12.1898 | 18.9905 | 18890.5467 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 12.1898 | 18.1302 | 18030.234 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 12.1898 | 19.8574 | 19757.4124 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 12.1898 | 19.9982 | 19898.1559 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 12.1898 | 20.0622 | 19962.1636 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 12.1898 | 19.4843 | 19384.2596 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 27.9167 | 1.8344 | 1734.4096 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 21.1877 | 45.4233 | 45323.3374 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 21.1877 | 5.8539 | 5753.8787 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 21.1877 | 1.7563 | 1656.3267 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 21.1877 | 5.8539 | 5753.8705 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 20.542 | 10.0726 | 9972.6077 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 10.0529 | 4.8325 | 4732.5072 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 10.0529 | 4.8325 | 4732.5072 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 4.9901 | 6.9959 | 6895.9178 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 4.9901 | 6.9494 | 6849.4444 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 12.1139 | 15.7726 | 15672.6304 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 12.1139 | 17.4038 | 17303.7812 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 12.1139 | 18.9706 | 18870.6417 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 12.1139 | 18.1385 | 18038.5447 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 12.1139 | 19.8656 | 19765.5584 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 12.1139 | 19.9951 | 19895.1064 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 12.1139 | 20.0476 | 19947.6271 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 12.1139 | 19.4938 | 19393.8271 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 27.9076 | 1.8338 | 1733.8331 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 21.1366 | 45.4153 | 45315.3136 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 21.1366 | 5.7747 | 5674.6624 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 21.1366 | 1.7451 | 1645.124 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 21.1366 | 5.7747 | 5674.6543 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 20.2102 | 10.1554 | 10055.4205 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 10.0494 | 4.8339 | 4733.8626 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 10.0494 | 4.8339 | 4733.8626 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 4.9044 | 0.19 | 89.9507 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 4.9044 | 0.1888 | 88.782 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 4.9044 | 7.0067 | 6906.6519 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 4.9044 | 6.9588 | 6858.7946 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 12.1859 | 15.7946 | 15694.6354 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 12.1859 | 17.4248 | 17324.7574 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 12.1859 | 18.9884 | 18888.3624 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 12.1859 | 18.1308 | 18030.8487 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 12.1859 | 19.8578 | 19757.7939 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 12.1859 | 19.9957 | 19895.6856 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 12.1859 | 20.0597 | 19959.7178 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 12.1859 | 19.485 | 19384.9564 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 27.9144 | 1.8337 | 1733.7112 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 21.1878 | 45.419 | 45319.0136 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 21.1878 | 5.8281 | 5728.0513 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 21.1878 | 1.7526 | 1652.6194 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 21.1878 | 5.828 | 5728.043 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 20.5405 | 10.0705 | 9970.5119 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 10.0528 | 4.8311 | 4731.1061 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 10.0528 | 4.8311 | 4731.1061 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 4.9868 | 0.1899 | 89.8618 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 4.9868 | 0.1887 | 88.6943 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 4.9868 | 6.9732 | 6873.1731 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 4.9868 | 6.9266 | 6826.6194 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 12.1897 | 15.7974 | 15697.4252 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 12.1897 | 17.4266 | 17326.6457 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 12.1897 | 18.9906 | 18890.5578 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 12.1897 | 18.1302 | 18030.236 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 12.1897 | 19.8574 | 19757.4196 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 12.1897 | 19.9982 | 19898.169 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 12.1897 | 20.0622 | 19962.1767 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 12.1897 | 19.4843 | 19384.2622 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 27.9168 | 1.8344 | 1734.4356 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 21.1876 | 45.4234 | 45323.4274 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 21.1876 | 5.8542 | 5754.1884 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 21.1876 | 1.7564 | 1656.3703 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 21.1876 | 5.8542 | 5754.1811 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 20.5418 | 10.0731 | 9973.0993 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 10.0529 | 4.8326 | 4732.5594 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 10.0529 | 4.8326 | 4732.5594 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 4.9901 | 6.9963 | 6896.2864 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 4.9901 | 6.9498 | 6849.8107 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 12.2889 | 15.8481 | 15748.0966 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 12.2889 | 17.4797 | 17379.6779 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 12.2889 | 19.0524 | 18952.4204 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 12.2889 | 18.1659 | 18065.9283 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 12.2889 | 19.9159 | 19815.9065 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 12.2889 | 20.0681 | 19968.1271 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 12.2889 | 20.1316 | 20031.5769 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 12.2889 | 19.4878 | 19387.8289 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 27.9243 | 1.8358 | 1735.7687 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 21.1943 | 45.4577 | 45357.7089 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 21.1943 | 5.9618 | 5861.8344 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 21.1943 | 1.7722 | 1672.203 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 21.1943 | 5.9618 | 5861.8254 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 20.5663 | 10.1183 | 10018.291 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 10.0544 | 4.8456 | 4745.5693 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 10.0544 | 4.8456 | 4745.5693 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 5.0016 | 0.1899 | 89.9078 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 5.0016 | 0.1887 | 88.7418 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 5.0016 | 7.0596 | 6959.6067 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 5.0016 | 7.0125 | 6912.4743 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 12.1609 | 15.8026 | 15702.6352 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 12.1609 | 17.4314 | 17331.3535 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 12.1609 | 18.9963 | 18896.2576 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 12.1609 | 18.1312 | 18031.2149 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 12.1609 | 19.8603 | 19760.3025 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 12.1609 | 20.0046 | 19904.6428 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 12.1609 | 20.0687 | 19968.6634 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 12.1609 | 19.4855 | 19385.4835 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 27.9144 | 1.8344 | 1734.3561 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 21.1685 | 45.4198 | 45319.8278 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 21.1685 | 5.8509 | 5750.9057 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 21.1685 | 1.7559 | 1655.9231 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 21.1685 | 5.8509 | 5750.8977 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 20.3826 | 10.2442 | 10144.1674 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 10.0497 | 4.8316 | 4731.6081 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 10.0497 | 4.8316 | 4731.6081 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 4.9454 | 0.1899 | 89.908 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 4.9454 | 0.1887 | 88.7404 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 4.9454 | 6.9928 | 6892.8193 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 4.9454 | 6.9462 | 6846.1535 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 12.2212 | 15.9046 | 15804.6152 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 12.2212 | 17.5471 | 17447.0736 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 12.2212 | 19.1324 | 19032.4388 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 12.2212 | 18.2399 | 18139.9298 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 12.2212 | 20.0067 | 19906.6862 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 12.2212 | 20.1589 | 20058.8693 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 12.2212 | 20.222 | 20122.02 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 12.2212 | 19.5734 | 19473.3692 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 27.8892 | 1.8272 | 1727.2035 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 18.8691 | 45.5099 | 45409.9349 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 18.8691 | 4.5736 | 4473.5945 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 18.8691 | 1.6163 | 1516.326 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 18.8691 | 4.5736 | 4473.5901 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 20.1881 | 10.2616 | 10161.624 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 10.0514 | 4.851 | 4751.0007 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 10.0514 | 4.851 | 4751.0007 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.868 | 0.1953 | 95.3468 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.868 | 0.1941 | 94.1122 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.868 | 8.2915 | 8191.5014 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.868 | 8.2012 | 8101.2492 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 12.1897 | 15.7974 | 15697.4285 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 12.1897 | 17.4266 | 17326.6472 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 12.1897 | 18.9906 | 18890.5609 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 12.1897 | 18.1302 | 18030.2359 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 12.1897 | 19.8574 | 19757.42 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 12.1897 | 19.9982 | 19898.171 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 12.1897 | 20.0622 | 19962.1801 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 12.1897 | 19.4843 | 19384.2619 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 27.9168 | 1.8344 | 1734.4365 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 21.1876 | 45.4234 | 45323.437 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 21.1876 | 5.8542 | 5754.2187 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 21.1876 | 1.7564 | 1656.3746 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 21.1876 | 5.8542 | 5754.2111 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 20.5418 | 10.0731 | 9973.1128 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 10.0529 | 4.8326 | 4732.5614 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 10.0529 | 4.8326 | 4732.5614 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 4.9901 | 6.9963 | 6896.3181 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 4.9901 | 6.9498 | 6849.8438 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 12.1897 | 15.7974 | 15697.4285 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 12.1897 | 17.4266 | 17326.6471 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 12.1897 | 18.9906 | 18890.5608 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 12.1897 | 18.1302 | 18030.2359 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 12.1897 | 19.8574 | 19757.42 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 12.1897 | 19.9982 | 19898.171 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 12.1897 | 20.0622 | 19962.1801 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 12.1897 | 19.4843 | 19384.2619 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 27.9168 | 1.8344 | 1734.4365 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 21.1876 | 45.4234 | 45323.437 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 21.1876 | 5.8542 | 5754.2187 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 21.1876 | 1.7564 | 1656.3746 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 21.1876 | 5.8542 | 5754.211 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 20.5418 | 10.0731 | 9973.1128 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 10.0529 | 4.8326 | 4732.5614 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 10.0529 | 4.8326 | 4732.5614 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 4.9901 | 6.9963 | 6896.3181 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 4.9901 | 6.9498 | 6849.8438 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 12.1885 | 15.7968 | 15696.8444 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 12.1885 | 17.4263 | 17326.2877 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 12.1885 | 18.9901 | 18890.1495 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 12.1885 | 18.1304 | 18030.425 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 12.1885 | 19.8576 | 19757.6031 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 12.1885 | 19.9977 | 19897.7069 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 12.1885 | 20.0617 | 19961.7223 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 12.1885 | 19.4845 | 19384.4795 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 27.9105 | 1.8346 | 1734.612 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 21.1862 | 45.4235 | 45323.4782 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 21.1862 | 5.8516 | 5751.6288 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 21.1862 | 1.756 | 1655.9991 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 21.1862 | 5.8516 | 5751.6201 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 20.3486 | 10.1394 | 10039.4314 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 10.0507 | 4.8333 | 4733.3495 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 10.0507 | 4.8333 | 4733.3495 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 4.9893 | 0.1899 | 89.8589 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 4.9893 | 0.1887 | 88.6921 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 4.9893 | 6.9957 | 6895.7487 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 4.9893 | 6.9492 | 6849.245 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 12.1897 | 15.7974 | 15697.4202 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 12.1897 | 17.4266 | 17326.6423 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 12.1897 | 18.9906 | 18890.5556 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 12.1897 | 18.1302 | 18030.2388 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 12.1897 | 19.8574 | 19757.4222 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 12.1897 | 19.9982 | 19898.165 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 12.1897 | 20.0622 | 19962.1744 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 12.1897 | 19.4843 | 19384.2662 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 27.9168 | 1.8344 | 1734.4338 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 21.1877 | 45.4234 | 45323.4498 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 21.1877 | 5.8542 | 5754.1957 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 21.1877 | 1.7564 | 1656.3721 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 21.1877 | 5.8542 | 5754.1884 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 20.5421 | 10.0729 | 9972.8514 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 10.0529 | 4.8326 | 4732.5556 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 10.0529 | 4.8326 | 4732.5556 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 4.9901 | 0.1899 | 89.8588 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 4.9901 | 0.1887 | 88.6921 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 4.9901 | 6.9963 | 6896.2733 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 4.9901 | 6.9498 | 6849.7987 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 12.1897 | 15.7974 | 15697.4211 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 12.1897 | 17.4266 | 17326.6431 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 12.1897 | 18.9906 | 18890.5565 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 12.1897 | 18.1302 | 18030.239 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 12.1897 | 19.8574 | 19757.4226 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 12.1897 | 19.9982 | 19898.1661 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 12.1897 | 20.0622 | 19962.1754 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 12.1897 | 19.4843 | 19384.2652 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 27.9168 | 1.8344 | 1734.4342 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 21.1877 | 45.4234 | 45323.4477 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 21.1877 | 5.8542 | 5754.1991 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 21.1877 | 1.7564 | 1656.3724 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 21.1877 | 5.8542 | 5754.1908 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 20.5421 | 10.0729 | 9972.9032 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 10.0529 | 4.8326 | 4732.5569 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 10.0529 | 4.8326 | 4732.5569 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 4.9901 | 0.1899 | 89.8588 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 4.9901 | 0.1887 | 88.6921 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 4.9901 | 6.9963 | 6896.2781 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 4.9901 | 6.9498 | 6849.8028 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 12.1886 | 15.7966 | 15696.6391 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 12.1886 | 17.4261 | 17326.1226 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 12.1886 | 18.99 | 18889.9515 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 12.1886 | 18.1304 | 18030.4252 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 12.1886 | 19.8576 | 19757.553 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 12.1886 | 19.9975 | 19897.484 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 12.1886 | 20.0615 | 19961.4988 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 12.1886 | 19.4845 | 19384.4776 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 25.7847 | 1.8762 | 1776.198 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 21.1789 | 45.4258 | 45325.8105 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 21.1789 | 5.8482 | 5748.1705 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 21.1789 | 1.7555 | 1655.4975 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 21.1789 | 5.8482 | 5748.1622 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 20.5209 | 10.0894 | 9989.4128 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 10.034 | 4.8383 | 4738.2921 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 10.034 | 4.8383 | 4738.2921 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 4.9875 | 0.1899 | 89.8609 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 4.9875 | 0.1887 | 88.6941 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 4.9875 | 6.9969 | 6896.9242 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 4.9875 | 6.9504 | 6850.3562 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 12.1898 | 15.7974 | 15697.4311 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 12.1898 | 17.4266 | 17326.6493 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 12.1898 | 18.9906 | 18890.5618 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 12.1898 | 18.1302 | 18030.2345 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 12.1898 | 19.8574 | 19757.4182 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 12.1898 | 19.9982 | 19898.1732 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 12.1898 | 20.0622 | 19962.1825 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 12.1898 | 19.4843 | 19384.2614 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 27.9164 | 1.8339 | 1733.9001 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 21.1877 | 45.4233 | 45323.3462 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 21.1877 | 5.8539 | 5753.9047 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 21.1877 | 1.7563 | 1656.3294 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 21.1877 | 5.8539 | 5753.8971 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 20.5418 | 10.0731 | 9973.0512 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 10.0529 | 4.8325 | 4732.4522 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 10.0529 | 4.8325 | 4732.4522 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 4.9901 | 0.1899 | 89.8585 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 4.9901 | 6.9962 | 6896.2284 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 4.9901 | 6.9498 | 6849.7535 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 12.1898 | 15.7974 | 15697.4317 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 12.1898 | 17.4266 | 17326.6497 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 12.1898 | 18.9906 | 18890.5632 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 12.1898 | 18.1302 | 18030.2345 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 12.1898 | 19.8574 | 19757.4179 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 12.1898 | 19.9982 | 19898.1739 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 12.1898 | 20.0622 | 19962.1831 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 12.1898 | 19.4843 | 19384.2611 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 27.9163 | 1.8339 | 1733.8844 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 21.1877 | 45.4233 | 45323.3435 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 21.1877 | 5.8539 | 5753.8962 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 21.1877 | 1.7563 | 1656.3282 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 21.1877 | 5.8539 | 5753.8882 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 20.5418 | 10.073 | 9973.0492 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 10.0529 | 4.8324 | 4732.449 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 10.0529 | 4.8324 | 4732.449 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 4.9901 | 6.9962 | 6896.2269 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 4.9901 | 6.9498 | 6849.7528 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 12.1914 | 15.7995 | 15699.4729 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 12.1914 | 17.4283 | 17328.2859 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 12.1914 | 18.9925 | 18892.524 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 12.1914 | 18.1302 | 18030.2201 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 12.1914 | 19.8579 | 19757.9094 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 12.1914 | 20.0004 | 19900.4052 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 12.1914 | 20.0644 | 19964.4051 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 12.1914 | 19.4843 | 19384.2731 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 27.9126 | 1.8349 | 1734.893 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 21.1814 | 45.4346 | 45334.6399 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 21.1814 | 5.8595 | 5759.5103 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 21.1814 | 1.7571 | 1657.0786 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 21.1814 | 5.8595 | 5759.5022 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 20.3584 | 9.871 | 9770.9519 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 10.0519 | 4.8331 | 4733.0741 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 10.0519 | 4.8331 | 4733.0741 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 4.988 | 0.1899 | 89.8553 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 4.988 | 0.1887 | 88.6887 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 4.988 | 7.0083 | 6908.2923 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 4.988 | 6.9614 | 6861.4339 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 12.1899 | 15.7976 | 15697.6415 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 12.1899 | 17.4268 | 17326.7811 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 12.1899 | 18.9907 | 18890.7148 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 12.1899 | 18.1302 | 18030.1708 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 12.1899 | 19.8574 | 19757.3589 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 12.1899 | 19.9983 | 19898.3442 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 12.1899 | 20.0624 | 19962.3512 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 12.1899 | 19.4842 | 19384.1878 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 27.9166 | 1.8346 | 1734.5952 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 21.1868 | 45.4236 | 45323.5544 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 21.1868 | 5.8565 | 5756.5347 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 21.1868 | 1.7567 | 1656.7115 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 21.1868 | 5.8565 | 5756.5266 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 20.548 | 10.0881 | 9988.1365 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 10.0527 | 4.8327 | 4732.726 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 10.0527 | 4.8327 | 4732.726 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 4.99 | 0.1899 | 89.8588 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 4.99 | 0.1887 | 88.6922 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 4.99 | 6.9973 | 6897.2892 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 4.99 | 6.9508 | 6850.8334 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 12.1891 | 15.7972 | 15697.2437 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 12.1891 | 17.4266 | 17326.5793 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 12.1891 | 18.9905 | 18890.4945 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 12.1891 | 18.1304 | 18030.3713 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 12.1891 | 19.8576 | 19757.6116 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 12.1891 | 19.9981 | 19898.0994 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 12.1891 | 20.0621 | 19962.1111 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 12.1891 | 19.4844 | 19384.4215 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 27.9166 | 1.8346 | 1734.6427 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 21.1868 | 45.4244 | 45324.4174 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 21.1868 | 5.8545 | 5754.4668 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 21.1868 | 1.7564 | 1656.404 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 21.1868 | 5.8545 | 5754.4582 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 20.5514 | 10.0636 | 9963.5666 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 10.0527 | 4.833 | 4733.0391 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 10.0527 | 4.833 | 4733.0391 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 4.9895 | 0.1899 | 89.8582 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 4.9895 | 0.1887 | 88.6915 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 4.9895 | 6.9983 | 6898.2937 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 4.9895 | 6.9518 | 6851.7632 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 12.1645 | 15.7781 | 15678.124 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 12.1645 | 17.4097 | 17309.6579 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 12.1645 | 18.9753 | 18875.2637 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 12.1645 | 18.1344 | 18034.3608 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 12.1645 | 19.8598 | 19759.7914 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 12.1645 | 19.9892 | 19889.1848 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 12.1645 | 20.045 | 19945.0391 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 12.1645 | 19.4889 | 19388.9266 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 27.9146 | 1.8339 | 1733.9029 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 21.1869 | 45.4164 | 45316.3836 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 21.1869 | 5.8223 | 5722.3034 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 21.1869 | 1.7518 | 1651.8172 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 21.1869 | 5.8223 | 5722.2959 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 20.5272 | 9.9671 | 9867.1373 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 10.0525 | 4.8301 | 4730.0987 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 10.0525 | 4.8301 | 4730.0987 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 4.9876 | 0.1899 | 89.863 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 4.9876 | 0.1887 | 88.6957 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 4.9876 | 6.9769 | 6876.9416 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 4.9876 | 6.9305 | 6830.5259 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 12.1892 | 15.7973 | 15697.2742 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 12.1892 | 17.4266 | 17326.591 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 12.1892 | 18.9905 | 18890.5064 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 12.1892 | 18.1303 | 18030.3487 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 12.1892 | 19.8576 | 19757.581 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 12.1892 | 19.9981 | 19898.1123 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 12.1892 | 20.0621 | 19962.1233 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 12.1892 | 19.4844 | 19384.3954 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 27.9167 | 1.8346 | 1734.6348 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 21.1868 | 45.4243 | 45324.3144 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 21.1868 | 5.8547 | 5754.7399 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 21.1868 | 1.7564 | 1656.4441 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 21.1868 | 5.8547 | 5754.7316 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 20.5504 | 10.0679 | 9967.946 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 10.0527 | 4.833 | 4733.0023 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 10.0527 | 4.833 | 4733.0023 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 4.9896 | 0.1899 | 89.8583 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 4.9896 | 0.1887 | 88.6916 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 4.9896 | 6.9982 | 6898.231 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 4.9896 | 6.9517 | 6851.7108 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 12.18 | 15.7916 | 15691.5802 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 12.18 | 17.423 | 17322.952 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 12.18 | 18.9863 | 18886.3258 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 12.18 | 18.132 | 18031.961 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 12.18 | 19.859 | 19758.9829 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 12.18 | 19.9934 | 19893.4004 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 12.18 | 20.0575 | 19957.4635 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 12.18 | 19.4862 | 19386.245 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 27.8232 | 1.8293 | 1729.326 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 21.1172 | 45.4634 | 45363.3924 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 21.1172 | 5.7969 | 5696.8898 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 21.1172 | 1.7481 | 1648.0632 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 21.1172 | 5.7969 | 5696.8827 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 18.8079 | 10.1334 | 10033.3755 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 10.0382 | 4.8321 | 4732.1108 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 10.0382 | 4.8321 | 4732.1108 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 4.9721 | 0.1899 | 89.866 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 4.9721 | 0.1887 | 88.6984 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 4.9721 | 6.9931 | 6893.0839 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 4.9721 | 6.9456 | 6845.63 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 12.1882 | 15.7972 | 15697.2496 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 12.1882 | 17.4267 | 17326.7198 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 12.1882 | 18.9907 | 18890.6881 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 12.1882 | 18.1306 | 18030.6039 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 12.1882 | 19.858 | 19758.0216 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 12.1882 | 19.9983 | 19898.3269 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 12.1882 | 20.0623 | 19962.3431 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 12.1882 | 19.4847 | 19384.7006 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 27.9111 | 1.8341 | 1734.098 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 21.1843 | 45.4247 | 45324.6785 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 21.1843 | 5.8425 | 5742.4712 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 21.1843 | 1.7547 | 1654.663 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 21.1843 | 5.8425 | 5742.4633 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 19.125 | 10.4828 | 10382.7662 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 10.0515 | 4.8327 | 4732.6932 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 10.0515 | 4.8327 | 4732.6932 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.9864 | 0.1899 | 89.8591 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.9864 | 0.1887 | 88.6922 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.9864 | 6.9928 | 6892.8284 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.9864 | 6.9461 | 6846.1299 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 12.1695 | 15.7823 | 15682.259 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 12.1695 | 17.4144 | 17314.4336 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 12.1695 | 18.9786 | 18878.553 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 12.1695 | 18.1335 | 18033.4892 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 12.1695 | 19.8593 | 19759.3075 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 12.1695 | 19.9887 | 19888.7189 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 12.1695 | 20.0487 | 19948.727 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 12.1695 | 19.4879 | 19387.9421 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 27.9147 | 1.8342 | 1734.1758 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 21.1857 | 45.4186 | 45318.5915 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 21.1857 | 5.8314 | 5731.3907 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 21.1857 | 1.7531 | 1653.1092 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 21.1857 | 5.8314 | 5731.3821 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 20.509 | 10.0215 | 9921.5276 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 10.0524 | 4.8309 | 4730.9057 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 10.0524 | 4.8309 | 4730.9057 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 4.9876 | 0.1899 | 89.8623 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 4.9876 | 0.1887 | 88.6953 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 4.9876 | 6.9832 | 6883.193 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 4.9876 | 6.9368 | 6836.763 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 12.18 | 15.7903 | 15690.2943 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 12.18 | 17.4218 | 17321.8127 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 12.18 | 18.9849 | 18884.9367 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 12.18 | 18.1318 | 18031.7926 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 12.18 | 19.8584 | 19758.3555 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 12.18 | 19.9918 | 19891.812 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 12.18 | 20.0559 | 19955.8794 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 12.18 | 19.486 | 19386.024 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 27.9155 | 1.8345 | 1734.487 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 21.1855 | 45.4218 | 45321.8311 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 21.1855 | 5.8455 | 5745.4626 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 21.1855 | 1.7551 | 1655.1189 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 21.1855 | 5.8455 | 5745.4543 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 20.5076 | 10.0838 | 9983.762 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 10.0524 | 4.8321 | 4732.0838 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 10.0524 | 4.8321 | 4732.0838 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 4.9885 | 0.1899 | 89.8605 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 4.9885 | 0.1887 | 88.6937 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 4.9885 | 6.9921 | 6892.0702 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 4.9885 | 6.9456 | 6845.6062 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 12.1786 | 15.789 | 15688.9665 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 12.1786 | 17.4209 | 17320.8865 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 12.1786 | 18.9839 | 18883.8554 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 12.1786 | 18.132 | 18032.0372 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 12.1786 | 19.8585 | 19758.4525 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 12.1786 | 19.9906 | 19890.5896 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 12.1786 | 20.0547 | 19954.6652 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 12.1786 | 19.4863 | 19386.2983 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 27.9157 | 1.8342 | 1734.2238 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 21.187 | 45.4205 | 45320.4572 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 21.187 | 5.8407 | 5740.6637 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 21.187 | 1.7544 | 1654.4317 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 21.187 | 5.8407 | 5740.6557 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 20.5308 | 10.0304 | 9930.4308 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 10.0527 | 4.8315 | 4731.5169 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 10.0527 | 4.8315 | 4731.5169 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 4.9889 | 0.1899 | 89.8606 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 4.9889 | 0.1887 | 88.6937 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 4.9889 | 6.9882 | 6888.2251 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 4.9889 | 6.9418 | 6841.7793 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 12.1887 | 15.7976 | 15697.6113 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 12.1887 | 17.4268 | 17326.804 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 12.1887 | 18.9908 | 18890.7505 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 12.1887 | 18.1302 | 18030.2496 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 12.1887 | 19.8575 | 19757.4912 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 12.1887 | 19.9984 | 19898.3883 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 12.1887 | 20.0624 | 19962.3963 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 12.1887 | 19.4843 | 19384.2812 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 27.9102 | 1.8338 | 1733.8331 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 21.1845 | 45.4232 | 45323.2073 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 21.1845 | 5.8513 | 5751.2577 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 21.1845 | 1.7559 | 1655.9428 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 21.1845 | 5.8512 | 5751.2495 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 4.8593 | 1.0002 | 900.179 | 199.98 | 222.09 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 10.0514 | 4.8313 | 4731.3346 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 10.0514 | 4.8313 | 4731.3346 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 4.9876 | 0.1899 | 89.8583 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 4.9876 | 0.1887 | 88.6915 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 4.9876 | 6.9947 | 6894.7205 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 4.9876 | 6.9482 | 6848.2093 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 12.2158 | 15.8142 | 15714.1561 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 12.2158 | 17.4403 | 17340.2749 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 12.2158 | 19.0064 | 18906.396 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 12.2158 | 18.1258 | 18025.7917 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 12.2158 | 19.8633 | 19763.3049 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 12.2158 | 20.0161 | 19916.0668 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 12.2158 | 20.0799 | 19979.9131 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 12.2158 | 19.4792 | 19379.2242 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 27.9186 | 1.835 | 1734.9861 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 21.1877 | 45.4288 | 45328.8309 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 21.1877 | 5.8892 | 5789.2014 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 21.1877 | 1.7614 | 1661.4496 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 21.1877 | 5.8892 | 5789.193 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 20.5534 | 10.0691 | 9969.0717 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 10.053 | 4.836 | 4736.042 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 10.053 | 4.836 | 4736.042 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 4.9928 | 0.1899 | 89.856 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 4.9928 | 0.1887 | 88.6899 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 4.9928 | 7.0133 | 6913.3383 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 4.9928 | 6.9669 | 6866.9311 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 12.1904 | 15.798 | 15698.0187 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 12.1904 | 17.4271 | 17327.0752 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 12.1904 | 18.9911 | 18891.0649 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 12.1904 | 18.1302 | 18030.1505 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 12.1904 | 19.8574 | 19757.4215 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 12.1904 | 19.9987 | 19898.7436 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 12.1904 | 20.0627 | 19962.7478 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 12.1904 | 19.4842 | 19384.1685 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 27.9167 | 1.8345 | 1734.4757 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 21.1877 | 45.4244 | 45324.3739 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 21.1877 | 5.8546 | 5754.629 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 21.1877 | 1.7564 | 1656.4264 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 21.1877 | 5.8546 | 5754.6203 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 20.5524 | 10.0389 | 9938.934 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 10.0529 | 4.8328 | 4732.8165 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 10.0529 | 4.8328 | 4732.8165 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 4.9902 | 0.1899 | 89.8578 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 4.9902 | 0.1887 | 88.6911 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 4.9902 | 6.9977 | 6897.6968 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 4.9902 | 6.9512 | 6851.1827 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 12.1932 | 15.8016 | 15701.5621 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 12.1932 | 17.4297 | 17329.68 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 12.1932 | 18.9941 | 18894.136 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 12.1932 | 18.1297 | 18029.7384 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 12.1932 | 19.8576 | 19757.5771 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 12.1932 | 20.0022 | 19902.2235 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 12.1932 | 20.0662 | 19966.2084 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 12.1932 | 19.4837 | 19383.7242 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 27.8154 | 1.8303 | 1730.3434 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 21.0005 | 45.4681 | 45368.1465 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 21.0005 | 5.8613 | 5761.3374 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 21.0005 | 1.7576 | 1657.5932 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 21.0005 | 5.8613 | 5761.329 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 20.2752 | 10.2578 | 10157.7556 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 10.0438 | 4.84 | 4739.9513 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 10.0438 | 4.84 | 4739.9513 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 4.9757 | 0.1899 | 89.8843 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 4.9757 | 0.1887 | 88.7168 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 4.9757 | 6.98 | 6879.9501 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 4.9757 | 6.9335 | 6833.5052 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 12.1869 | 15.798 | 15698.0422 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 12.1869 | 17.4273 | 17327.2644 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 12.1869 | 18.9913 | 18891.3182 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 12.1869 | 18.1305 | 18030.4534 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 12.1869 | 19.8579 | 19757.9441 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 12.1869 | 19.999 | 19899.0352 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 12.1869 | 20.063 | 19963.0475 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 12.1869 | 19.4845 | 19384.5296 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 27.8931 | 1.8343 | 1734.3486 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 20.9849 | 45.5407 | 45440.6709 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 20.9849 | 5.8565 | 5756.5018 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 20.9849 | 1.7565 | 1656.4877 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 20.9849 | 5.8565 | 5756.4935 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 20.517 | 10.0867 | 9986.6787 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 10.0447 | 4.8341 | 4734.1446 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 10.0447 | 4.8341 | 4734.1446 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 4.9508 | 0.1899 | 89.9022 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 4.9508 | 0.1887 | 88.735 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 4.9508 | 7.0349 | 6934.9412 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 4.9508 | 6.987 | 6887.0392 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1838 | 15.7957 | 15695.7211 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1838 | 17.4256 | 17325.5932 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1838 | 18.9894 | 18889.3547 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1838 | 18.1308 | 18030.7893 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1838 | 19.858 | 19757.954 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1838 | 19.9968 | 19896.8113 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1838 | 20.0608 | 19960.8377 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1838 | 19.4849 | 19384.8998 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 27.894 | 1.8348 | 1734.7842 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 21.0597 | 45.4655 | 45365.4702 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 21.0597 | 5.8945 | 5794.5455 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 21.0597 | 1.7622 | 1662.2329 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 21.0597 | 5.8945 | 5794.5378 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 20.4989 | 10.0851 | 9985.1187 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 10.0509 | 4.8303 | 4730.3236 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 10.0509 | 4.8303 | 4730.3236 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 4.9359 | 0.1899 | 89.9156 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 4.9359 | 0.1887 | 88.7484 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 4.9359 | 7.0341 | 6934.06 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 4.9359 | 6.9865 | 6886.5047 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 12.1871 | 15.798 | 15697.9826 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 12.1871 | 17.4272 | 17327.1763 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 12.1871 | 18.9912 | 18891.2066 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 12.1871 | 18.1304 | 18030.3819 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 12.1871 | 19.8578 | 19757.8086 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 12.1871 | 19.9989 | 19898.9084 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 12.1871 | 20.0629 | 19962.9194 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 12.1871 | 19.4844 | 19384.4443 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 27.8944 | 1.8342 | 1734.1829 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 21.003 | 45.5122 | 45412.1938 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 21.003 | 5.8407 | 5740.7171 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 21.003 | 1.7543 | 1654.2524 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 21.003 | 5.8407 | 5740.7091 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 20.519 | 10.0834 | 9983.4307 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 10.0453 | 4.8338 | 4733.7646 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 10.0453 | 4.8338 | 4733.7646 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 4.954 | 0.1899 | 89.8904 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 4.954 | 0.1887 | 88.7233 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 4.954 | 7.0246 | 6924.5814 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 4.954 | 6.977 | 6876.9707 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 12.1889 | 15.7972 | 15697.2438 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 12.1889 | 17.4265 | 17326.5128 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 12.1889 | 18.9904 | 18890.4031 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 12.1889 | 18.1303 | 18030.2554 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 12.1889 | 19.8574 | 19757.4112 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 12.1889 | 19.998 | 19897.9947 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 12.1889 | 20.062 | 19962.0023 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 12.1889 | 19.4843 | 19384.2829 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 27.916 | 1.8347 | 1734.7207 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 21.156 | 45.4083 | 45308.3388 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 21.156 | 5.8382 | 5738.1532 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 21.156 | 1.7542 | 1654.2023 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 21.156 | 5.8381 | 5738.1456 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 20.5405 | 10.0751 | 9975.1283 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 10.0525 | 4.8327 | 4732.7429 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 10.0525 | 4.8327 | 4732.7429 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 4.9849 | 0.1899 | 89.8699 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 4.9849 | 0.1887 | 88.7029 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 4.9849 | 6.9876 | 6887.5618 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 4.9849 | 6.9413 | 6841.2789 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 12.1889 | 15.7972 | 15697.2375 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 12.1889 | 17.4265 | 17326.509 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 12.1889 | 18.9904 | 18890.3987 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 12.1889 | 18.1303 | 18030.2562 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 12.1889 | 19.8574 | 19757.4108 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 12.1889 | 19.998 | 19897.9895 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 12.1889 | 20.062 | 19961.9974 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 12.1889 | 19.4843 | 19384.2848 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 27.916 | 1.8347 | 1734.7262 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 21.1562 | 45.4081 | 45308.1284 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 21.1562 | 5.8379 | 5737.9221 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 21.1562 | 1.7542 | 1654.1694 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 21.1562 | 5.8379 | 5737.9132 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 20.5405 | 10.0751 | 9975.1164 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 10.0525 | 4.8327 | 4732.7411 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 10.0525 | 4.8327 | 4732.7411 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 4.9849 | 0.1899 | 89.8699 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 4.9849 | 0.1887 | 88.7029 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 4.9849 | 6.9875 | 6887.4836 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 4.9849 | 6.9412 | 6841.2026 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.1361 | 15.7825 | 15682.5212 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.1361 | 17.4149 | 17314.9332 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.1361 | 18.9798 | 18879.7966 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.1361 | 18.1348 | 18034.8193 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.1361 | 19.8616 | 19761.5929 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.1361 | 19.9911 | 19891.0642 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.1361 | 20.0502 | 19950.1814 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.1361 | 19.4895 | 19389.5173 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 27.898 | 1.8333 | 1733.2687 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.869 | 49.7674 | 49667.45 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.869 | 7.0467 | 6946.7356 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.869 | 1.9313 | 1831.2725 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.869 | 7.0467 | 6946.7235 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 20.3709 | 10.1283 | 10028.3153 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 10.0523 | 4.8267 | 4726.6724 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 10.0523 | 4.8267 | 4726.6724 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 4.1189 | 0.1915 | 91.46 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 4.1189 | 0.1903 | 90.2688 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 4.1189 | 7.1911 | 7091.0679 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 4.1189 | 7.1337 | 7033.6965 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 11.9552 | 15.7708 | 15670.8374 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 11.9552 | 17.4023 | 17302.2939 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 11.9552 | 18.9694 | 18869.3775 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 11.9552 | 18.1431 | 18043.0752 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 11.9552 | 19.8727 | 19772.6677 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 11.9552 | 20.0024 | 19902.4301 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 11.9552 | 20.055 | 19955.0235 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 11.9552 | 19.4992 | 19399.1601 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 27.9009 | 1.8336 | 1733.6051 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 19.2401 | 46.1963 | 46096.2893 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 19.2401 | 6.0111 | 5911.0752 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 19.2401 | 1.7814 | 1681.4349 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 19.2401 | 6.0111 | 5911.0668 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 20.0966 | 10.1404 | 10040.4429 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 10.051 | 4.8289 | 4728.8989 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 10.051 | 4.8289 | 4728.8989 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.1768 | 0.198 | 98.0245 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.1768 | 0.1967 | 96.7402 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.1768 | 9.2969 | 9196.8967 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.1768 | 9.127 | 9027.0383 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 12.715 | 16.042 | 15942.0429 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 12.715 | 17.703 | 17602.9787 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 12.715 | 19.3121 | 19212.0548 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 12.715 | 18.4429 | 18342.8739 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 12.715 | 20.2141 | 20114.1486 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 12.715 | 20.362 | 20261.9737 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 12.715 | 20.4226 | 20322.6245 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 12.715 | 19.8058 | 19705.7555 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 27.8337 | 1.8433 | 1743.282 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 19.3655 | 46.5657 | 46465.6905 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 19.3655 | 6.876 | 6776.0217 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 19.3655 | 1.9203 | 1820.3455 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 19.3655 | 6.876 | 6776.0099 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 20.4857 | 10.1238 | 10023.8129 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 9.9839 | 4.8323 | 4732.3194 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 9.9839 | 4.8323 | 4732.3194 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 4.9341 | 0.1899 | 89.86 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 4.9341 | 0.1887 | 88.7083 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 4.9341 | 7.5635 | 7463.542 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 4.9341 | 7.5151 | 7415.114 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 12.1928 | 15.7999 | 15699.875 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 12.1928 | 17.4283 | 17328.2915 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 12.1928 | 18.9925 | 18892.4704 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 12.1928 | 18.1297 | 18029.682 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 12.1928 | 19.8571 | 19757.0596 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 12.1928 | 20.0003 | 19900.3276 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 12.1928 | 20.0643 | 19964.3171 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 12.1928 | 19.4836 | 19383.6331 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 27.9174 | 1.8347 | 1734.66 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 21.158 | 45.367 | 45266.975 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 21.158 | 5.7636 | 5663.6152 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 21.158 | 1.7438 | 1643.8281 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 21.158 | 5.7636 | 5663.6076 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 20.5418 | 10.0733 | 9973.3143 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 10.0527 | 4.8314 | 4731.4223 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 10.0527 | 4.8314 | 4731.4223 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 4.9893 | 0.1899 | 89.861 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 4.9893 | 0.1887 | 88.6943 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 4.9893 | 6.9925 | 6892.4935 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 4.9893 | 6.9461 | 6846.1187 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 12.1904 | 15.798 | 15698.0352 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 12.1904 | 17.4271 | 17327.0642 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 12.1904 | 18.991 | 18891.0461 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 12.1904 | 18.1301 | 18030.1126 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 12.1904 | 19.8574 | 19757.3558 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 12.1904 | 19.9987 | 19898.7208 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 12.1904 | 20.0627 | 19962.724 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 12.1904 | 19.4841 | 19384.1233 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 27.8748 | 1.8347 | 1734.6705 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 21.1663 | 45.4379 | 45337.8573 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 21.1663 | 5.8597 | 5759.6752 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 21.1663 | 1.7572 | 1657.1858 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 21.1663 | 5.8597 | 5759.6669 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 20.5395 | 10.0734 | 9973.3918 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 9.2586 | 5.0857 | 4985.6821 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 9.2586 | 5.0857 | 4985.6821 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 4.9896 | 0.1899 | 89.8609 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 4.9896 | 0.1887 | 88.6941 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 4.9896 | 6.9953 | 6895.2832 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 4.9896 | 6.9488 | 6848.7865 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 12.1897 | 15.7974 | 15697.3841 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 12.1897 | 17.4266 | 17326.6162 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 12.1897 | 18.9905 | 18890.5251 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 12.1897 | 18.1302 | 18030.2439 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 12.1897 | 19.8574 | 19757.423 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 12.1897 | 19.9981 | 19898.1302 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 12.1897 | 20.0621 | 19962.1397 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 12.1897 | 19.4843 | 19384.2708 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 27.9166 | 1.8344 | 1734.417 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 21.1874 | 45.4237 | 45323.6916 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 21.1874 | 5.8545 | 5754.4745 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 21.1874 | 1.7564 | 1656.4108 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 21.1874 | 5.8545 | 5754.4668 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 20.5418 | 10.073 | 9973.0275 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 10.0486 | 4.8142 | 4714.185 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 10.0486 | 4.8142 | 4714.185 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 4.9901 | 6.9964 | 6896.3737 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 4.9901 | 6.9499 | 6849.9005 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 12.1896 | 15.7974 | 15697.372 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 12.1896 | 17.4266 | 17326.6087 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 12.1896 | 18.9905 | 18890.5152 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 12.1896 | 18.1302 | 18030.2461 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 12.1896 | 19.8574 | 19757.4239 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 12.1896 | 19.9981 | 19898.119 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 12.1896 | 20.0621 | 19962.1286 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 12.1896 | 19.4843 | 19384.2735 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 27.9167 | 1.8344 | 1734.4104 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 21.1873 | 45.4238 | 45323.802 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 21.1873 | 5.8546 | 5754.6111 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 21.1873 | 1.7564 | 1656.4301 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 21.1873 | 5.8546 | 5754.6028 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 20.5418 | 10.073 | 9973.0068 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 10.0482 | 4.8047 | 4704.6889 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 10.0482 | 4.8047 | 4704.6889 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 4.9901 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 4.9901 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 4.9901 | 6.9964 | 6896.3847 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 4.9901 | 6.9499 | 6849.9109 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 12.3739 | 15.8866 | 15786.605 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 12.3739 | 17.5238 | 17423.7842 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 12.3739 | 19.1035 | 19003.5145 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 12.3739 | 18.2214 | 18121.3702 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 12.3739 | 19.9746 | 19874.6253 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 12.3739 | 20.1259 | 20025.8816 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 12.3739 | 20.1887 | 20088.7415 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 12.3739 | 19.5514 | 19451.3507 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 27.9333 | 1.8378 | 1737.8362 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 21.221 | 45.5694 | 45469.4412 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 21.221 | 6.0288 | 5928.7643 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 21.221 | 1.782 | 1681.9965 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 21.221 | 6.0288 | 5928.7552 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 20.5472 | 10.0885 | 9988.4985 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 10.0578 | 4.8505 | 4750.491 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 10.0578 | 4.8505 | 4750.491 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 5.0122 | 0.1899 | 89.8565 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 5.0122 | 0.1887 | 88.694 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 5.0122 | 7.1427 | 7042.6799 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 5.0122 | 7.0961 | 6996.0844 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 12.2681 | 15.8403 | 15740.255 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 12.2681 | 17.4704 | 17370.371 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 12.2681 | 19.0414 | 18941.4027 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 12.2681 | 18.1556 | 18055.5684 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 12.2681 | 19.9034 | 19803.3991 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 12.2681 | 20.0556 | 19955.6424 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 12.2681 | 20.1191 | 20019.1408 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 12.2681 | 19.4759 | 19375.8595 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 27.8567 | 1.8361 | 1736.1183 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 20.9554 | 45.5042 | 45404.1648 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 20.9554 | 5.8734 | 5773.3532 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 20.9554 | 1.759 | 1659.0011 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 20.9554 | 5.8733 | 5773.3445 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 20.5229 | 10.082 | 9981.9944 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 10.0171 | 4.8399 | 4739.9342 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 10.0171 | 4.8399 | 4739.9342 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 4.9787 | 0.1899 | 89.8603 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 4.9787 | 0.1887 | 88.6954 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 4.9787 | 7.0646 | 6964.5804 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 4.9787 | 7.0179 | 6917.9187 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.1906 | 15.7982 | 15698.2403 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.1906 | 17.4272 | 17327.1929 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.1906 | 18.9912 | 18891.1936 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.1906 | 18.13 | 18030.0489 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.1906 | 19.8573 | 19757.2956 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.1906 | 19.9989 | 19898.8872 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.1906 | 20.0629 | 19962.8881 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.1906 | 19.4841 | 19384.0505 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 27.9052 | 1.8345 | 1734.4929 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 21.1859 | 45.4467 | 45346.6735 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 21.1859 | 5.8478 | 5747.8226 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 21.1859 | 1.7553 | 1655.3372 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 21.1859 | 5.8478 | 5747.814 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 20.5412 | 10.0728 | 9972.8488 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 10.0508 | 4.8287 | 4728.696 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 10.0508 | 4.8287 | 4728.696 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 4.9906 | 0.1899 | 89.8576 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 4.9906 | 0.1887 | 88.691 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 4.9906 | 7.0008 | 6900.7666 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 4.9906 | 6.9542 | 6854.2331 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 12.1652 | 15.78 | 15680.0383 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 12.1652 | 17.4119 | 17311.9245 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 12.1652 | 18.9771 | 18877.0614 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 12.1652 | 18.1343 | 18034.2789 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 12.1652 | 19.8601 | 19760.133 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 12.1652 | 19.9895 | 19889.549 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 12.1652 | 20.0471 | 19947.0523 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 12.1652 | 19.4889 | 19388.8551 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 27.9007 | 1.8325 | 1732.5461 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 21.1551 | 45.4011 | 45301.145 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 21.1551 | 5.7319 | 5631.9185 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 21.1551 | 1.7393 | 1639.2632 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 21.1551 | 5.7319 | 5631.9115 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 20.5408 | 10.0708 | 9970.8061 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 10.0468 | 4.8232 | 4723.197 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 10.0468 | 4.8232 | 4723.197 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 4.9824 | 0.1899 | 89.8654 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 4.9824 | 0.1887 | 88.6972 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 4.9824 | 6.9508 | 6850.8064 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 4.9824 | 6.9042 | 6804.1877 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1876 | 15.7971 | 15697.1412 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1876 | 17.4265 | 17326.525 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1876 | 18.9904 | 18890.4321 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1876 | 18.1304 | 18030.4251 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1876 | 19.8577 | 19757.6739 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1876 | 19.998 | 19898.0293 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1876 | 20.062 | 19962.0433 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 12.1876 | 19.4845 | 19384.4838 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 27.9007 | 1.8334 | 1733.3563 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 21.1607 | 45.4203 | 45320.2637 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 21.1607 | 5.7569 | 5656.853 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 21.1607 | 1.7426 | 1642.6361 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 21.1607 | 5.7568 | 5656.8449 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 20.5105 | 10.0853 | 9985.2835 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 10.0531 | 4.8319 | 4731.8935 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 10.0531 | 4.8319 | 4731.8935 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 4.9582 | 0.1899 | 89.8883 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 4.9582 | 0.1887 | 88.7207 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 4.9582 | 7.0046 | 6904.5712 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 4.9582 | 6.9572 | 6857.1814 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 12.1875 | 15.7966 | 15696.5601 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 12.1875 | 17.4261 | 17326.0888 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 12.1875 | 18.9899 | 18889.9176 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 12.1875 | 18.1305 | 18030.4779 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 12.1875 | 19.8576 | 19757.6242 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 12.1875 | 19.9974 | 19897.4446 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 12.1875 | 20.0615 | 19961.4619 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 12.1875 | 19.4845 | 19384.539 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 27.9123 | 1.8344 | 1734.36 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 21.0132 | 45.4749 | 45374.894 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 21.0132 | 5.8568 | 5756.7544 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 21.0132 | 1.7568 | 1656.8061 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 21.0132 | 5.8567 | 5756.7464 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 20.5334 | 10.075 | 9975.0359 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 10.0512 | 4.8316 | 4731.6408 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 10.0512 | 4.8316 | 4731.6408 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 4.9739 | 0.1899 | 89.8759 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 4.9739 | 0.1887 | 88.7089 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 4.9739 | 7.0002 | 6900.2381 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 4.9739 | 6.9535 | 6853.5432 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 12.3658 | 15.884 | 15783.974 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 12.3658 | 17.5207 | 17420.7095 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 12.3658 | 19.0999 | 18999.9071 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 12.3658 | 18.2177 | 18117.7455 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 12.3658 | 19.9705 | 19870.5036 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 12.3658 | 20.1218 | 20021.7962 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 12.3658 | 20.1847 | 20084.6838 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 12.3658 | 19.5472 | 19447.1799 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 27.9048 | 1.8378 | 1737.7769 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 20.9247 | 45.6094 | 45509.434 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 20.9247 | 6.0599 | 5959.9406 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 20.9247 | 1.7864 | 1686.3803 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 20.9247 | 6.0599 | 5959.932 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 20.5293 | 10.0864 | 9986.426 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 10.0372 | 4.8442 | 4744.1598 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 10.0372 | 4.8442 | 4744.1598 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 4.9873 | 0.1899 | 89.8517 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 4.9873 | 0.1887 | 88.6895 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 4.9873 | 7.1514 | 7051.4022 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 4.9873 | 7.1047 | 7004.656 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 12.1893 | 15.7973 | 15697.2985 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 12.1893 | 17.4266 | 17326.568 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 12.1893 | 18.9905 | 18890.4701 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 12.1893 | 18.1303 | 18030.2783 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 12.1893 | 19.8575 | 19757.4608 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 12.1893 | 19.9981 | 19898.0687 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 12.1893 | 20.0621 | 19962.0792 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 12.1893 | 19.4843 | 19384.3109 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 27.9152 | 1.8345 | 1734.4672 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 21.1598 | 45.4313 | 45331.2603 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 21.1598 | 5.8567 | 5756.7 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 21.1598 | 1.7567 | 1656.7452 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 21.1598 | 5.8567 | 5756.6914 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 20.5411 | 10.0732 | 9973.2499 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 10.0512 | 4.8329 | 4732.8999 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 10.0512 | 4.8329 | 4732.8999 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 4.9884 | 0.1899 | 89.8603 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 4.9884 | 0.1887 | 88.6936 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 4.9884 | 6.9965 | 6896.4832 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 4.9884 | 6.95 | 6849.9968 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 12.1892 | 15.7973 | 15697.3078 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 12.1892 | 17.4266 | 17326.5797 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 12.1892 | 18.9905 | 18890.4847 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 12.1892 | 18.1303 | 18030.2862 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 12.1892 | 19.8575 | 19757.4765 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 12.1892 | 19.9981 | 19898.0856 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 12.1892 | 20.0621 | 19962.0963 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 12.1892 | 19.4843 | 19384.3203 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 27.9143 | 1.8345 | 1734.4887 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 21.1439 | 45.4373 | 45337.2713 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 21.1439 | 5.8586 | 5758.6194 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 21.1439 | 1.757 | 1657.0204 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 21.1439 | 5.8586 | 5758.6113 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 20.5407 | 10.0734 | 9973.3567 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 10.0502 | 4.8331 | 4733.1227 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 10.0502 | 4.8331 | 4733.1227 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 4.9875 | 0.1899 | 89.8612 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 4.9875 | 0.1887 | 88.6944 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 4.9875 | 6.9968 | 6896.8157 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 4.9875 | 6.9503 | 6850.3166 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.101 | 15.7542 | 15654.2302 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.101 | 17.3821 | 17282.1499 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.101 | 18.9453 | 18845.3496 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.101 | 18.1398 | 18039.7871 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.101 | 19.8632 | 19763.1937 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.101 | 19.9926 | 19892.5818 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.101 | 20.045 | 19945.0226 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 12.101 | 19.4951 | 19395.068 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 27.8913 | 1.8308 | 1730.8131 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 9.6573 | 49.5309 | 49430.8634 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 9.6573 | 5.1414 | 5041.4153 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 9.6573 | 1.7266 | 1626.5886 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 9.6573 | 5.1414 | 5041.4091 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 20.3719 | 10.0951 | 9995.1129 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 10.0518 | 4.8278 | 4727.8049 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 10.0518 | 4.8278 | 4727.8049 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 4.1091 | 0.191 | 91.047 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 4.1091 | 0.1899 | 89.8565 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 4.1091 | 6.858 | 6757.9882 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 4.1091 | 6.8074 | 6707.4044 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.189 | 15.7969 | 15696.8947 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.189 | 17.4263 | 17326.2929 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.189 | 18.9901 | 18890.1492 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.189 | 18.1304 | 18030.3639 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.189 | 19.8575 | 19757.5103 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.189 | 19.9977 | 19897.7057 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.189 | 20.0617 | 19961.7197 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 12.189 | 19.4844 | 19384.4088 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 27.9115 | 1.8344 | 1734.417 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 21.1379 | 45.4388 | 45338.8422 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 21.1379 | 5.8158 | 5715.7832 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 21.1379 | 1.7509 | 1650.9219 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 21.1379 | 5.8158 | 5715.7743 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 20.5422 | 10.073 | 9972.9575 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 10.0101 | 4.8412 | 4741.1982 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 10.0101 | 4.8412 | 4741.1982 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 4.989 | 0.1899 | 89.8613 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 4.989 | 0.1887 | 88.6946 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 4.989 | 6.9966 | 6896.5872 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 4.989 | 6.9501 | 6850.0765 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 12.1804 | 15.7904 | 15690.4339 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 12.1804 | 17.422 | 17321.9969 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 12.1804 | 18.9851 | 18885.1166 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 12.1804 | 18.1318 | 18031.8313 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 12.1804 | 19.8585 | 19758.4688 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 12.1804 | 19.9919 | 19891.9322 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 12.1804 | 20.0561 | 19956.085 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 12.1804 | 19.4861 | 19386.0738 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 27.9149 | 1.8335 | 1733.4552 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 21.1308 | 45.4057 | 45305.6765 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 21.1308 | 5.8107 | 5710.6529 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 21.1308 | 1.7504 | 1650.3822 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 21.1308 | 5.8106 | 5710.6447 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 20.542 | 10.0722 | 9972.2071 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 10.0532 | 4.8385 | 4738.5118 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 10.0532 | 4.8385 | 4738.5118 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 4.9846 | 0.1899 | 89.8662 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 4.9846 | 0.1887 | 88.6986 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 4.9846 | 6.9679 | 6867.9422 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 4.9846 | 6.9215 | 6821.4598 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 12.1901 | 15.798 | 15697.9931 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 12.1901 | 17.427 | 17327.0169 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 12.1901 | 18.991 | 18890.9886 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 12.1901 | 18.1301 | 18030.0905 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 12.1901 | 19.8573 | 19757.3053 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 12.1901 | 19.9987 | 19898.6532 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 12.1901 | 20.0627 | 19962.6575 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 12.1901 | 19.4841 | 19384.0956 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 27.9155 | 1.8345 | 1734.4959 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 21.1548 | 45.3827 | 45282.6592 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 21.1548 | 5.8001 | 5700.0634 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 21.1548 | 1.7489 | 1648.893 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 21.1548 | 5.8001 | 5700.0549 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 20.5411 | 10.0726 | 9972.6204 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 10.0531 | 4.8356 | 4735.6311 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 10.0531 | 4.8356 | 4735.6311 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 4.9888 | 0.1899 | 89.8614 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 4.9888 | 0.1887 | 88.6947 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 4.9888 | 6.9935 | 6893.5114 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 4.9888 | 6.9471 | 6847.15 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 12.1748 | 15.7863 | 15686.3229 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 12.1748 | 17.4191 | 17319.132 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 12.1748 | 18.9818 | 18881.84 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 12.1748 | 18.1327 | 18032.6811 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 12.1748 | 19.8589 | 19758.9258 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 12.1748 | 19.9883 | 19888.3328 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 12.1748 | 20.0524 | 19952.4138 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 12.1748 | 19.487 | 19387.032 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 27.9117 | 1.8336 | 1733.5532 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 21.0965 | 45.3683 | 45268.2891 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 21.0965 | 5.6918 | 5591.807 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 21.0965 | 1.7341 | 1634.1048 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 21.0965 | 5.6918 | 5591.7991 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 20.5415 | 10.0718 | 9971.8489 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 10.0517 | 4.8345 | 4734.4552 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 10.0517 | 4.8345 | 4734.4552 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 4.9833 | 0.1899 | 89.8692 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 4.9833 | 0.1887 | 88.7013 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 4.9833 | 6.962 | 6861.9687 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 4.9833 | 6.9155 | 6815.5252 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 12.1943 | 15.8012 | 15701.2073 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 12.1943 | 17.4292 | 17329.1652 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 12.1943 | 18.9935 | 18893.4786 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 12.1943 | 18.1293 | 18029.3431 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 12.1943 | 19.8568 | 19756.7979 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 12.1943 | 20.0015 | 19901.4678 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 12.1943 | 20.0654 | 19965.4445 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 12.1943 | 19.4832 | 19383.2464 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 27.915 | 1.8345 | 1734.5107 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 21.126 | 45.3754 | 45275.4202 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 21.126 | 5.9284 | 5828.366 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 21.126 | 1.7678 | 1667.8185 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 21.126 | 5.9284 | 5828.3578 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 20.5404 | 10.0723 | 9972.2752 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 10.0515 | 4.8367 | 4736.7188 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 10.0515 | 4.8367 | 4736.7188 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 4.9871 | 0.1899 | 89.865 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 4.9871 | 0.1887 | 88.6983 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 4.9871 | 6.9915 | 6891.4762 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 4.9871 | 6.9452 | 6845.2327 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 12.2795 | 15.8716 | 15771.6314 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 12.2795 | 17.5121 | 17412.0676 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 12.2795 | 19.0939 | 18993.905 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 12.2795 | 18.1849 | 18084.9104 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 12.2795 | 19.9612 | 19861.222 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 12.2795 | 20.1156 | 20015.6193 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 12.2795 | 20.1799 | 20079.8569 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 12.2795 | 19.5111 | 19411.0865 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 27.9171 | 1.8346 | 1734.5782 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 21.1875 | 45.4277 | 45327.7449 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 21.1875 | 5.8734 | 5773.3507 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 21.1875 | 1.7591 | 1659.1382 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 21.1875 | 5.8733 | 5773.3426 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 20.5418 | 10.0761 | 9976.0559 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 10.0529 | 4.8358 | 4735.7719 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 10.0529 | 4.8358 | 4735.7719 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 4.989 | 0.1899 | 89.8628 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 4.989 | 0.1887 | 88.6958 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 4.989 | 6.9911 | 6891.1443 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 4.989 | 6.9446 | 6844.5524 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 12.2827 | 15.8718 | 15771.8044 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 12.2827 | 17.5122 | 17412.189 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 12.2827 | 19.094 | 18993.9899 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 12.2827 | 18.1854 | 18085.3551 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 12.2827 | 19.9613 | 19861.347 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 12.2827 | 20.1157 | 20015.7062 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 12.2827 | 20.1799 | 20079.926 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 12.2827 | 19.5116 | 19411.5712 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 27.9172 | 1.8346 | 1734.5828 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 21.1875 | 45.4278 | 45327.7905 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 21.1875 | 5.8737 | 5773.7254 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 21.1875 | 1.7592 | 1659.1928 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 21.1875 | 5.8737 | 5773.7173 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 20.5419 | 10.076 | 9976.0281 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 10.0529 | 4.8358 | 4735.7978 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 10.0529 | 4.8358 | 4735.7978 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 4.9891 | 0.1899 | 89.8627 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 4.9891 | 0.1887 | 88.6957 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 4.9891 | 6.9914 | 6891.3607 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 4.9891 | 6.9448 | 6844.7715 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 10.4554 | 15.9636 | 15863.5601 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 10.4554 | 17.6475 | 17547.5302 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 10.4554 | 19.2678 | 19167.7859 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 10.4554 | 18.2894 | 18189.3835 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 10.4554 | 20.1645 | 20064.4883 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 10.4554 | 20.3139 | 20213.8777 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 10.4554 | 20.3821 | 20282.1289 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 10.4554 | 19.6746 | 19574.5811 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 27.9077 | 1.8342 | 1734.1798 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 21.1632 | 45.4223 | 45322.2887 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 21.1632 | 5.8088 | 5708.8179 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 21.1632 | 1.7499 | 1649.888 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 21.1632 | 5.8088 | 5708.8101 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 20.515 | 10.0808 | 9980.8403 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 10.0493 | 4.828 | 4728.0317 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 10.0493 | 4.828 | 4728.0317 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 4.9782 | 0.1899 | 89.8614 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 4.9782 | 0.1887 | 88.6957 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 4.9782 | 7.0323 | 6932.3454 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 4.9782 | 6.9858 | 6885.7818 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 12.187 | 15.7677 | 15667.6738 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 12.187 | 17.3968 | 17296.8424 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 12.187 | 18.9617 | 18861.6721 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 12.187 | 18.1316 | 18031.5595 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 12.187 | 19.8525 | 19752.4786 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 12.187 | 19.9816 | 19881.5902 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 12.187 | 20.034 | 19933.9695 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 12.187 | 19.4855 | 19385.4582 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 27.9172 | 1.8344 | 1734.383 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 21.1886 | 45.4226 | 45322.6346 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 21.1886 | 5.8495 | 5749.5198 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 21.1886 | 1.7557 | 1655.699 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 21.1886 | 5.8495 | 5749.5122 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 20.5428 | 10.0729 | 9972.8706 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 10.0531 | 4.8323 | 4732.3314 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 10.0531 | 4.8323 | 4732.3314 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 4.9903 | 0.1899 | 89.8588 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 4.9903 | 0.1887 | 88.692 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 4.9903 | 6.9939 | 6893.9114 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 4.9903 | 6.9474 | 6847.4324 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 12.2414 | 15.8259 | 15725.9102 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 12.2414 | 17.4538 | 17353.813 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 12.2414 | 19.0221 | 18922.1333 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 12.2414 | 18.1251 | 18025.1357 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 12.2414 | 19.8813 | 19781.3264 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 12.2414 | 20.0339 | 19933.8556 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 12.2414 | 20.0975 | 19997.5438 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 12.2414 | 19.4746 | 19374.624 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 27.9217 | 1.8357 | 1735.6528 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 21.1873 | 45.4375 | 45337.5295 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 21.1873 | 5.9181 | 5818.1185 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 21.1873 | 1.7657 | 1665.688 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 21.1873 | 5.9181 | 5818.1103 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 20.5428 | 10.0771 | 9977.1135 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 10.0542 | 4.8459 | 4745.9495 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 10.0542 | 4.8459 | 4745.9495 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 4.9952 | 0.1899 | 89.855 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 4.9952 | 0.1887 | 88.6895 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 4.9952 | 7.0316 | 6931.6191 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 4.9952 | 6.9852 | 6885.2097 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 12.2414 | 15.8259 | 15725.9214 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 12.2414 | 17.4538 | 17353.826 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 12.2414 | 19.0221 | 18922.1484 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 12.2414 | 18.1252 | 18025.1594 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 12.2414 | 19.8813 | 19781.3437 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 12.2414 | 20.0339 | 19933.8713 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 12.2414 | 20.0976 | 19997.5593 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 12.2414 | 19.4746 | 19374.6224 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 27.9221 | 1.8357 | 1735.6537 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 21.1874 | 45.4375 | 45337.5345 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 21.1874 | 5.9181 | 5818.1456 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 21.1874 | 1.7657 | 1665.6921 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 21.1874 | 5.9181 | 5818.1371 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 20.5428 | 10.0771 | 9977.1185 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 10.0543 | 4.846 | 4745.9552 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 10.0543 | 4.846 | 4745.9552 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 4.9952 | 0.1899 | 89.855 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 4.9952 | 0.1887 | 88.6895 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 4.9952 | 7.0316 | 6931.6343 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 4.9952 | 6.9852 | 6885.2257 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 12.2487 | 15.8293 | 15729.2886 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 12.2487 | 17.4577 | 17357.7023 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 12.2487 | 19.0267 | 18926.6534 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 12.2487 | 18.1328 | 18032.7669 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 12.2487 | 19.8865 | 19786.5027 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 12.2487 | 20.039 | 19938.9641 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 12.2487 | 20.1026 | 20002.6063 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 12.2487 | 19.4739 | 19373.9488 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 27.9201 | 1.8358 | 1735.7907 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 21.1868 | 45.4394 | 45339.4089 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 21.1868 | 5.9267 | 5826.6892 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 21.1868 | 1.767 | 1666.9575 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 21.1868 | 5.9267 | 5826.6804 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 20.5426 | 10.0775 | 9977.5392 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 10.0534 | 4.8477 | 4747.7045 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 10.0534 | 4.8477 | 4747.7045 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 4.9957 | 0.1899 | 89.8547 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 4.9957 | 0.1887 | 88.6893 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 4.9957 | 7.0362 | 6936.2497 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 4.9957 | 6.9899 | 6889.85 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 12.2474 | 15.8287 | 15728.6985 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 12.2474 | 17.457 | 17357.0245 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 12.2474 | 19.0259 | 18925.8669 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 12.2474 | 18.1314 | 18031.4227 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 12.2474 | 19.8856 | 19785.6014 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 12.2474 | 20.0381 | 19938.0742 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 12.2474 | 20.1017 | 20001.7247 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 12.2474 | 19.4741 | 19374.0789 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 27.92 | 1.8358 | 1735.831 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 21.1868 | 45.4397 | 45339.6718 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 21.1868 | 5.9253 | 5825.3003 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 21.1868 | 1.7667 | 1666.7495 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 21.1868 | 5.9253 | 5825.291 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 20.5426 | 10.0777 | 9977.7418 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 10.0534 | 4.8479 | 4747.8963 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 10.0534 | 4.8479 | 4747.8963 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 4.9956 | 0.1899 | 89.855 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 4.9956 | 0.1887 | 88.6896 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 4.9956 | 7.0356 | 6935.6365 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 4.9956 | 6.9892 | 6889.2281 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 12.4925 | 15.9489 | 15848.8524 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 12.4925 | 17.5972 | 17497.1734 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 12.4925 | 19.1901 | 19090.0815 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 12.4925 | 18.3055 | 18205.4811 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 12.4925 | 20.0733 | 19973.3107 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 12.4925 | 20.224 | 20124.0314 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 12.4925 | 20.2864 | 20186.3568 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 12.4925 | 19.6484 | 19548.3761 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 27.9242 | 1.8373 | 1737.3456 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 21.1855 | 45.4927 | 45392.6762 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 21.1855 | 6.1344 | 6034.4295 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 21.1855 | 1.7991 | 1699.1286 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 21.1855 | 6.1344 | 6034.4199 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 20.5454 | 10.1286 | 10028.6024 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 10.053 | 4.8641 | 4764.0797 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 10.053 | 4.8641 | 4764.0797 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 5.0026 | 0.1899 | 89.9028 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 5.0026 | 0.1887 | 88.7381 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 5.0026 | 7.1158 | 7015.8194 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 5.0026 | 7.0682 | 6968.173 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 12.4583 | 15.9634 | 15863.422 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 12.4583 | 17.6196 | 17519.6013 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 12.4583 | 19.2203 | 19120.2601 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 12.4583 | 18.3109 | 18210.8618 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 12.4583 | 20.1056 | 20005.5862 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 12.4583 | 20.2588 | 20158.8083 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 12.4583 | 20.3221 | 20222.1183 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 12.4583 | 19.6561 | 19556.1201 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 27.9185 | 1.8352 | 1735.2146 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 21.1861 | 45.4472 | 45347.2277 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 21.1861 | 5.9481 | 5848.0869 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 21.1861 | 1.7701 | 1670.1382 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 21.1861 | 5.9481 | 5848.0787 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 20.5419 | 10.0932 | 9993.1658 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 10.0529 | 4.8478 | 4747.8425 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 10.0529 | 4.8478 | 4747.8425 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 4.9877 | 0.1899 | 89.8825 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 4.9877 | 0.1887 | 88.715 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 4.9877 | 6.9957 | 6895.7055 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 4.9877 | 6.9486 | 6848.6031 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 12.19 | 15.7951 | 15695.0778 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 12.19 | 17.4247 | 17324.7264 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 12.19 | 18.9883 | 18888.2605 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 12.19 | 18.1302 | 18030.1702 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 12.19 | 19.8567 | 19756.7339 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 12.19 | 19.9956 | 19895.5592 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 12.19 | 20.0596 | 19959.5729 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 12.19 | 19.4842 | 19384.1528 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 27.9171 | 1.8344 | 1734.433 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 21.1879 | 45.4234 | 45323.3874 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 21.1879 | 5.8539 | 5753.9245 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 21.1879 | 1.7563 | 1656.333 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 21.1879 | 5.8539 | 5753.9172 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 20.5421 | 10.0731 | 9973.0933 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 10.053 | 4.8325 | 4732.5478 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 10.053 | 4.8325 | 4732.5478 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 4.9902 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 4.9902 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 4.9902 | 6.9962 | 6896.1549 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 4.9902 | 6.9497 | 6849.6796 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 12.19 | 15.7952 | 15695.1779 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 12.19 | 17.4248 | 17324.8056 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 12.19 | 18.9884 | 18888.3549 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 12.19 | 18.1302 | 18030.1677 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 12.19 | 19.8568 | 19756.7548 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 12.19 | 19.9957 | 19895.6655 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 12.19 | 20.0597 | 19959.6788 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 12.19 | 19.4842 | 19384.1521 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 27.9171 | 1.8344 | 1734.4332 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 21.1879 | 45.4234 | 45323.3895 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 21.1879 | 5.8539 | 5753.9378 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 21.1879 | 1.7563 | 1656.3348 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 21.1879 | 5.8539 | 5753.9298 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 20.5421 | 10.0731 | 9973.0956 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 10.053 | 4.8325 | 4732.5484 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 10.053 | 4.8325 | 4732.5484 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 4.9902 | 0.1899 | 89.8586 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 4.9902 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 4.9902 | 6.9962 | 6896.1622 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 4.9902 | 6.9497 | 6849.6877 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 12.2027 | 15.8076 | 15707.6218 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 12.2027 | 17.4336 | 17333.5831 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 12.2027 | 18.9986 | 18898.6309 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 12.2027 | 18.1281 | 18028.0804 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 12.2027 | 19.8562 | 19756.1835 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 12.2027 | 20.0073 | 19907.2927 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 12.2027 | 20.0712 | 19971.2231 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 12.2027 | 19.4818 | 19381.8247 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 27.9181 | 1.8352 | 1735.1822 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 21.1879 | 45.4328 | 45332.8252 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 21.1879 | 5.8711 | 5771.1102 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 21.1879 | 1.7588 | 1658.789 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 21.1879 | 5.8711 | 5771.1018 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 20.5421 | 10.0768 | 9976.8198 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 10.0541 | 4.8113 | 4711.2881 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 10.0541 | 4.8113 | 4711.2881 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 4.9915 | 0.1899 | 89.8583 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 4.9915 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 4.9915 | 7.0075 | 6907.5031 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 4.9915 | 6.961 | 6860.9788 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 12.194 | 15.8008 | 15700.7536 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 12.194 | 17.4289 | 17328.9128 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 12.194 | 18.9932 | 18893.198 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 12.194 | 18.1295 | 18029.5322 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 12.194 | 19.857 | 19757.0183 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 12.194 | 20.0012 | 19901.1529 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 12.194 | 20.0651 | 19965.1354 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 12.194 | 19.4835 | 19383.4664 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 27.9174 | 1.8347 | 1734.6727 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 21.1876 | 45.4268 | 45326.7738 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 21.1876 | 5.8598 | 5759.7799 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 21.1876 | 1.7572 | 1657.168 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 21.1876 | 5.8598 | 5759.772 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 20.5419 | 10.0744 | 9974.4418 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 10.0524 | 4.7961 | 4696.056 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 10.0524 | 4.7961 | 4696.056 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 4.9905 | 0.1899 | 89.8585 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 4.9905 | 0.1887 | 88.6919 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 4.9905 | 7.0001 | 6900.0641 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 4.9905 | 6.9536 | 6853.5702 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 12.3744 | 15.8868 | 15786.8262 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 12.3744 | 17.524 | 17423.967 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 12.3744 | 19.1037 | 19003.6765 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 12.3744 | 18.2218 | 18121.8467 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 12.3744 | 19.9748 | 19874.8246 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 12.3744 | 20.1261 | 20026.0569 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 12.3744 | 20.1889 | 20088.9012 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 12.3744 | 19.5519 | 19451.8839 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 27.9256 | 1.8378 | 1737.8261 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 21.1839 | 45.514 | 45414.046 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 21.1839 | 6.3552 | 6255.2082 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 21.1839 | 1.8371 | 1737.0924 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 21.1839 | 6.3552 | 6255.198 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 20.544 | 10.08 | 9979.9772 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 10.0525 | 4.8574 | 4757.3958 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 10.0525 | 4.8574 | 4757.3958 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 5.0163 | 0.1898 | 89.8305 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 5.0163 | 0.1887 | 88.67 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 5.0163 | 7.1759 | 7075.8667 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 5.0163 | 7.13 | 7030.0068 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 8.7876 | 16.1114 | 16011.3711 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 8.7876 | 17.845 | 17744.9645 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 8.7876 | 19.5168 | 19416.7667 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 8.7876 | 18.4303 | 18330.2752 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 8.7876 | 20.4409 | 20340.8713 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 8.7876 | 20.5982 | 20498.2393 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 8.7876 | 20.6705 | 20570.4594 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 8.7876 | 19.8434 | 19743.4444 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 27.9145 | 1.8343 | 1734.2827 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 21.1767 | 45.4205 | 45320.4842 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 21.1767 | 5.8272 | 5727.2182 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 21.1767 | 1.7525 | 1652.5107 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 21.1767 | 5.8272 | 5727.21 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 20.5194 | 10.0765 | 9976.473 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 10.0522 | 4.8298 | 4729.7622 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 10.0522 | 4.8298 | 4729.7622 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 4.979 | 0.1899 | 89.8597 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 4.979 | 0.1887 | 88.6937 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 4.979 | 7.0175 | 6917.5432 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 4.979 | 6.9711 | 6871.0725 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 12.1889 | 15.7631 | 15663.0761 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 12.1889 | 17.3914 | 17291.4187 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 12.1889 | 18.9553 | 18855.3145 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 12.1889 | 18.1317 | 18031.733 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 12.1889 | 19.8517 | 19751.6631 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 12.1889 | 19.9807 | 19880.7273 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 12.1889 | 20.0331 | 19933.078 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 12.1889 | 19.4856 | 19385.6073 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 27.9174 | 1.8344 | 1734.3646 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 21.1889 | 45.4223 | 45322.349 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 21.1889 | 5.8479 | 5747.9319 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 21.1889 | 1.7555 | 1655.4711 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 21.1889 | 5.8479 | 5747.9232 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 20.5431 | 10.0728 | 9972.7744 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 10.0532 | 4.8323 | 4732.2646 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 10.0532 | 4.8323 | 4732.2646 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 4.9904 | 0.1899 | 89.8589 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 4.9904 | 0.1887 | 88.6921 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 4.9904 | 6.9929 | 6892.9392 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 4.9904 | 6.9465 | 6846.4584 | 198.13 | 233.2 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 12.1573 | 15.7623 | 15662.3098 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 12.1573 | 17.4185 | 17318.5063 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 12.1573 | 19.0316 | 18931.5734 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 12.1573 | 18.1955 | 18095.5234 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 12.1573 | 19.9584 | 19858.4494 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 12.1573 | 20.0934 | 19993.427 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 12.1573 | 20.1513 | 20051.2999 | 40.38 | 88.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-009 | Lawton East Side to Oklaunion 345kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 12.1573 | 19.5613 | 19461.2966 | 28.85 | 63 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-017 | 230kV Lamb County Interchange | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 27.9175 | 1.8342 | 1734.1895 | 71.16 | 74.88 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 21.1904 | 45.4214 | 45321.4022 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 21.1904 | 5.8335 | 5733.5121 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 21.1904 | 1.7534 | 1653.4053 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-059 | Tuco-Yoakum-Hobbs 345 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 21.1904 | 5.8335 | 5733.5039 | 62.5 | 141.53 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-060 | Lubbock East Substation 230 kV | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 20.5443 | 10.0742 | 9974.1515 | 199.98 | 222.09 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 10.0534 | 4.8319 | 4731.89 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-062 | OASIS 230kV Substation | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 10.0534 | 4.8319 | 4731.89 | 128 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 4.9895 | 0.1899 | 89.8616 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-067 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 4.9895 | 0.1887 | 88.6944 | 176.25 | 200.51 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 4.9895 | 6.9827 | 6882.6582 | 201.87 | 237.6 | FAIL | PASS
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | GEN-2020-068 | Tuco to Yoakum 345kV line | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 4.9895 | 6.9361 | 6836.0748 | 198.13 | 233.2 | FAIL | PASS

## WSCR
Study Name | Group | Season | Contingency | WSCR | WSCR PASS/FAIL | WSCR POI Group | POI 1 | POI 1 Gen Number | POI 2 | POI 2 Gen Number | POI 3 | POI 3 Gen Number | POI 4 | POI 4 Gen Number | POI 5 | POI 5 Gen Number
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 2.6146 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 2.8149 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 3.6741 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 4.3506 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764555 [GEN-2020-087345.00] CKT 1 | 6.0225 | PASS | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 2.4614 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 2.647 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 6.5216 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 764540 [GEN-2020-075345.00] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 2.4578 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 3.6712 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 4.3464 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 4.4245 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 5.0218 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 764550 [G20-075-TAP 345.00] TO BUS 511409 [TREASILD7 345.00] CKT 1 | 7.6253 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 3.4483 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 3.6832 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 4.0366 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 4.1438 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 4.3639 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 4.4412 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 6.3404 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 7.4477 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763516 [GEN-2019-011345.00] TO BUS 763517 [G19-011-XFM134.500] CKT 1 | 7.6273 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 2.4613 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 2.615 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 3.4383 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 3.6748 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 4.0204 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 4.3518 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 4.4291 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763605 [G19-021-XFM134.500] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 2.4616 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 2.6165 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 2.6472 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 3.4387 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 3.677 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 4.0211 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 4.3539 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 4.4322 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763483 [GEN-2019-003230.00] TO BUS 763484 [G19-003-XFM134.500] CKT 1 | 7.6281 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 2.4613 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 2.6469 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 4.0203 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 6.5215 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763322 [G18-115-XFM234.500] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 2.4613 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 2.6469 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 4.0203 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 6.5215 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 763318 [GEN-2018-115345.00] TO BUS 763319 [G18-115-XFM134.500] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 2.4606 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 3.0352 | FAIL | Group Number 14 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 3.4371 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 3.6759 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 4.0187 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 4.3521 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 4.4306 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 4.8562 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 6.5255 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762467 [G18-015-TAP 345.00] TO BUS 762460 [GEN-2018-015345.00] CKT 1 | 7.6272 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762467 [G18-015-TAP 345.00] CKT 1 | 2.5764 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 2.4642 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 3.6802 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 4.3591 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 4.4368 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762216 [G17-151TAP 345.00] TO BUS 762217 [GEN-2017-151345.00] CKT 1 | 7.6274 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 2.4625 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 2.6483 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 3.4403 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 3.6769 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 4.0237 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 4.3538 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 4.4321 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 5.0255 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763255 [G18-099-XFM234.500] CKT 1 | 7.6275 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 2.4626 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 2.6483 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 3.4403 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 3.6769 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 4.0237 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 4.3538 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 4.4322 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 5.0255 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 763252 [G18-099-XFM134.500] CKT 1 | 7.6275 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 2.4625 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 2.6482 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 3.4401 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 3.6768 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 4.0234 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 4.3536 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 4.432 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 5.0257 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762136 [G17-158XFM2 34.500] CKT 1 | 7.6281 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 2.4625 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 2.6482 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 3.4401 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 3.6768 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 4.0234 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 4.3536 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 4.432 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 5.0256 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 762132 [GEN-2017-158230.00] TO BUS 762133 [G17-158XFM1 34.500] CKT 1 | 7.628 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 2.4613 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 3.1429 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 3.4383 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 6.5215 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 760939 [GEN-2017-171345.00] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 2.4571 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 2.6125 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 2.8126 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 760938 [G17-171-TAP 345.00] TO BUS 511568 [TERRYRD7 345.00] CKT 1 | 3.6707 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661104 [LEWIS72G 13.800] CKT 1 | 5.6863 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661055 [LEWIS71G 13.800] CKT 1 | 5.6406 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 5.611 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 5.6644 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT 1 | 5.5005 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT 1 | 5.5529 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 655957 [EASTFORK-MW7115.00] TO BUS 659601 [EASTFORKTERT13.800] CKT 1 | 5.6473 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 4.4999 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 4.5418 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 4.7152 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 13.5112 | PASS | Group Number 18 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659393 [PG.KU19A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 2 | 5.6207 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659393 [PG.KU19A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 2 | 5.6735 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659392 [PG.KU17A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 5.6209 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659392 [PG.KU17A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 5.6737 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 1 | 5.6207 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 1 | 5.6734 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 5.6209 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 5.6737 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 2 | 5.603 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 2 | 5.6565 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 5.5951 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 5.6492 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 5.3398 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655889 [LC_GAS_P-MK7115.00] CKT 1 | 5.6459 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655889 [LC_GAS_P-MK7115.00] CKT 1 | 5.7002 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655856 [STNJOHNY-MK7115.00] CKT 1 | 5.6323 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655856 [STNJOHNY-MK7115.00] CKT 1 | 5.6844 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655844 [TIMBERCK-MK7115.00] CKT 1 | 5.6408 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655844 [TIMBERCK-MK7115.00] CKT 1 | 5.6936 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655899 [FNCYBTAP-MK7115.00] CKT 1 | 5.6481 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655899 [FNCYBTAP-MK7115.00] CKT 1 | 5.7015 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655882 [GALAXYTP-MK7115.00] CKT 1 | 5.6384 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655882 [GALAXYTP-MK7115.00] CKT 1 | 5.6913 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655881 [DAP_____-MK7115.00] CKT 1 | 5.6477 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655881 [DAP_____-MK7115.00] CKT 1 | 5.7012 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655873 [BBCOMPTP-MK7115.00] CKT 1 | 5.6317 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655873 [BBCOMPTP-MK7115.00] CKT 1 | 5.6834 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655849 [VEEDER -MK7115.00] CKT 1 | 5.6337 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655849 [VEEDER -MK7115.00] CKT 1 | 5.6859 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 5.1753 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 5.2181 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659394 [KR.KU6A_-BE913.800] CKT 2 | 5.6522 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659394 [KR.KU6A_-BE913.800] CKT 2 | 5.7061 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659394 [KR.KU6A_-BE913.800] CKT 2 | 13.5665 | PASS | Group Number 18 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659389 [KR.KU4A_-BE913.800] CKT 1 | 5.6522 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659389 [KR.KU4A_-BE913.800] CKT 1 | 5.7061 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659389 [KR.KU4A_-BE913.800] CKT 1 | 13.5665 | PASS | Group Number 18 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 5.2288 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 5.2849 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 5.6394 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 5.6928 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659600 [EFORK_-BE334345.00] CKT 1 | 5.4334 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 4.7739 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659334 [JUDSON__-BE4230.00] TO BUS 659335 [JDS.KU6A-BE913.800] CKT 1 | 5.4103 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659334 [JUDSON__-BE4230.00] TO BUS 659335 [JDS.KU6A-BE913.800] CKT 1 | 5.4615 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659302 [CHARL_CK-BE4230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 5.6365 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659302 [CHARL_CK-BE4230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 5.6866 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659269 [CULB_GEN-BE7115.00] CKT 1 | 5.6704 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659112 [CULBRTSN-UM7115.00] CKT 1 | 5.65 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659112 [CULBRTSN-UM7115.00] CKT 1 | 5.7031 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659186 [E.SIDNEY-LY7115.00] TO BUS 659180 [KOCH_OIL-BE7115.00] CKT 1 | 5.6056 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659186 [E.SIDNEY-LY7115.00] TO BUS 659180 [KOCH_OIL-BE7115.00] CKT 1 | 5.659 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659186 [E.SIDNEY-LY7115.00] TO BUS 659180 [KOCH_OIL-BE7115.00] CKT 1 | 13.39 | PASS | Group Number 18 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 5.0639 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 5.1095 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 5.6484 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 5.7021 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 5.648 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 5.701 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 5.65 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 5.7033 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659185 [FOUREYES-RR7115.00] CKT 1 | 5.6495 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659185 [FOUREYES-RR7115.00] CKT 1 | 5.703 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659184 [ROUGHRDR-BE7115.00] CKT 1 | 5.6084 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659184 [ROUGHRDR-BE7115.00] CKT 1 | 5.6615 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 5.5951 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 5.6473 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 655833 [GRSYBTTP-MK7115.00] CKT 1 | 5.65 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 655833 [GRSYBTTP-MK7115.00] CKT 1 | 5.7034 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 652419 [KILDEER7 115.00] CKT 1 | 5.6155 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 652419 [KILDEER7 115.00] CKT 1 | 5.6692 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 5.5054 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 5.5616 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 659186 [E.SIDNEY-LY7115.00] CKT 1 | 5.6056 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 659186 [E.SIDNEY-LY7115.00] CKT 1 | 5.659 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 659186 [E.SIDNEY-LY7115.00] CKT 1 | 13.3899 | PASS | Group Number 18 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 5.4441 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 5.4982 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659433 [TRIPLEH__UA3345.00] CKT 1 | 5.7129 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT Z | 4.5087 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT Z | 4.5505 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 652806 [FTTHOM1-LNX3345.00] CKT 1 | 4.4479 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 652806 [FTTHOM1-LNX3345.00] CKT 1 | 4.4915 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 763703 [GEN-2019-037345.00] CKT 1 | 13.7084 | PASS | Group Number 18 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659424 [LO.LS-FT-BE3345.00] CKT Z | 4.6874 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659424 [LO.LS-FT-BE3345.00] CKT Z | 13.5103 | PASS | Group Number 18 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659422 [LO.LS-GR-BE3345.00] CKT Z | 5.6238 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659422 [LO.LS-GR-BE3345.00] CKT Z | 5.6824 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659422 [LO.LS-GR-BE3345.00] CKT Z | 13.6485 | PASS | Group Number 18 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659111 [LELAND_2-BEG20.000] CKT 1 | 5.6545 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 5.6347 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 5.6887 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 5.631 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 5.685 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 5.6039 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 5.6612 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 588210 [GEN-2016-130345.00] CKT 1 | 5.7048 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 5.6224 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 5.68 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 5.2805 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 5.3379 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 5.7017 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 13.554 | PASS | Group Number 18 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 5.6503 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 5.7037 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 5.6503 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 5.7037 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 5.6423 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 13.6909 | PASS | Group Number 18 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 5.4787 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 5.5335 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 5.6116 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 5.6128 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 5.6661 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 5.6128 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 5.6661 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 5.6113 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655926 [SW.WLSTN-MW7115.00] CKT 1 | 5.65 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655926 [SW.WLSTN-MW7115.00] CKT 1 | 5.7034 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655924 [STATELIN-MW7115.00] CKT 1 | 5.6284 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655924 [STATELIN-MW7115.00] CKT 1 | 5.6832 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 655792 [NOHLEY -LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 5.6493 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 655792 [NOHLEY -LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 5.7027 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 655791 [SPRINGLK-LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 5.6509 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 655791 [SPRINGLK-LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 5.7045 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 655790 [HELMUT -LY7115.00] TO BUS 659151 [RICHLAND-BE7115.00] CKT 1 | 5.6492 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 655790 [HELMUT -LY7115.00] TO BUS 659151 [RICHLAND-BE7115.00] CKT 1 | 5.7027 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 800121 [MAURINE 2 345.00] CKT 1 | 5.5802 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 800121 [MAURINE 2 345.00] CKT 1 | 5.6346 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 800121 [MAURINE 2 345.00] CKT 1 | 13.4468 | PASS | Group Number 18 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 5.4534 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 5.5006 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 5.6436 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 5.6967 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 5.6398 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 5.6927 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 659262 [CULBSN.E-BE7115.00] CKT 1 | 5.6188 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 659262 [CULBSN.E-BE7115.00] CKT 1 | 5.6747 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 5.628 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 5.6823 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655793 [MARLEY -LY7115.00] CKT 1 | 5.6495 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655793 [MARLEY -LY7115.00] CKT 1 | 5.7028 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 5.4523 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 5.5056 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659362 [WHEELOCK-BE4230.00] CKT 1 | 5.6252 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659362 [WHEELOCK-BE4230.00] CKT 1 | 5.6779 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659334 [JUDSON__-BE4230.00] CKT 1 | 5.4103 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659334 [JUDSON__-BE4230.00] CKT 1 | 5.4615 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652421 [WILISTN7 115.00] TO BUS 652621 [WILISTN9 13.200] CKT 1 | 5.6269 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652421 [WILISTN7 115.00] TO BUS 652621 [WILISTN9 13.200] CKT 1 | 5.68 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652403 [DAWSONC4 230.00] CKT 1 | 5.6028 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652403 [DAWSONC4 230.00] CKT 1 | 5.6547 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 5.6412 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 5.6959 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 13.5249 | PASS | Group Number 18 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 5.6487 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 5.7021 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 5.6454 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 5.6991 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 5.648 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 5.7022 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 5.6286 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 5.6833 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25SP | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 5.6271 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 5.6802 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 6.2415 | PASS | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 4.5478 | FAIL | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.3254 | FAIL | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.5766 | FAIL | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.045 | FAIL | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.7557 | FAIL | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 6.2248 | PASS | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 5.9617 | FAIL | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 6.2093 | PASS | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 6.4548 | PASS | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 5.8002 | FAIL | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 2.461 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 2.6155 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 3.4377 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 3.6755 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 4.0196 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 4.3515 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 4.4301 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588765 [G17-033XFMR234.500] CKT 1 | 7.6271 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 2.4609 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 2.6155 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 3.4377 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 3.6755 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 4.0195 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 4.3515 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 4.4301 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 588760 [GEN-2017-033345.00] TO BUS 588761 [G17-033XFMR134.500] CKT 1 | 7.6271 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.2957 | FAIL | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.4899 | FAIL | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 5.3058 | FAIL | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 5.5212 | FAIL | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 6.264 | PASS | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 6.3078 | PASS | Group Number 17 | Orleans-Holdrege Substation 115kV | GEN-2020-013 | Axtell-Sweetwater Substation 345kV | GEN-2020-011
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 2.4588 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 2.6441 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 3.4343 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 3.6709 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 4.0183 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 4.3494 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 4.4236 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 6.511 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528025 [RDRUNNER 3115.00] TO BUS 528023 [RDRNNER_TR1113.200] CKT 1 | 7.6249 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 2.4571 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 2.6423 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 3.4315 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 3.6688 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 4.0159 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 4.3476 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 4.4204 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 4.8468 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 5.0154 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 528027 [RDRUNNER 7345.00] TO BUS 528015 [PHANTOM 7345.00] CKT 1 | 7.6269 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 2.4584 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 3.1387 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 3.4335 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 3.6704 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 4.3482 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 4.4228 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 6.5122 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528185 [N_LOVING 7345.00] CKT 1 | 7.6258 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 2.4599 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 2.6453 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 3.4362 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 3.6726 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.0193 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.3504 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.426 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 6.515 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 7.6231 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 2.46 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 3.4362 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 3.6723 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 4.0193 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 4.3502 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 4.4256 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 5.0194 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527966 [KIOWA 3115.00] TO BUS 527964 [KIOWA_TR1 113.200] CKT 1 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 2.4584 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 3.4356 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 3.6717 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 4.3503 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 4.4247 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 6.5039 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 7.5999 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 1.9396 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 2.5901 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 2.8128 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 3.8106 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 6.0079 | PASS | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 2.4596 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 2.6451 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 3.4356 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 3.6717 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 4.0188 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 4.3497 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 4.4247 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 6.5138 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 2 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 2.4596 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 2.6451 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 3.4356 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 3.6717 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.0188 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.3497 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 4.4247 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 6.5138 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 2.4559 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 2.6409 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 3.4298 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 3.6668 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 4.0161 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 4.3474 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 4.4176 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 4.8418 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 5.0101 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1 | 7.6226 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 2.4529 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 2.6061 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 3.0241 | FAIL | Group Number 14 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 3.4253 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 4.0179 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 4.4094 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 5.8028 | FAIL | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527903 [HOBBS_PLT3 118.000] CKT 1 | 7.6173 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 2.4313 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 2.6139 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 3.3901 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 3.6272 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 4.001 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 4.3333 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 4.3609 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 4.7691 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 6.3659 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527896 [HOBBS_INT 7345.00] TO BUS 527895 [HOBBS_TR3 113.200] CKT 1 | 7.6212 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 2.46 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 3.4363 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 3.6724 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 4.0191 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 4.35 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 4.4257 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 5.0198 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527890 [HOBBS_TR1 113.200] CKT 1 | 7.6245 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 2.4593 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 3.4352 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 3.6712 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 4.0185 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 4.3494 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 4.424 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 5.0178 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527891 [HOBBS_INT 3115.00] TO BUS 527889 [HOBBS_TR2 113.200] CKT 2 | 7.624 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 2.4525 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 3.424 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 3.6616 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 4.0097 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 4.3418 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 4.4104 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 6.4912 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527867 [CUNNIGHM_S 6230.00] CKT 1 | 7.6237 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 2.4522 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 3.4236 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 3.6627 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 3.9989 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 4.3336 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 4.4127 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 5.0199 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 6.019 | PASS | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 2.4555 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 2.6406 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 3.4294 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 3.6648 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 4.0174 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 4.3477 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 4.4147 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 6.4874 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 2 | 7.6193 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 2.4555 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 2.6406 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 3.4294 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 3.6648 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 4.0174 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 4.3477 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 4.4147 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 6.4874 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527896 [HOBBS_INT 7345.00] CKT 1 | 7.6193 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 3.4383 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 3.6753 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 4.0205 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 4.3518 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 4.4298 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 6.5231 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527802 [EDDY_CNTY 7345.00] CKT 1 | 7.6251 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 2.4583 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 2.6436 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 3.4337 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 3.6715 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 4.0154 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 4.3474 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 4.4243 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 5.0212 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527669 [CROSSROADS 9765.00] TO BUS 527668 [CROSSROADTR113.200] CKT 1 | 7.6226 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 2.4508 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 2.6355 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 3.4231 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 3.6619 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 4.0122 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 4.3443 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 4.411 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 4.9995 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527655 [RSVLT_CC_E 7345.00] CKT 1 | 7.6064 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 2.4677 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 3.6813 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 4.3599 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 4.4384 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527656 [CROSSROADS 7345.00] TO BUS 527610 [SAGA_SCOL 7345.00] CKT 1 | 7.6287 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 2.4382 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 3.437 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 3.6738 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 4.0198 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 4.4277 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 4.9353 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527799 [EDDY_NORTH 6230.00] CKT 1 | 7.1451 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 2.4611 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 3.6745 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 4.3512 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 4.4288 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 6.521 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527479 [CHAVES_TR2 113.200] CKT 2 | 7.6232 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 2.4611 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 3.6745 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 4.3512 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 4.4288 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 6.521 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527483 [CHAVES_CNTY6230.00] TO BUS 527482 [CHAVES_CNTY3115.00] TO BUS 527478 [CHAVES_TR1 113.200] CKT 1 | 7.6233 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 2.4602 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 3.4365 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 3.6729 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 4.0197 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 4.3506 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 4.4265 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 6.5164 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 528604 [ANDREWS 6345.00] CKT 1 | 7.6256 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 2.3962 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 527020 [SIDEWINDER 7345.00] TO BUS 527000 [GAINES_PLNT7345.00] CKT 1 | 2.5493 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 1.8457 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.2447 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.517 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 4.6272 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 4.7719 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 6.0936 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 7.4071 | PASS | Group Number 11 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 2.0273 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 3.4689 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 3.802 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 4.7997 | FAIL | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 4.8711 | FAIL | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 5.7961 | FAIL | Group Number 11 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 764866 [G20-059-TAP 345.00] CKT 1 | 7.6258 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 3.4483 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 3.6832 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 4.0366 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 4.1438 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 4.3639 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 4.4412 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 6.3404 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 7.4477 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526936 [YOAKUM_345 345.00] TO BUS 763516 [GEN-2019-011345.00] CKT 1 | 7.6273 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 2.447 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 3.4154 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 3.6483 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 3.9967 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 4.3243 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 4.3917 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 4.9988 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527149 [MUSTANG 6230.00] CKT 1 | 7.6203 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 2.4439 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 3.4102 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 3.6515 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 3.9845 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 4.3207 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 4.3967 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 5.0119 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527028 [INK_BASIN 6230.00] CKT 1 | 7.6241 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 2.4456 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 3.4133 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 3.6457 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 3.9946 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 4.3215 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 4.3881 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 4.9965 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 527009 [BRU_SUB 6230.00] CKT 1 | 7.6197 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 2.1209 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 2.2707 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 2.8849 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 3.0862 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 3.4542 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 3.5825 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 3.741 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 4.3849 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 6.0211 | PASS | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526936 [YOAKUM_345 345.00] TO BUS 526937 [YOAKUM_TR1 13.200] CKT 1 | 7.6247 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 2.4591 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 2.6122 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 3.2327 | FAIL | Group Number 14 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 3.4347 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 4.347 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526932 [YOAKUM_TR2 113.200] CKT 2 | 6.0217 | PASS | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 2.4591 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 2.6122 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 3.2327 | FAIL | Group Number 14 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 3.4347 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 4.347 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526934 [YOAKUM 3115.00] TO BUS 526931 [YOAKUM_TR1 113.200] CKT 1 | 6.0217 | PASS | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 2.4477 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 3.0232 | FAIL | Group Number 14 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 3.417 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 3.6509 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 3.9994 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 4.3272 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 4.4051 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 6.4821 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526935 [YOAKUM 6230.00] TO BUS 526460 [AMOCO_SS 6230.00] CKT 1 | 7.616 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 2.4621 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 3.0371 | FAIL | Group Number 14 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 3.4395 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 3.6753 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 4.0224 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 4.3525 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 4.4294 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 4.8571 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 5.0238 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526679 [CIRRUS_WND 6230.00] CKT 1 | 7.6256 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 2.4614 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 2.6471 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 3.4385 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 3.6759 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 4.0207 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 4.3533 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 4.4292 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 6.522 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1 | 7.6257 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 2.462 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 3.4394 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 3.6762 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 4.0222 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 4.3539 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 4.4292 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 6.5219 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1 | 7.6257 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 2.1937 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 2.7918 | FAIL | Group Number 12 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 3.0032 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 3.3272 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 4.4279 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 6.5211 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526299 [LUBBCK_EST 6230.00] CKT 1 | 7.6248 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 2.4246 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 2.5837 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 3.0243 | FAIL | Group Number 14 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 3.3793 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 3.9313 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.4196 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.7372 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526334 [JONES_4 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 7.6209 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 2.4255 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 2.5838 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 3.0247 | FAIL | Group Number 14 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 3.3808 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 3.9335 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.4196 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.7399 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526333 [JONES_3 116.500] TO BUS 526337 [JONES 6230.00] CKT 1 | 7.621 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526332 [JONES_2 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 2.4182 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526332 [JONES_2 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 2.577 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526332 [JONES_2 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.417 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526332 [JONES_2 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 7.6195 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526331 [JONES_1 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 2.5756 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526331 [JONES_1 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 3.3658 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526331 [JONES_1 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 3.9108 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526331 [JONES_1 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.1067 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526331 [JONES_1 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.4163 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526331 [JONES_1 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 6.3209 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526331 [JONES_1 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 7.4347 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526331 [JONES_1 122.000] TO BUS 526337 [JONES 6230.00] CKT 1 | 7.6192 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 2.4607 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 3.1421 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 3.4373 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 3.6734 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 4.3496 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 4.4279 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 5.0218 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526562 [SLATON 269.000] CKT 1 | 7.6253 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 2.4602 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 3.1413 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 3.4365 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 3.6738 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 4.3501 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 4.4282 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 5.0222 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526310 [CLUTTER 269.000] CKT 1 | 7.6253 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 2.46 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 3.6712 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 4.3461 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 4.4262 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 6.5209 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526297 [LUBBCK_EST 269.000] TO BUS 526284 [PLANTERS 269.000] CKT 1 | 7.625 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526296 [LBB_EST TR3113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 2 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526296 [LBB_EST TR3113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 2 | 2.6468 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526296 [LBB_EST TR3113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 2 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526296 [LBB_EST TR3113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 2 | 3.6746 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526296 [LBB_EST TR3113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 2 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526296 [LBB_EST TR3113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 2 | 4.3515 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526296 [LBB_EST TR3113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 2 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526296 [LBB_EST TR3113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 2 | 6.5215 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526296 [LBB_EST TR3113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 2 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526295 [LBB_EST TR2113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526295 [LBB_EST TR2113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 1 | 2.6468 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526295 [LBB_EST TR2113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526295 [LBB_EST TR2113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 1 | 3.6746 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526295 [LBB_EST TR2113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526295 [LBB_EST TR2113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 1 | 4.3515 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526295 [LBB_EST TR2113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526295 [LBB_EST TR2113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 1 | 6.5215 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526295 [LBB_EST TR2113.200] TO BUS 526298 [LUBBCK_EST 3115.00] TO BUS 526297 [LUBBCK_EST 269.000] CKT 1 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 2.4361 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 2.6191 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 3.3974 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 3.63 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 3.9554 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.2804 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.4275 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.7628 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.9195 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526294 [LBB_EST TR1113.200] TO BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 7.6249 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 2.4249 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 3.3801 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 3.6109 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 3.9325 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 4.417 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 6.5071 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526525 [WOLFFORTH 6230.00] CKT 1 | 7.6141 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 2 | 2.4589 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 2 | 3.4345 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 2 | 3.6705 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 2 | 4.0148 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 2 | 4.3451 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 2 | 4.4277 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 2 | 6.5204 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 2 | 7.6246 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 2.4589 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 3.4345 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 3.6705 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.0148 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.3451 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.4277 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 6.5204 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 7.6246 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 2.4613 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 3.675 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 4.0204 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 4.3521 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 6.5213 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526602 [WOODROW 3115.00] CKT 1 | 7.6253 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 2.4586 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 3.4339 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 3.6703 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.0136 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.3446 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.4282 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 5.0139 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 7.6252 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 2.6468 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 3.6746 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 4.3514 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 6.5216 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526265 [LBB_STH TR1113.200] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 3.6746 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 4.0203 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 4.3514 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 6.5215 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526269 [LUBBCK_STH 6230.00] TO BUS 526264 [LBB_STH TR3113.200] CKT 2 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 2.4603 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 3.6726 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 4.3483 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 4.4272 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 6.5212 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526267 [LUBBCK_STH 269.000] TO BUS 526266 [LBB_STH TR2113.200] CKT 1 | 7.6252 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 2.4574 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 3.0351 | FAIL | Group Number 14 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 3.432 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 3.6671 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 4.0108 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 4.3393 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 4.4283 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 4.8435 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 6.5219 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526268 [LUBBCK_STH 3115.00] TO BUS 526213 [ALLEN 3115.00] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 2.4544 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 2.6449 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 3.4362 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 3.6725 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 4.0177 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 4.3486 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 4.4267 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 6.4801 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526036 [LC-OPDYKE 3115.00] CKT 1 | 7.5026 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 6.5214 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526018 [HOCKLEY_TR2113.200] CKT 2 | 7.6252 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 6.5214 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 526020 [HOCKLEY 3115.00] TO BUS 526019 [HOCKLEY 269.000] TO BUS 526017 [HOCKLEY_TR1113.200] CKT 1 | 7.6252 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 2.4577 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 3.4325 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 3.6681 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.0112 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.341 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.4287 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 6.5216 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 7.625 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 6.5214 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525924 [CROSBY_TR2 113.200] CKT 2 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 6.5214 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525925 [CROSBY 269.000] TO BUS 525923 [CROSBY_TR1 113.200] CKT 1 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 2.4576 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 3.4324 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 3.6682 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 4.0112 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 4.3412 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 4.4282 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 5.0085 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525926 [CROSBY 3115.00] TO BUS 525803 [BLANCO 3115.00] CKT 1 | 7.6242 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 3.6163 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 4.2661 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 4.352 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525845 [ELK_2 1 18.000] CKT 1 | 7.6183 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 3.6117 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 4.2594 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 4.3459 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525850 [ELK_CT1 345.00] TO BUS 525844 [ELK_1 118.000] CKT 1 | 7.6177 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 1.8824 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.0352 | FAIL | Group Number 12 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.0672 | FAIL | Group Number 12 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.1105 | FAIL | Group Number 13 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.7894 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 764945 [G20-067-TAP 345.00] CKT 1 | 2.8264 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 762216 [G17-151TAP 345.00] CKT 1 | 2.4118 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 762216 [G17-151TAP 345.00] CKT 1 | 2.5838 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 525850 [ELK_CT1 345.00] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 525850 [ELK_CT1 345.00] CKT 1 | 2.5314 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 525850 [ELK_CT1 345.00] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 525850 [ELK_CT1 345.00] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525832 [TUCO_INT 7345.00] TO BUS 525850 [ELK_CT1 345.00] CKT 1 | 7.6069 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 2.4031 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 3.3446 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 3.5885 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.2178 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.3881 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 4.8797 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1 | 5.7237 | FAIL | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 2.4471 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 3.1226 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 3.4154 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 3.658 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 4.3252 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 4.4155 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 5.0055 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 526161 [CARLISLE 6230.00] CKT 1 | 7.6253 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 2.4646 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 2.6182 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 2.6506 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 3.4436 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 4.0285 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 4.3581 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 4.4356 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 4.8588 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 6.5265 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525957 [HALE_WNDCL16230.00] CKT 1 | 7.6278 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 3.6503 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 4.3153 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 4.4021 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 5.0042 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525840 [ANTELOPE_1 6230.00] CKT 1 | 7.6187 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 2.4604 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 3.4368 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 3.6739 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 4.3503 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 4.4279 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 6.5215 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525820 [TUCO_SVC 113.000] CKT 1 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 2.4334 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 2.5977 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 2.6162 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 4.3984 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 6.5161 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525830 [TUCO_INT 6230.00] TO BUS 525213 [SWISHER 6230.00] CKT 1 | 7.6216 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 2.4492 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 2.6336 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 3.4188 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 3.6542 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 3.9902 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.3194 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.425 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 4.8196 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 6.5199 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526298 [LUBBCK_EST 3115.00] CKT 1 | 7.6242 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 2.4604 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 3.4369 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 3.6736 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 4.0183 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 4.3498 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 4.4279 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 6.5215 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 526076 [STANTON_W 3115.00] CKT 1 | 7.6252 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 2.4577 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 2.643 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 3.4325 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 3.6703 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 4.0118 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 4.3448 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 4.425 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 6.5209 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525821 [TUCO_TR4 113.200] CKT 1 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 2.4579 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 2.6124 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 2.6432 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 3.4328 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 4.0122 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 4.345 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 4.4251 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 6.5208 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525830 [TUCO_INT 6230.00] TO BUS 525819 [TUCO_TR3 113.200] CKT 2 | 7.6252 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 3.6743 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525823 [TUCO_TR6 113.200] CKT 1 | 7.6253 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 3.6743 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525826 [TUCO_INT 269.000] TO BUS 525822 [TUCO_TR5 113.200] CKT 2 | 7.6253 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 2.4608 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 3.1423 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 3.4375 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 3.6734 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 4.3496 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 4.4275 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 6.521 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525816 [TUCO_INT2 269.000] TO BUS 525814 [TUCO_TR7 113.200] CKT 1 | 7.625 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 2.4602 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 3.4365 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 3.6736 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 4.0178 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 4.3499 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 4.4272 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 6.5212 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525780 [FLOYD_CNTY 3115.00] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 2.456 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 3.43 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 3.6689 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 4.3425 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 4.4247 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 6.5191 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525828 [TUCO_INT 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 7.6192 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525825 [TUCO_TR2 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 2 | 2.4224 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525825 [TUCO_TR2 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 2 | 2.604 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525825 [TUCO_TR2 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 2 | 3.6257 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525825 [TUCO_TR2 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 2 | 4.2766 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525825 [TUCO_TR2 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 2 | 4.3665 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525825 [TUCO_TR2 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 2 | 5.0046 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525825 [TUCO_TR2 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 2 | 5.9923 | FAIL | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525824 [TUCO_TR1 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 2.4122 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525824 [TUCO_TR1 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 3.3587 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525824 [TUCO_TR1 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 3.6131 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525824 [TUCO_TR1 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 4.2574 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525824 [TUCO_TR1 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 4.3506 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525824 [TUCO_TR1 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 4.9997 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525824 [TUCO_TR1 113.200] TO BUS 525832 [TUCO_INT 7345.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 5.9844 | FAIL | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525636 [LAMB_CNTY 3115.00] TO BUS 526020 [HOCKLEY 3115.00] CKT 1 | 2.4545 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525636 [LAMB_CNTY 3115.00] TO BUS 526020 [HOCKLEY 3115.00] CKT 1 | 2.6451 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525636 [LAMB_CNTY 3115.00] TO BUS 526020 [HOCKLEY 3115.00] CKT 1 | 3.4365 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525636 [LAMB_CNTY 3115.00] TO BUS 526020 [HOCKLEY 3115.00] CKT 1 | 3.6734 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525636 [LAMB_CNTY 3115.00] TO BUS 526020 [HOCKLEY 3115.00] CKT 1 | 4.018 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525636 [LAMB_CNTY 3115.00] TO BUS 526020 [HOCKLEY 3115.00] CKT 1 | 4.3497 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525636 [LAMB_CNTY 3115.00] TO BUS 526020 [HOCKLEY 3115.00] CKT 1 | 4.4276 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525636 [LAMB_CNTY 3115.00] TO BUS 526020 [HOCKLEY 3115.00] CKT 1 | 4.8324 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525636 [LAMB_CNTY 3115.00] TO BUS 526020 [HOCKLEY 3115.00] CKT 1 | 6.4794 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525636 [LAMB_CNTY 3115.00] TO BUS 526020 [HOCKLEY 3115.00] CKT 1 | 7.4975 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 2.4611 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 3.1427 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 3.674 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 4.3506 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 4.4281 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 5.0227 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525687 [LC-LUMSCHAP269.000] CKT 1 | 7.6243 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 2.4608 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 3.1423 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 3.4376 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 3.6737 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 4.3502 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 4.4277 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 5.0223 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525650 [LC-LTTLFLD+269.000] CKT 1 | 6.0212 | PASS | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 2.4611 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 3.1427 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 3.6741 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 4.3506 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 4.4281 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 5.0228 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525620 [LTFLD_S&CTY269.000] CKT 1 | 7.6245 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 2.4609 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 3.1423 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 3.4377 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 3.6737 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 4.3501 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 4.4276 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 5.0223 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525635 [LAMB_CNTY 269.000] TO BUS 525613 [W_LITTLFLD 269.000] CKT 1 | 7.6231 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 2.4441 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 3.4376 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 3.6746 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 4.0192 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 4.4289 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 6.3992 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525633 [LAMB_TR3 113.200] TO BUS 525637 [LAMB_CNTY 6230.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 7.2452 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525632 [LAMB_TR2 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 2 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525632 [LAMB_TR2 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 2 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525632 [LAMB_TR2 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 2 | 3.6743 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525632 [LAMB_TR2 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 2 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525632 [LAMB_TR2 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 2 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525632 [LAMB_TR2 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 2 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525632 [LAMB_TR2 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 2 | 6.5213 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525632 [LAMB_TR2 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 2 | 7.6251 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525631 [LAMB_TR1 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525631 [LAMB_TR1 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525631 [LAMB_TR1 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 1 | 3.6743 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525631 [LAMB_TR1 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525631 [LAMB_TR1 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 1 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525631 [LAMB_TR1 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 1 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525631 [LAMB_TR1 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 1 | 6.5213 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525631 [LAMB_TR1 113.200] TO BUS 525636 [LAMB_CNTY 3115.00] TO BUS 525635 [LAMB_CNTY 269.000] CKT 1 | 7.6251 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 526935 [YOAKUM 6230.00] CKT 1 | 2.449 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 526935 [YOAKUM 6230.00] CKT 1 | 3.4217 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 526935 [YOAKUM 6230.00] CKT 1 | 3.6583 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 526935 [YOAKUM 6230.00] CKT 1 | 4.3348 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 526935 [YOAKUM 6230.00] CKT 1 | 4.4053 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 526935 [YOAKUM 6230.00] CKT 1 | 6.4812 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 526935 [YOAKUM 6230.00] CKT 1 | 7.579 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 2.4602 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 2.6458 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 3.4376 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 3.6749 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 4.0208 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 4.3517 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 4.4295 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 5.021 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525586 [NEEDMORE 6230.00] TO BUS 525585 [BLUECLDPOI 6230.00] CKT Z1 | 7.6137 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 527656 [CROSSROADS 7345.00] CKT 1 | 2.4474 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 527656 [CROSSROADS 7345.00] CKT 1 | 2.6326 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 527656 [CROSSROADS 7345.00] CKT 1 | 3.4225 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 527656 [CROSSROADS 7345.00] CKT 1 | 3.6577 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 527656 [CROSSROADS 7345.00] CKT 1 | 4.017 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 527656 [CROSSROADS 7345.00] CKT 1 | 4.3475 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 527656 [CROSSROADS 7345.00] CKT 1 | 4.4052 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 527656 [CROSSROADS 7345.00] CKT 1 | 5.9868 | FAIL | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 527656 [CROSSROADS 7345.00] CKT 1 | 7.5389 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 2.4562 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 2.6111 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 2.8115 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 3.6721 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525549 [TOLK 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 5.0153 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 762132 [GEN-2017-158230.00] CKT 1 | 2.4662 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 762132 [GEN-2017-158230.00] CKT 1 | 2.6186 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 762132 [GEN-2017-158230.00] CKT 1 | 4.4368 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 762132 [GEN-2017-158230.00] CKT 1 | 6.5265 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 762132 [GEN-2017-158230.00] CKT 1 | 7.6303 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 2.4248 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 3.3839 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 3.6429 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 3.9361 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 4.3014 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 4.3965 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 6.4938 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525830 [TUCO_INT 6230.00] CKT 1 | 7.544 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 2.4141 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 2.6465 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 3.4377 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 3.6745 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 4.0194 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 4.4289 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 5.4165 | FAIL | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1 | 7.9706 | PASS | Group Number 11 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525586 [NEEDMORE 6230.00] CKT 1 | 2.4513 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525586 [NEEDMORE 6230.00] CKT 1 | 2.6364 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525586 [NEEDMORE 6230.00] CKT 1 | 3.4268 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525586 [NEEDMORE 6230.00] CKT 1 | 3.6631 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525586 [NEEDMORE 6230.00] CKT 1 | 4.0091 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525586 [NEEDMORE 6230.00] CKT 1 | 4.3396 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525586 [NEEDMORE 6230.00] CKT 1 | 4.4123 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525586 [NEEDMORE 6230.00] CKT 1 | 6.4834 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525586 [NEEDMORE 6230.00] CKT 1 | 7.5626 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525562 [TOLK_2 124.000] CKT 1 | 2.4273 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525562 [TOLK_2 124.000] CKT 1 | 2.5959 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525562 [TOLK_2 124.000] CKT 1 | 3.4054 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525561 [TOLK_1 124.000] CKT 1 | 2.5928 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525561 [TOLK_1 124.000] CKT 1 | 3.4176 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525561 [TOLK_1 124.000] CKT 1 | 4.0007 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525561 [TOLK_1 124.000] CKT 1 | 4.1048 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525561 [TOLK_1 124.000] CKT 1 | 4.408 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525561 [TOLK_1 124.000] CKT 1 | 4.7787 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525561 [TOLK_1 124.000] CKT 1 | 5.6832 | FAIL | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525561 [TOLK_1 124.000] CKT 1 | 6.4138 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525561 [TOLK_1 124.000] CKT 1 | 7.3741 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525538 [TOLK_TR 2 113.200] CKT 2 | 2.4583 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525538 [TOLK_TR 2 113.200] CKT 2 | 2.644 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525538 [TOLK_TR 2 113.200] CKT 2 | 3.4361 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525538 [TOLK_TR 2 113.200] CKT 2 | 3.6733 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525538 [TOLK_TR 2 113.200] CKT 2 | 4.0199 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525538 [TOLK_TR 2 113.200] CKT 2 | 4.3514 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525538 [TOLK_TR 2 113.200] CKT 2 | 4.4272 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525538 [TOLK_TR 2 113.200] CKT 2 | 4.8452 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525538 [TOLK_TR 2 113.200] CKT 2 | 5.0137 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525538 [TOLK_TR 2 113.200] CKT 2 | 7.5915 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525537 [TOLK_TR 113.200] CKT 1 | 2.4581 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525537 [TOLK_TR 113.200] CKT 1 | 2.6438 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525537 [TOLK_TR 113.200] CKT 1 | 3.436 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525537 [TOLK_TR 113.200] CKT 1 | 3.6731 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525537 [TOLK_TR 113.200] CKT 1 | 4.0199 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525537 [TOLK_TR 113.200] CKT 1 | 4.3513 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525537 [TOLK_TR 113.200] CKT 1 | 4.4269 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525537 [TOLK_TR 113.200] CKT 1 | 4.8443 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525537 [TOLK_TR 113.200] CKT 1 | 5.0128 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525531 [TOLK 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525537 [TOLK_TR 113.200] CKT 1 | 7.5886 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 2.4594 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 2.6451 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 3.6725 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 4.3483 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 4.4261 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 5.0203 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 760498 [G17-146-TAP 230.00] CKT 1 | 6.0173 | PASS | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 2.4502 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 3.4231 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 3.6617 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 4.333 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 4.4191 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 6.5026 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 526435 [SUNDOWN 6230.00] CKT 1 | 7.5847 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.4599 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 3.4377 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 3.674 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 4.0196 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 4.3505 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 4.4283 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 6.5131 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 7.6002 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.46 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 3.4378 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 3.674 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 4.0196 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 4.3506 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 4.4283 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 6.5135 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 7.6014 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 2.4488 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 2.6342 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 3.4265 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 3.6663 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 4.009 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 4.3421 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 4.4192 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 4.8194 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 4.9957 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525494 [PLANT_X4 120.000] CKT 1 | 7.5264 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 2.4586 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 3.1404 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 3.4357 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 3.6728 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 4.3485 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 4.4268 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 6.5123 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525481 [PLANT_X 6230.00] TO BUS 525461 [NEWHART 6230.00] CKT 1 | 7.5966 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 2.4532 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 3.438 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 3.5861 | FAIL | Group Number 15 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 3.6742 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 4.3509 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 4.4282 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 5.9534 | FAIL | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525636 [LAMB_CNTY 3115.00] CKT 1 | 6.4636 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 6.5215 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525493 [PLANT_X3 113.800] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 6.5215 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525492 [PLANT_X2 113.800] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 6.5215 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525491 [PLANT_X1 113.800] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 2.4595 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 2.6458 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 3.437 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 3.674 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 4.0184 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 4.3503 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 6.5152 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525481 [PLANT_X 6230.00] TO BUS 525479 [PLANTX_TR1 113.200] CKT 1 | 7.6049 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 2.4595 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 3.4363 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 3.673 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 4.0173 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 4.349 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 4.4277 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 6.5169 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525454 [HALE_CNTY 3115.00] CKT 1 | 7.6116 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 2.46 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 3.4372 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 3.6736 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 4.0188 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 4.3499 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 4.428 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525446 [RKYFORD_TP 3115.00] CKT 1 | 7.6101 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 2.4607 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 3.438 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 3.6743 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 4.02 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 4.3509 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 4.4284 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 5.0211 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525056 [BC-EARTH 3115.00] CKT 1 | 7.6149 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 2.4509 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 3.6745 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 4.0201 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 4.3512 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 4.4289 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 6.461 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 525480 [PLANT_X 3115.00] TO BUS 525019 [MULSHVLY_TP3115.00] CKT 1 | 7.4377 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 2.4613 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 6.5218 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524977 [GREYHOUND 3115.00] CKT 1 | 7.6263 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 6.5217 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524935 [KILGORE 3115.00] CKT 1 | 7.626 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 2.4611 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 5.0229 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524922 [PORTLES_TR2113.200] CKT 2 | 7.6247 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 5.023 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524924 [PORTALES 3115.00] TO BUS 524923 [PORTALES 269.000] TO BUS 524921 [PORTLES_TR1113.200] CKT 1 | 7.6249 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 763483 [GEN-2019-003230.00] CKT 1 | 2.4617 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 763483 [GEN-2019-003230.00] CKT 1 | 2.6168 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 763483 [GEN-2019-003230.00] CKT 1 | 3.1435 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 763483 [GEN-2019-003230.00] CKT 1 | 3.4389 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 763483 [GEN-2019-003230.00] CKT 1 | 3.6774 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 763483 [GEN-2019-003230.00] CKT 1 | 4.3546 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 763483 [GEN-2019-003230.00] CKT 1 | 4.4329 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 763483 [GEN-2019-003230.00] CKT 1 | 7.6281 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 2.3935 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 3.4386 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 3.6748 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 4.0207 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 4.3515 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 4.4291 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 4.7577 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 2 | 6.1452 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 2.3925 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 3.4386 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 3.6748 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 4.0207 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 4.3515 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 4.4291 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 4.7539 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 525531 [TOLK 6230.00] CKT 1 | 6.1239 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.3669 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 3.0909 | FAIL | Group Number 14 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.3512 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.6448 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524909 [ROOSEVELT 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 5.2041 | FAIL | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 2.4604 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 4.0203 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 5.0196 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 7.6057 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 2.4608 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 5.0201 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524908 [ROOSEVELT 3115.00] TO BUS 524822 [CURRY 3115.00] CKT 2 | 7.609 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524907 [ROSEVLT_TR1113.200] TO BUS 524909 [ROOSEVELT 6230.00] TO BUS 524908 [ROOSEVELT 3115.00] CKT 1 | 2.4617 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524907 [ROSEVLT_TR1113.200] TO BUS 524909 [ROOSEVELT 6230.00] TO BUS 524908 [ROOSEVELT 3115.00] CKT 1 | 2.6153 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524907 [ROSEVLT_TR1113.200] TO BUS 524909 [ROOSEVELT 6230.00] TO BUS 524908 [ROOSEVELT 3115.00] CKT 1 | 3.2373 | FAIL | Group Number 14 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524907 [ROSEVLT_TR1113.200] TO BUS 524909 [ROOSEVELT 6230.00] TO BUS 524908 [ROOSEVELT 3115.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524907 [ROSEVLT_TR1113.200] TO BUS 524909 [ROOSEVELT 6230.00] TO BUS 524908 [ROOSEVELT 3115.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524907 [ROSEVLT_TR1113.200] TO BUS 524909 [ROOSEVELT 6230.00] TO BUS 524908 [ROOSEVELT 3115.00] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524907 [ROSEVLT_TR1113.200] TO BUS 524909 [ROOSEVELT 6230.00] TO BUS 524908 [ROOSEVELT 3115.00] CKT 1 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524907 [ROSEVLT_TR1113.200] TO BUS 524909 [ROOSEVELT 6230.00] TO BUS 524908 [ROOSEVELT 3115.00] CKT 1 | 7.6373 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 2.4617 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 3.4384 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 3.6746 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 4.0205 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 4.3513 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 4.4288 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 6.5244 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524889 [SN_JUAN_WND6230.00] TO BUS 524886 [SNJN-CB1 134.500] CKT 1 | 7.6338 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 527483 [CHAVES_CNTY6230.00] CKT 1 | 2.4198 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 527483 [CHAVES_CNTY6230.00] CKT 1 | 2.6013 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 527483 [CHAVES_CNTY6230.00] CKT 1 | 3.4372 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 527483 [CHAVES_CNTY6230.00] CKT 1 | 3.6733 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 527483 [CHAVES_CNTY6230.00] CKT 1 | 4.0206 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 527483 [CHAVES_CNTY6230.00] CKT 1 | 4.3515 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 527483 [CHAVES_CNTY6230.00] CKT 1 | 4.4271 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 527483 [CHAVES_CNTY6230.00] CKT 1 | 6.7363 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524889 [SN_JUAN_WND6230.00] CKT 1 | 2.4618 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524889 [SN_JUAN_WND6230.00] CKT 1 | 3.4384 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524889 [SN_JUAN_WND6230.00] CKT 1 | 3.6746 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524889 [SN_JUAN_WND6230.00] CKT 1 | 4.0205 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524889 [SN_JUAN_WND6230.00] CKT 1 | 4.3513 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524889 [SN_JUAN_WND6230.00] CKT 1 | 4.4288 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524889 [SN_JUAN_WND6230.00] CKT 1 | 6.5247 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524889 [SN_JUAN_WND6230.00] CKT 1 | 7.6346 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.4218 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 3.437 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 3.674 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.0206 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.3519 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.4281 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524885 [SN_JUAN_TAP6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 6.7817 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524874 [OASIS 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 2.4596 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524874 [OASIS 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 2.645 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524874 [OASIS 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 3.438 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524874 [OASIS 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524874 [OASIS 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 4.0201 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524874 [OASIS 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524874 [OASIS 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524874 [OASIS 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 6.5094 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524874 [OASIS 3115.00] TO BUS 524924 [PORTALES 3115.00] CKT 1 | 7.5881 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 2.4519 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 4.0203 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 6.4503 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524872 [OASIS_TR1 113.200] TO BUS 524875 [OASIS 6230.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 7.4063 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 2.4583 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 3.438 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 4.0201 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 6.4979 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 7.553 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 2.4586 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 3.6743 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 4.4284 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524863 [FE-CHZPLT 3115.00] TO BUS 524764 [NORRIS_TP 3115.00] CKT 1 | 7.5563 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 2.4607 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 6.5145 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524874 [OASIS 3115.00] CKT 1 | 7.604 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 2.4607 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 6.5144 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524797 [PERIMETER 3115.00] TO BUS 524790 [CANNON_TP 3115.00] CKT 1 | 7.6039 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524909 [ROOSEVELT 6230.00] CKT 1 | 2.4566 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524909 [ROOSEVELT 6230.00] CKT 1 | 3.4383 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524909 [ROOSEVELT 6230.00] CKT 1 | 3.6745 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524909 [ROOSEVELT 6230.00] CKT 1 | 4.0204 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524909 [ROOSEVELT 6230.00] CKT 1 | 4.3512 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524909 [ROOSEVELT 6230.00] CKT 1 | 4.4287 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524909 [ROOSEVELT 6230.00] CKT 1 | 6.4891 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524909 [ROOSEVELT 6230.00] CKT 1 | 7.5252 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 2.452 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 3.1429 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 6.4512 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524875 [OASIS 6230.00] CKT 1 | 7.4086 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 2.4608 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 6.5198 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524831 [FE-HOLLAND 3115.00] CKT 1 | 7.6202 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 2.4611 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 4.0203 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 5.0223 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524776 [N_CLOVIS_TP3115.00] CKT 1 | 7.621 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 2.4608 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 2.6464 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 4.0202 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 5.0224 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524773 [E_CLOVIS 3115.00] CKT 1 | 7.6216 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 2.4598 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 3.6735 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 4.3501 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 4.4274 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 6.4795 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524768 [PLSNT_HILL 3115.00] TO BUS 524502 [NORTON 3115.00] CKT 1 | 7.5003 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524767 [PLSNHIL_TR1113.200] TO BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524768 [PLSNT_HILL 3115.00] CKT 1 | 2.4607 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524767 [PLSNHIL_TR1113.200] TO BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524768 [PLSNT_HILL 3115.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524767 [PLSNHIL_TR1113.200] TO BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524768 [PLSNT_HILL 3115.00] CKT 1 | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 524767 [PLSNHIL_TR1113.200] TO BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524768 [PLSNT_HILL 3115.00] CKT 1 | 4.0203 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524767 [PLSNHIL_TR1113.200] TO BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524768 [PLSNT_HILL 3115.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524767 [PLSNHIL_TR1113.200] TO BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524768 [PLSNT_HILL 3115.00] CKT 1 | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524767 [PLSNHIL_TR1113.200] TO BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524768 [PLSNT_HILL 3115.00] CKT 1 | 6.5132 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 524767 [PLSNHIL_TR1113.200] TO BUS 524770 [PLSNT_HILL 6230.00] TO BUS 524768 [PLSNT_HILL 3115.00] CKT 1 | 7.6001 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 525832 [TUCO_INT 7345.00] CKT 1 | 2.4145 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 525832 [TUCO_INT 7345.00] CKT 1 | 2.5893 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 2.4072 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 515458 [BORDER 7345.00] TO BUS 516059 [BECKHAM7 345.00] CKT 1 | 2.5851 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 764550 [G20-075-TAP 345.00] CKT 1 | 2.613 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 764550 [G20-075-TAP 345.00] CKT 1 | 2.8132 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 764550 [G20-075-TAP 345.00] CKT 1 | 3.4329 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 764550 [G20-075-TAP 345.00] CKT 1 | 3.6715 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 764550 [G20-075-TAP 345.00] CKT 1 | 4.0124 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 764550 [G20-075-TAP 345.00] CKT 1 | 4.1224 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 764550 [G20-075-TAP 345.00] CKT 1 | 4.3467 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 764550 [G20-075-TAP 345.00] CKT 1 | 6.0209 | PASS | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 764550 [G20-075-TAP 345.00] CKT 1 | 6.3394 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 764550 [G20-075-TAP 345.00] CKT 1 | 7.447 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 2.4613 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 2.6469 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 3.4383 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 3.6745 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 4.0204 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 4.3512 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 4.4287 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 4.8565 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 6.5216 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 763318 [GEN-2018-115345.00] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 760938 [G17-171-TAP 345.00] CKT 1 | 2.4572 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 760938 [G17-171-TAP 345.00] CKT 1 | 2.6125 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 760938 [G17-171-TAP 345.00] CKT 1 | 2.8126 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 760938 [G17-171-TAP 345.00] CKT 1 | 3.6708 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511468 [L.E.S.-7 345.00] TO BUS 760938 [G17-171-TAP 345.00] CKT 1 | 5.0208 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 2.461 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 3.4379 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 3.6742 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 4.0198 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 4.3508 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 4.4283 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 5.023 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511494 [COMMTAP4 138.00] CKT 1 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 3.6741 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 4.0201 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 4.3507 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 4.4282 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 5.023 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511486 [ELGINJT4 138.00] CKT 1 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 2.4613 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 3.6745 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 4.3512 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 4.4287 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 6.5216 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511474 [SHERID4 138.00] CKT 1 | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 3.6743 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 4.0201 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 5.023 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511416 [LES#1-1 13.800] CKT 1 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 3.6743 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 4.0201 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 5.023 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511466 [L.E.S.-2 69.000] TO BUS 511415 [LES#2-1 13.800] CKT 2 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 3.4382 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 3.6743 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 4.0203 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 4.351 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 4.4285 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 5.023 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511439 [LWSTAP 4 138.00] CKT 1 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 2.4611 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 3.438 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 3.6743 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 4.02 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 4.3509 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 4.4284 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 6.5214 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511437 [COMANC-4 138.00] CKT 1 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 3.6741 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 4.0201 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 4.3507 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 4.4282 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 5.023 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511467 [L.E.S.-4 138.00] TO BUS 511423 [FLE TAP4 138.00] CKT 1 | 7.6254 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 588760 [GEN-2017-033345.00] CKT 1 | 2.4606 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 588760 [GEN-2017-033345.00] CKT 1 | 2.6154 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 588760 [GEN-2017-033345.00] CKT 1 | 3.2373 | FAIL | Group Number 14 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 588760 [GEN-2017-033345.00] CKT 1 | 3.6752 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 588760 [GEN-2017-033345.00] CKT 1 | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 588760 [GEN-2017-033345.00] CKT 1 | 6.0232 | PASS | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 2.46 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 2.6152 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 2.8156 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 3.675 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 4.3512 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511456 [O.K.U.-7 345.00] TO BUS 511565 [OKLAUN HVDC7345.00] CKT 1 | 6.0245 | PASS | Group Number 10 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511414 [LES#4-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 2.4607 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511414 [LES#4-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 3.4374 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511414 [LES#4-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 3.6738 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511414 [LES#4-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 4.0191 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511414 [LES#4-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 4.3502 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511414 [LES#4-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 4.4278 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511414 [LES#4-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 6.5212 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511414 [LES#4-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 1 | 7.6253 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511411 [LES#5-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 2 | 2.4603 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 511411 [LES#5-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 2 | 3.4367 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511411 [LES#5-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 2 | 3.6732 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511411 [LES#5-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 2 | 4.3494 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511411 [LES#5-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 2 | 4.4271 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511411 [LES#5-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 2 | 6.5209 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 511411 [LES#5-1 13.800] TO BUS 511467 [L.E.S.-4 138.00] TO BUS 511468 [L.E.S.-7 345.00] CKT 2 | 7.6252 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 2.4647 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 2.6192 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 2.6507 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 3.4438 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 4.029 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 4.3592 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 4.4386 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 4.8567 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 6.5303 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 20003 [GSU_2_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764850 [G20-059-XFM234.500] CKT 1 | 7.6272 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 2.4647 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 2.6192 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 2.6507 | FAIL | Group Number 8 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 3.4438 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 4.029 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 4.3592 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 4.4386 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 4.8567 | FAIL | Group Number 9 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 6.5303 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | OPEN LINE FROM BUS 10003 [GSU_1_LV 13.800] TO BUS 764840 [GEN-2020-059345.00] TO BUS 764845 [G20-059-XFM134.500] CKT 1 | 7.6272 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | Base | 2.4612 | FAIL | Group Number 1 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | Base | 3.1428 | FAIL | Group Number 2 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060 | 230kV Lamb County Interchange | GEN-2020-017
DISIS-2020-001-1 | 05 SOUTHWEST | 25WP | Base | 3.4381 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | Base | 3.6744 | FAIL | Group Number 3 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | Base | 4.3511 | FAIL | Group Number 4 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Lubbock East Substation 230 kV | GEN-2020-060
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | Base | 4.4286 | FAIL | Group Number 5 | Tuco to Yoakum 345kV line | GEN-2020-068 GEN-2020-067 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | Base | 6.5215 | PASS | Group Number 6 | Tuco-Yoakum-Hobbs 345 kV | GEN-2020-059 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 05 SOUTHWEST | 25SP | Base | 7.6255 | PASS | Group Number 7 | 230kV Lamb County Interchange | GEN-2020-017 | OASIS 230kV Substation | GEN-2020-062
DISIS-2020-001-1 | 01 NORTH | 25SP | Base | 5.6503 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083
DISIS-2020-001-1 | 01 NORTH | 25WP | Base | 5.7037 | FAIL | Group Number 16 | LeLand Olds-Chapelle Creek 345kV line | GEN-2020-021 | Patent Gate Substation 345 kV | GEN-2020-091 | Fairview 115kV Substation | GEN-2020-083