02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_025 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_026 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_027 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_028 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_029 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_030 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_031 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_032 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_033 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_034 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_035 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_036 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_038 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_039 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_040 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_041 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_042 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_043 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_044 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_045 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_046 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_047 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_048 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_049 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_050 | 3 Phase fault on BVISTA 5 161.00 (635280) 161 kV Bus a. Apply fault at the BVISTA 5 161.00 (635280) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_051 | 3 Phase fault on VICTORY5 161.00 (635310) 161 kV Bus a. Apply fault at the VICTORY5 161.00 (635310) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_052 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_053 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_054 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_055 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_056 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_057 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_058 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_059 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_060 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_061 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_062 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_063 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_064 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_065 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_066 | 3 Phase fault on DENISON5 161.00 (652561) 161 kV Bus a. Apply fault at the DENISON5 161.00 (652561) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_067 | 3 Phase fault on OSGOOD5 161.00 (656527) 161 kV Bus a. Apply fault at the OSGOOD5 161.00 (656527) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_068 | 3 Phase fault on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_069 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_070 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_071 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_072 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_073 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_074 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_075 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_076 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_077 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_078 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_079 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_080 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT_REACT7 (541517) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_081 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_082 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_083 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_084 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_085 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_086 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_087 | 3 Phase fault on E7THST 7 115.00 (641085) 115 kV Bus a. Apply fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_088 | 3 Phase fault on NW5&BENTON7 115.00 (650212) 115 kV Bus a. Apply fault at the NW5&BENTON7 115.00 (650212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4&MORTON 7 (650205) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.2. W LINCOLN 7 (650208) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.3. NW5&BENTON7 (650212) 115.0 kV to NW5BENTN 9 (650312) 12.5 kV to 121TERTIARY (650512) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_089 | 3 Phase fault on 4&MORTON 7 115.00 (650205) 115 kV Bus a. Apply fault at the 4&MORTON 7 115.00 (650205) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4&MORTON 7 (650205) 115.0 kV to 19&ALVO 7 (650215) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_090 | 3 Phase fault on W LINCOLN 7 115.00 (650208) 115 kV Bus a. Apply fault at the W LINCOLN 7 115.00 (650208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_091 | 3 Phase fault on NW12&ARBOR7 115.00 (650226) 115 kV Bus a. Apply fault at the NW12&ARBOR7 115.00 (650226) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.3. NW12&ARBOR7 (650226) 115.0 kV to NW12&AR 9 (650326) 12.5 kV to 261TERTIARY (650526) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_092 | 3 Phase fault on 27FLETCHER7 115.00 (650228) 115 kV Bus a. Apply fault at the 27FLETCHER7 115.00 (650228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 27FLETCHER7 (650228) 115.0 kV Transmission Circuit #1 b.2. 27FLETCHER7 (650228) 115.0 kV to 33SUPERIOR7 (650233) 115.0 kV Transmission Circuit #1 b.3. 27FLETCHER7 (650228) 115.0 kV to 27&FL 9 (650328) 12.5 kV to 281TERTIARY (650528) 9.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_093 | 3 Phase fault on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.2. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.3. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_094 | 3 Phase fault on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 29LEIGHTON7 (650240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_095 | 3 Phase fault on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.2. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.6. 33SUPERIOR7 (650233) 115.0 kV Fixed Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_096 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_097 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_098 | 3 Phase fault on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_099 | 3 Phase fault on 84LEIGHTON7 115.00 (650267) 115 kV Bus a. Apply fault at the 84LEIGHTON7 115.00 (650267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_100 | 3 Phase fault on 70&BLUFF 7 115.00 (650269) 115 kV Bus a. Apply fault at the 70&BLUFF 7 115.00 (650269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_101 | 3 Phase fault on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_102 | 3 Phase fault on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_103 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_104 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_105 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_106 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_107 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_108 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_109 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_110 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_111 | 3 Phase fault on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.2. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 b.4. 70&BLUFF 9 (650369) 13.8 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 5 (650169) 161.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_112 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_113 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_114 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_115 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_116 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_117 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_118 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_119 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_120 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_121 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_122 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_123 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_124 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_125 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_126 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_127 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_128 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_129 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_130 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_131 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_132 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_133 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_134 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_135 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_136 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_137 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_138 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_139 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_140 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_141 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_142 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_143 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_144 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_145 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_146 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_147 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_148 | 3 Phase fault on HARMONY7 115.00 (640210) 115 kV Bus a. Apply fault at the HARMONY7 115.00 (640210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARMONY7 (640210) 115.0 kV to ST.FRANC (640351) 115.0 kV Transmission Circuit #1 b.2. HARMONY7 (640210) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.3. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_149 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_150 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_151 | 3 Phase fault on GOTHNBG7 115.00 (640196) 115 kV Bus a. Apply fault at the GOTHNBG7 115.00 (640196) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 b.2. GOTHNBG7 (640196) 115.0 kV to JEFFREY7 (640238) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_152 | 3 Phase fault on WESTMIN7 115.00 (640407) 115 kV Bus a. Apply fault at the WESTMIN7 115.00 (640407) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_153 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_154 | 3 Phase fault on ATKINSN7 115.00 (640058) 115 kV Bus a. Apply fault at the ATKINSN7 115.00 (640058) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLECREEK 7 (640465) 115.0 kV to EMMET 7 (640165) 115.0 kV Transmission Circuit #1 b.2. ATKINSN7 (640058) 115.0 kV to EMMET 7 (640165) 115.0 kV Transmission Circuit #1 b.3. ATKINSN7 (640058) 115.0 kV to STUART 7 (640367) 115.0 kV Transmission Circuit #1 b.4. STUART 7 (640367) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_155 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_156 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_157 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_158 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_159 | 3 Phase fault on DAVEY 7 115.00 (640155) 115 kV Bus a. Apply fault at the DAVEY 7 115.00 (640155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVEY 7 (640155) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 b.2. DAVEY 7 (640155) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_160 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_161 | 3 Phase fault on WINSLOW7 115.00 (640409) 115 kV Bus a. Apply fault at the WINSLOW7 115.00 (640409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_162 | 3 Phase fault on W.POINT7 115.00 (640400) 115 kV Bus a. Apply fault at the W.POINT7 115.00 (640400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_163 | 3 Phase fault on STANTON7 115.00 (640357) 115 kV Bus a. Apply fault at the STANTON7 115.00 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_164 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 b.2. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_165 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_166 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_167 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_168 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_169 | 3 Phase fault on CANADAY4 230.00 (640102) 230 kV Bus a. Apply fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_170 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_171 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_172 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_173 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_174 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_175 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_176 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_177 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_178 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_179 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_180 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_181 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_182 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_183 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_184 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_185 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_186 | 3 Phase fault on HASTING4 230.00 (640214) 230 kV Bus a. Apply fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_187 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_188 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_189 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_190 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_191 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_192 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_193 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_194 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_195 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_196 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_197 | 3 Phase fault on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_198 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_199 | 3 Phase fault on ORLEANS8 69.000 (640311) 69 kV Bus a. Apply fault at the ORLEANS8 69.000 (640311) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS8 (640311) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_200 | 3 Phase fault on VALENTN7 115.00 (640392) 115 kV Bus a. Apply fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALENTN7 (640392) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_201 | 3 Phase fault on COOPER 869.000 (640446) 69 kV Bus a. Apply fault at the COOPER 869.000 (640446) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_202 | 3 Phase fault on HILDRTH8 69.000 (640223) 69 kV Bus a. Apply fault at the HILDRTH8 69.000 (640223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_203 | 3 Phase fault on BASSETT 7115.00 (640580) 115 kV Bus a. Apply fault at the BASSETT 7115.00 (640580) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 7 (640580) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_204 | 3 Phase fault on BASSETT 869.000 (640581) 69 kV Bus a. Apply fault at the BASSETT 869.000 (640581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 8 (640581) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_205 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_206 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_207 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_208 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_209 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_210 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_211 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_212 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_213 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_214 | 3 Phase fault on VETAL_TP-RM7115.00 (659153) 115 kV Bus a. Apply fault at the VETAL_TP-RM7115.00 (659153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.2. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_215 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_216 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_217 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_218 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_219 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_220 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_221 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_222 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_223 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_224 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_225 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_226 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_227 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_228 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_229 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_230 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_231 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_232 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_233 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_234 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_235 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_236 | 3 Phase fault on WINNER 7 115.00 (652494) 115 kV Bus a. Apply fault at the WINNER 7 115.00 (652494) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREGORY7 (652478) 115.0 kV to WINNER 7 (652494) 115.0 kV Transmission Circuit #1 b.2. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.3. WINNER 7 (652494) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_237 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_238 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_239 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_240 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_241 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_242 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_243 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_244 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_245 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_246 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_247 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_248 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_249 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_250 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_251 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_252 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_253 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_254 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_255 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1299 5 (646299) 161.0 kV Load #O0 b.4. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_256 | 3 Phase fault on S1299 5 161.00 (646299) 161 kV Bus a. Apply fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-037-TAP (762712) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1299 5 (646299) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_257 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_258 | 3 Phase fault on S1222 5 161.00 (646222) 161 kV Bus a. Apply fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_259 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_260 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_261 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_262 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_263 | 3 Phase fault on S1227 5 161.00 (646227) 161 kV Bus a. Apply fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_264 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_265 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_266 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_267 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_268 | 3 Phase fault on S1234 5 161.00 (646234) 161 kV Bus a. Apply fault at the S1234 5 161.00 (646234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_269 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_270 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_271 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_272 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_273 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_274 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_275 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_276 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_277 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_278 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_279 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1278 5 (646278) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_280 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_281 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_282 | 3 Phase fault on S1286 5 161.00 (646286) 161 kV Bus a. Apply fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_283 | 3 Phase fault on S1298 5 161.00 (646298) 161 kV Bus a. Apply fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_284 | 3 Phase fault on S1305 5 161.00 (646305) 161 kV Bus a. Apply fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_285 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_286 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_287 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_288 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_289 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_290 | 3 Phase fault on S1361 5 161.00 (646361) 161 kV Bus a. Apply fault at the S1361 5 161.00 (646361) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1361 5 (646361) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_291 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_292 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_293 | 3 Phase fault on 991TP 8 69.000 (647091) 69 kV Bus a. Apply fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 991TP 8 (647091) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 b.2. 991TP 8 (647091) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.3. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_294 | 3 Phase fault on JCT205 8 69.000 (647105) 69 kV Bus a. Apply fault at the JCT205 8 69.000 (647105) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.3. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_295 | 3 Phase fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_296 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_297 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S972 8 (647972) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_298 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_299 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_300 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_301 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_302 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_303 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_304 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_305 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_306 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_307 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_308 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_309 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_310 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_311 | 3 Phase fault on S910 8 69.000 (647910) 69 kV Bus a. Apply fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_312 | 3 Phase fault on S911 8 69.000 (647911) 69 kV Bus a. Apply fault at the S911 8 69.000 (647911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_313 | 3 Phase fault on S916 8 69.000 (647916) 69 kV Bus a. Apply fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_314 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_315 | 3 Phase fault on S916 8 69.000 (647916) 69 kV Bus a. Apply fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_316 | 3 Phase fault on S917 8 69.000 (647917) 69 kV Bus a. Apply fault at the S917 8 69.000 (647917) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_317 | 3 Phase fault on S918 8 69.000 (647918) 69 kV Bus a. Apply fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_318 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_319 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_320 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_321 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_322 | 3 Phase fault on S928 8 69.000 (647928) 69 kV Bus a. Apply fault at the S928 8 69.000 (647928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S928 8 (647928) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_323 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_324 | 3 Phase fault on S938 8 69.000 (647938) 69 kV Bus a. Apply fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_325 | 3 Phase fault on FREM F 8 69.000 (647426) 69 kV Bus a. Apply fault at the FREM F 8 69.000 (647426) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM F 8 (647426) 69.0 kV to S992 8 (647992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_326 | 3 Phase fault on FREM D 8 69.000 (647424) 69 kV Bus a. Apply fault at the FREM D 8 69.000 (647424) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM D 8 (647424) 69.0 kV to FREM E 8 (647425) 69.0 kV Transmission Circuit #1 b.2. FREM D 8 (647424) 69.0 kV to S976 8 (647976) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_327 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_328 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_329 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM C 8 (647423) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_330 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_331 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_332 | 3 Phase fault on FREM C 8 69.000 (647423) 69 kV Bus a. Apply fault at the FREM C 8 69.000 (647423) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM C 8 (647423) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_333 | 3 Phase fault on FREM E 8 69.000 (647425) 69 kV Bus a. Apply fault at the FREM E 8 69.000 (647425) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM E 8 (647425) 69.0 kV to FREM F 8 (647426) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_334 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.2. S991 E 8 (647291) 69.0 kV to S1291 5 (646291) 161.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_335 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_336 | 3 Phase fault on 6815TP98 69.000 (647017) 69 kV Bus a. Apply fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_337 | 3 Phase fault on S939 8 69.000 (647939) 69 kV Bus a. Apply fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_338 | 3 Phase fault on ASH GRV8 69.000 (647100) 69 kV Bus a. Apply fault at the ASH GRV8 69.000 (647100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_339 | 3 Phase fault on 979TP 8 69.000 (647079) 69 kV Bus a. Apply fault at the 979TP 8 69.000 (647079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 979TP 8 (647079) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.2. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 b.3. 979TP 8 (647079) 69.0 kV to S979 8 (647979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_340 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_341 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_342 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_343 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_344 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_345 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_346 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_347 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_348 | 3 Phase fault on S3761 3 345.00 (645761) 345 kV Bus a. Apply fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_349 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_350 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_351 | 3 Phase fault on S1210 5 161.00 (646210) 161 kV Bus a. Apply fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_352 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_353 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_354 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_355 | 3 Phase fault on S1217 5 161.00 (646217) 161 kV Bus a. Apply fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_356 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_357 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_358 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_359 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_360 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_361 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_362 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_363 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_364 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_365 | 3 Phase fault on S942 8 69.000 (647942) 69 kV Bus a. Apply fault at the S942 8 69.000 (647942) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S942 8 (647942) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_366 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT_REACT7 (541517) 345.0 kV remove bus # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_367 | 3 Phase fault on RENNER 7 115.00 (603274) 115 kV Bus a. Apply fault at the RENNER 7 115.00 (603274) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERRYC7 (603008) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 b.2. SPLT RK7 (603016) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_368 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips: POMEROY W3 (636035). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_369 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_370 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_371 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to SMITHLD8 (635303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_372 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_373 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to EASTSID8 (635247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_374 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to SLOAN 8 (635237) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_375 | 3 Phase fault on SBRIDGE T8 69.000 (635227) 69 kV Bus a. Apply fault at the SBRIDGE T8 69.000 (635227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SBRIDGE T8 (635227) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_376 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_377 | 3 Phase fault on KELLOGG8 69.000 (635222) 69 kV Bus a. Apply fault at the KELLOGG8 69.000 (635222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG8 (635222) 69.0 kV to STSTEEL8 (635240) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_378 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to DANBURY8 (635304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_379 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_380 | 3 Phase fault on STSTEEL8 69.000 (635240) 69 kV Bus a. Apply fault at the STSTEEL8 69.000 (635240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STSTEEL8 (635240) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_381 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to MERRIL 8 (635393) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_382 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to MAPLTN 8 (635302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_383 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_384 | 3 Phase fault on IRETONT8 69.000 (635391) 69 kV Bus a. Apply fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_385 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_386 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_387 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_388 | 3 Phase fault on J1620 POI 115.00 (46207) 115 kV Bus a. Apply fault at the J1620 POI 115.00 (46207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1620 POI (46207) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_389 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_390 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_391 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_392 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_393 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to K318MEC -NI8 (659855) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_394 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_395 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_396 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_397 | 3 Phase fault on N HAYS3 115.00 (530581) 115 kV Bus a. Apply fault at the N HAYS3 115.00 (530581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_398 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_399 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_400 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_401 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_402 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_403 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_404 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_405 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_406 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_407 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_408 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_409 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_410 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_411 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_412 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_413 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_414 | 3 Phase fault on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_415 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_416 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_417 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_418 | 3 Phase fault on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_419 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to SIOUXCY8 (652574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_420 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10215A_-NI8 (659922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_421 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10225A_-NI8 (659923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_422 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to K121MPLM-NI8 (659990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_423 | 3 Phase fault on AINSWND7 115.00 (640050) 115 kV Bus a. Apply fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_424 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_425 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_426 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_427 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_428 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_429 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_430 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_431 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_432 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_433 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_434 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_435 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_436 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_437 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_438 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_439 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_440 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_441 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_442 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_443 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_444 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_445 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_446 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_447 | 3 Phase fault on CODY 7 115.00 (640117) 115 kV Bus a. Apply fault at the CODY 7 115.00 (640117) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CODY 7 (640117) 115.0 kV to G20-069-TAP (764475) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_448 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_449 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_450 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_451 | 3 Phase fault on COOPER_ESST869.000 (640141) 69 kV Bus a. Apply fault at the COOPER_ESST869.000 (640141) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_ESST8 (640141) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_452 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_453 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_454 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_455 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_456 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_457 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_458 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_459 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_460 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_461 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_462 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_463 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_464 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_465 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_466 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_467 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_468 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_469 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_470 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_471 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_472 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_473 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_474 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_475 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_476 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_477 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_478 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_479 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to JOHN.1 7 (640240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_480 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_481 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_482 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_483 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LXNGTN 7 (640256) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_484 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_485 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to PROSSER7 (640321) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_486 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_487 | 3 Phase fault on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_488 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_489 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_490 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_491 | 3 Phase fault on RIVERDL7 115.00 (640331) 115 kV Bus a. Apply fault at the RIVERDL7 115.00 (640331) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_492 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_493 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_494 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_495 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_496 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_497 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_498 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_499 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_500 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_501 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_502 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_503 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 3 (640520) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_504 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_505 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_506 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_507 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_508 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_509 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_510 | 3 Phase fault on S1220 5 161.00 (646220) 161 kV Bus a. Apply fault at the S1220 5 161.00 (646220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1220 5 (646220) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_511 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_512 | 3 Phase fault on S1236 5 161.00 (646236) 161 kV Bus a. Apply fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_513 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_514 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_515 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_516 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_517 | 3 Phase fault on S1299 5 161.00 (646299) 161 kV Bus a. Apply fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1299 5 (646299) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_518 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_519 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_520 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM F 8 (647426) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_521 | 3 Phase fault on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_522 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_523 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_524 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_525 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_526 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_527 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_528 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_529 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_530 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_531 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_532 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_533 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K216LIBE-NI8 (659946) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_534 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_535 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K301HINT-NI8 (659971) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_536 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K135CONC-NI8 (659980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_537 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_538 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_539 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_540 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_541 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_542 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_543 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_544 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_545 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_546 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_547 | 3 Phase fault on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_548 | 3 Phase fault on K10215A_-NI869.000 (659922) 69 kV Bus a. Apply fault at the K10215A_-NI869.000 (659922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10215A_-NI8 (659922) 69.0 kV to K144LWTN-NI8 (659979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_549 | 3 Phase fault on K10225A_-NI869.000 (659923) 69 kV Bus a. Apply fault at the K10225A_-NI869.000 (659923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10225A_-NI8 (659923) 69.0 kV to K127WHTG-NI8 (659981) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_550 | 3 Phase fault on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_551 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_552 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_553 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_554 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_555 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT8 (640052) 69.0 kV to AINSWRT7 (640051) 115.0 kV to AINSWORTHT29 (643002) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_556 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_557 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT19 (643023) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_558 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT29 (643024) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_559 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG8 (640101) 69.0 kV to CAMBRIG7 (640100) 115.0 kV to CAMBRIDGET19 (643028) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_560 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 8 (640145) 69.0 kV to COZAD 7 (640144) 115.0 kV to COZAD T2 9 (643174) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_561 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK 8 (640162) 69.0 kV to ELMCRK_7 (640161) 115.0 kV to ELMCREEK T19 (643053) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_562 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV to HILDRTH7 (640222) 115.0 kV to HILDRETH T19 (643079) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_563 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_564 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.LK8 (640245) 69.0 kV to JOHN.LK7 (640244) 115.0 kV to JOHNSONLKT19 (643089) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_565 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNGTN8 (640257) 69.0 kV to LXNGTN 7 (640256) 115.0 kV to LEXINGTONT29 (643093) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_566 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 8 (640262) 69.0 kV to LOWELL 7 (640261) 115.0 kV to LOWELL T1 9 (643096) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_567 | 3 Phase fault on ORLEANS7 115.00 (640310) 115 kV Bus a. Apply fault at the ORLEANS7 115.00 (640310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS8 (640311) 69.0 kV to ORLEANS7 (640310) 115.0 kV to ORLEANS T1 9 (643120) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_568 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_569 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_570 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T1 9 (643157) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_571 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T2 9 (643158) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_572 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_573 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_574 | 3 Phase fault on BASSETT 7115.00 (640580) 115 kV Bus a. Apply fault at the BASSETT 7115.00 (640580) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 8 (640581) 69.0 kV to BASSETT 7 (640580) 115.0 kV to BASSETT T1 9 (643180) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_575 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_576 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_577 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_578 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_579 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_580 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_581 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_582 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_583 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_584 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_585 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_586 | 3 Phase fault on MISSION7 115.00 (652482) 115 kV Bus a. Apply fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MISSION7 (652482) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_587 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_001 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_002 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_003 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_004 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_005 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_006 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_007 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_008 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_009 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_010 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_011 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_012 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_014 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_015 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_017 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_018 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_019 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_020 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_021 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_022 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_023 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_024 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_025 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_026 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_027 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_028 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_029 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_030 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_031 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_032 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_033 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_036 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_037 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_040 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_041 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_042 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_043 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_044 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_045 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_046 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_047 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_048 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply Fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 b.2. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SALIX 5 161.00 (635235) 161 kV Bus a. Apply Fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.3. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CRWFRD 5 161.00 (635330) 161 kV Bus a. Apply Fault at the CRWFRD 5 161.00 (635330) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.2. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.3. CRWFRD 5 (635330) 161.0 kV to NEWHRVST 9 (635331) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.4. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 b.3. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.4. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.6. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.7. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.8. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 b.9. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. HOSK.T89 (640230) 34.5 kV to HOSKINS4 (640227) 230.0 kV Two Winding #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 b.5. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply Fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.3. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT19 (643039) 13.8 kV Three Winding #1 b.4. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT29 (643040) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.3. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.4. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply Fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.2. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.3. AINSWRT7 (640051) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 b.4. AINSWRT9 (640053) 34.5 kV to AINSWRT7 (640051) 115.0 kV Two Winding #1 b.5. AINSWRT7 (640051) 115.0 kV to AINSWRT8 (640052) 69.0 kV to AINSWORTHT29 (643002) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on AINSWND7 115.00 (640050) 115 kV Bus a. Apply Fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWND.PLTD (640025) 34.5 kV Two Winding #1 b.2. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.3. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.4. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.4. BELDEN 7 (640080) 115.0 kV to BELDEN 8 (640081) 69.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to CANADY1G (640005) 13.8 kV Two Winding #1 b.2. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 b.3. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.4. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #2 b.5. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 b.6. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on COZAD 7 115.00 (640144) 115 kV Bus a. Apply Fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COZAD 7 (640144) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 b.2. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 b.3. COZAD 7 (640144) 115.0 kV to COZAD 8 (640145) 69.0 kV to COZAD T2 9 (643174) 13.8 kV Three Winding #1 b.4. COZAD 7 (640144) 115.0 kV to COZAD 9 (640146) 34.5 kV to COZAD T1 9 (643043) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CRETE__7 115.00 (640153) 115 kV Bus a. Apply Fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.3. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T1 9 (643048) 13.8 kV Three Winding #1 b.4. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T2 9 (643049) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply Fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 b.2. LXNGTN 7 (640256) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 b.3. LXNGTN 7 (640256) 115.0 kV to LEXNGTN8 (640257) 69.0 kV to LEXINGTONT29 (643093) 13.8 kV Three Winding #1 b.4. LXNGTN 7 (640256) 115.0 kV to LEXNGTN9 (640258) 34.5 kV to LEXINGTONT19 (643094) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply Fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. LOWELL 7 (640261) 115.0 kV to PROSSER7 (640321) 115.0 kV Transmission Circuit #1 b.4. LOWELL 7 (640261) 115.0 kV to LOWELL 8 (640262) 69.0 kV to LOWELL T1 9 (643096) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on MINDEN 7 115.00 (640275) 115 kV Bus a. Apply Fault at the MINDEN 7 115.00 (640275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. MINDEN 7 (640275) 115.0 kV to MINDEN 9 (640276) 34.5 kV to MINDEN T1 9 (643102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T1 9 (643112) 13.8 kV Three Winding #1 b.5. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T2 9 (643113) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply Fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT19 (643110) 13.8 kV Three Winding #1 b.5. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT29 (643111) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.3. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.4. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.5. OAKLAND7 (640300) 115.0 kV to OAKLAND9 (640301) 34.5 kV to OAKLAND T1 9 (643114) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on PAULINE7 115.00 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.4. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 b.5. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.6. PAULINE7 (640313) 115.0 kV to PAULINE8 (640314) 69.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on STNTN.N7 115.00 (640363) 115 kV Bus a. Apply Fault at the STNTN.N7 115.00 (640363) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. STNTN.N7 (640363) 115.0 kV to STNTN.N9 (640364) 34.5 kV to STANTN.N T19 (643145) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on TEKAMAH7 115.00 (640378) 115 kV Bus a. Apply Fault at the TEKAMAH7 115.00 (640378) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.2. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 b.3. TEKAMAH7 (640378) 115.0 kV to TEKAMAH9 (640379) 34.5 kV to TEKAMAH T2 9 (643152) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on TOWER 7 115.00 (640383) 115 kV Bus a. Apply Fault at the TOWER 7 115.00 (640383) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.2. RIVERDL7 (640331) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.3. TOWER 9 (640385) 12.5 kV to TOWER 7 (640383) 115.0 kV Two Winding #1 b.4. TOWER 7 (640383) 115.0 kV to TOWER A9 (640384) 34.5 kV to TOWER T2 9 (643154) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on VALENTN7 115.00 (640392) 115 kV Bus a. Apply Fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.2. HARMONY7 (640210) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.3. VALENTN7 (640392) 115.0 kV to VALTN.W7 (640394) 115.0 kV Transmission Circuit #1 b.4. VALENTN7 (640392) 115.0 kV to VALENTN9 (640393) 34.5 kV to VALENTINET19 (643160) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.3. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.5. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET29 (643081) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.3. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to G20-013-TAP (764445) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.3. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET29 (643081) 13.8 kV Three Winding #1 b.9. HOLDREG7 (640224) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.3. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREGE 8 (640448) 69.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 b.9. HOLDREG7 (640224) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.8. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.6. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on MISSION7 115.00 (652482) 115 kV Bus a. Apply Fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARMONY7 (640210) 115.0 kV to ST.FRANC (640351) 115.0 kV Transmission Circuit #1 b.2. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 b.3. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #1 b.4. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #2 b.5. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.6. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.7. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.8. WINNER 7 (652494) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.3. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply Fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. ROCKRPDMUNI8 (658122) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.3. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 b.4. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.5. RKRPDTAP-LO8 (659714) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.6. LESTERSS-LO8 (659722) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.7. STEEN -LO8 (659726) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.8. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.3. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.4. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.5. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.6. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.7. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on SPENCER5 161.00 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.2. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.3. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.4. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.5. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.6. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on MISSION7 115.00 (652482) 115 kV Bus a. Apply Fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 b.2. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #1 b.3. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #2 b.4. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.5. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.6. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.7. MISSION7 (652482) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on NEBCTY1G 18.000 (645011) 18 kV Bus a. Apply Fault at the NEBCTY1G 18.000 (645011) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEBCTY1G (645011) 18.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on NEBCTY2G 23.000 (645012) 23 kV Bus a. Apply Fault at the NEBCTY2G 23.000 (645012) 23 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEBCTY2G (645012) 23.0 kV to Generator #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on S1367 5 161.00 (646367) 161 kV Bus a. Apply Fault at the S1367 5 161.00 (646367) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on S1256 5 161.00 (646256) 161 kV Bus a. Apply Fault at the S1256 5 161.00 (646256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on S1255 5 161.00 (646255) 161 kV Bus a. Apply Fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1341 5 (646341) 161.0 kV to Load #O0 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on S1361 5 161.00 (646361) 161 kV Bus a. Apply Fault at the S1361 5 161.00 (646361) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1361 5 (646361) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.2. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on SARPY 5G 13.800 (645035) 13.80000019 kV Bus a. Apply Fault at the SARPY 5G 13.800 (645035) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to Generator #4 b.3. SARPY 5G (645035) 13.8 kV to Generator #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.2. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1211T39 (645127) 13.8 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.4. S1211 5 (646211) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 b.2. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.4. S1299 5 (646299) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1211T49 (645128) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on S1227 5 161.00 (646227) 161 kV Bus a. Apply Fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on S1232 5 161.00 (646232) 161 kV Bus a. Apply Fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on S1233 5 161.00 (646233) 161 kV Bus a. Apply Fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 b.2. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.3. S1235 5 (646235) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on S1236 5 161.00 (646236) 161 kV Bus a. Apply Fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on S1249 5 161.00 (646249) 161 kV Bus a. Apply Fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 b.5. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.3. S1211 5 (646211) 161.0 kV to Load #O0 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1211 5 (646211) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FC1A 5 (645100) 161.0 kV to FC1A3 9 (645103) 4.2 kV Two Winding #1 b.2. FC1A 5 (645100) 161.0 kV to FC1A4 9 (645104) 4.2 kV Two Winding #1 b.3. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.4. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.5. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.6. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.3. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.4. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1278 5 (646278) 161.0 kV to Load #O0 b.2. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1278 5 (646278) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.3. S1278 5 (646278) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 b.9. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.6. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.7. S1260 5 (646260) 161.0 kV to load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to Load #O0 b.2. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on S1287 5 161.00 (646287) 161 kV Bus a. Apply Fault at the S1287 5 161.00 (646287) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1298 5 (646298) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.2. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on S1291 5 161.00 (646291) 161 kV Bus a. Apply Fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on S1345 5 161.00 (646345) 161 kV Bus a. Apply Fault at the S1345 5 161.00 (646345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply Fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 b.2. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.3. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.4. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.4. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.2. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.3. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.4. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.5. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.6. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.7. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. SUB701 5 (635003) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply Fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on MONONA 5 161.00 (635300) 161 kV Bus a. Apply Fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to IDA GRV B1 9 (635207) 34.5 kV Two Winding #1 b.2. IDA CO 3 (635206) 345.0 kV to IDA GRV B2 9 (635208) 34.5 kV Two Winding #1 b.3. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to IDA GRV B1 9 (635207) 34.5 kV Two Winding #1 b.2. IDA CO 3 (635206) 345.0 kV to IDA GRV B2 9 (635208) 34.5 kV Two Winding #1 b.3. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FALLOW 3 (635590) 345.0 kV to ARBR HL 3 (635580) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to GLACIAL EDGE (637009) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. ARBR HL 3 (635580) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B1 9 (635401) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply Fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. GARD AVE 3 (635219) 345.0 kV to RICHLAND W (637024) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B2 9 (635402) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to Load #M2 b.2. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on SHAYS_230 230.00 (530610) 230 kV Bus a. Apply Fault at the SHAYS_230 230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.5. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply Fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 27FLETCHER7 (650228) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.3. 27FLETCHER7 (650228) 115.0 kV to 33SUPERIOR7 (650233) 115.0 kV Transmission Circuit #1 b.4. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.5. 27FLETCHER7 (650228) 115.0 kV to 27&FL 9 (650328) 12.5 kV to 281TERTIARY (650528) 9.2 kV Three Winding #1 b.6. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply Fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAVEY 7 (640155) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.3. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.4. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.5. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 b.6. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on TBGS_A 7 115.00 (650277) 115 kV Bus a. Apply Fault at the TBGS_A 7 115.00 (650277) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TBGS 4G (650004) 13.8 kV to TBGS LFG G (650010) 4.2 kV Two Winding #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.4. TBGS_A 7 (650277) 115.0 kV to TBGS 4G (650004) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply Fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on TBGS_B 7 115.00 (650278) 115 kV Bus a. Apply Fault at the TBGS_B 7 115.00 (650278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TBGS 4G (650004) 13.8 kV to TBGS LFG G (650010) 4.2 kV Two Winding #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.4. TBGS_A 7 (650277) 115.0 kV to TBGS 4G (650004) 13.8 kV Two Winding #1 b.5. TBGS_B 7 (650278) 115.0 kV to TBGS 1G (650001) 13.8 kV Two Winding #1 b.6. TBGS_B 7 (650278) 115.0 kV to TBGS 2G (650002) 13.8 kV Two Winding #1 b.7. TBGS_B 7 (650278) 115.0 kV to TBGS 3G (650003) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. TBGS_B 7 (650278) 115.0 kV to TBGS 1G (650001) 13.8 kV Two Winding #1 b.5. TBGS_B 7 (650278) 115.0 kV to TBGS 2G (650002) 13.8 kV Two Winding #1 b.6. TBGS_B 7 (650278) 115.0 kV to TBGS 3G (650003) 13.8 kV Two Winding #1 b.7. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply Fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 120&ALVO 7 (650279) 115.0 kV to 120&ALVO 9 (650379) 12.5 kV to 791TERTIARY (650579) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on WAVERLY 7 115.00 (650283) 115 kV Bus a. Apply Fault at the WAVERLY 7 115.00 (650283) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.3. WAVERLY 7 (650283) 115.0 kV to WAVERLY A9 (650383) 13.2 kV to 831TERTIARY (650583) 7.2 kV Three Winding #1 b.4. WAVERLY 7 (650283) 115.0 kV to WAVERLY B9 (650483) 12.5 kV to 832TERTIARY (650683) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on WAGENER 7 115.00 (650285) 115 kV Bus a. Apply Fault at the WAGENER 7 115.00 (650285) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to HALLAM3G (640021) 13.8 kV Two Winding #1 b.2. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to SHELDN1G (640019) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SHELDN2G (640020) 13.8 kV Two Winding #1 b.2. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLM1G (640010) 23.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.3. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.3. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 b.2. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 8 (640446) 69.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 b.5. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on S900 8 69.000 (647900) 69 kV Bus a. Apply Fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 979TP 8 (647079) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.2. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 b.3. 979TP 8 (647079) 69.0 kV to S979 8 (647979) 69.0 kV Transmission Circuit #1 b.4. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.5. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.6. S900 8 (647900) 69.0 kV to S972 8 (647972) 69.0 kV Transmission Circuit #1 b.7. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on S902 8 69.000 (647902) 69 kV Bus a. Apply Fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 b.3. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.5. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.9. S906 N 8 (647006) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.2. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.4. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.9. S906 S 8 (647906) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on S907 8 69.000 (647907) 69 kV Bus a. Apply Fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.2. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.5. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.6. S909 8 (647909) 69.0 kV to S1209 5 (646209) 161.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.5. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.5. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 1G (645021) 13.8 kV to NO1 AUX9 (645121) 2.4 kV Two Winding #1 b.2. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.3. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.4. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 b.5. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.6. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on S914 8 69.000 (647914) 69 kV Bus a. Apply Fault at the S914 8 69.000 (647914) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.2. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.2. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.2. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_363 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.2. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.3. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.5. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on S918 8 69.000 (647918) 69 kV Bus a. Apply Fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.3. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on S919 8 69.000 (647919) 69 kV Bus a. Apply Fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 b.2. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.3. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.2. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.3. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 b.4. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on S930 8 69.000 (647930) 69 kV Bus a. Apply Fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on S930 8 69.000 (647930) 69 kV Bus a. Apply Fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.2. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on S939 8 69.000 (647939) 69 kV Bus a. Apply Fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on S939 8 69.000 (647939) 69 kV Bus a. Apply Fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on S983 8 69.000 (647983) 69 kV Bus a. Apply Fault at the S983 8 69.000 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on 991TP 8 69.000 (647091) 69 kV Bus a. Apply Fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 991TP 8 (647091) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 b.2. 991TP 8 (647091) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.3. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 b.4. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on FREM B 8 69.000 (647422) 69 kV Bus a. Apply Fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.2. FREM A 8 (647421) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.3. FREM B 8 (647422) 69.0 kV to FREM C 8 (647423) 69.0 kV Transmission Circuit #1 b.4. FREM B 8 (647422) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 b.5. FREM B 8 (647422) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on S937 8 69.000 (647937) 69 kV Bus a. Apply Fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S937 8 (647937) 69.0 kV to S902 8 (647902) 69.0 kV Transmission Circuit #1 b.2. S937 8 (647937) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on SBRIDGE T8 69.000 (635227) 69 kV Bus a. Apply Fault at the SBRIDGE T8 69.000 (635227) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SBRIDGE T8 (635227) 69.0 kV to NEAL N 8 (635204) 69.0 kV Transmission Circuit #1 b.2. SBRIDGE T8 (635227) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply Fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply Fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_381 | Single Phase Fault with Stuck Breaker on GOSPER 7 115.00 (640194) 115 kV Bus a. Apply Fault at the GOSPER 7 115.00 (640194) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GOSPER 7 (640194) 115.0 kV to CAMBRIG7 (640100) 115.0 kV Transmission Circuit #1 b.2. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_382 | Single Phase Fault with Stuck Breaker on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply Fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEFFREY7 (640238) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 b.2. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_383 | Single Phase Fault with Stuck Breaker on JOHN.1 7 115.00 (640240) 115 kV Bus a. Apply Fault at the JOHN.1 7 115.00 (640240) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHN.1 7 (640240) 115.0 kV to JEFFREY7 (640238) 115.0 kV Transmission Circuit #1 b.2. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_384 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.2. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_385 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to COLMB.E3 (640125) 345.0 kV Transmission Circuit #1 b.2. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_386 | Single Phase Fault with Stuck Breaker on STUART 7 115.00 (640367) 115 kV Bus a. Apply Fault at the STUART 7 115.00 (640367) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STUART 7 (640367) 115.0 kV to ATKINSN7 (640058) 115.0 kV Transmission Circuit #1 b.2. STUART 7 (640367) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_387 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_388 | Single Phase Fault with Stuck Breaker on TOBIAS 3345.00 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3345.00 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. TOBIAS 3 (640525) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_389 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_390 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_391 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_392 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.2. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_393 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_394 | Single Phase Fault with Stuck Breaker on S6846 8 69.000 (647846) 69 kV Bus a. Apply Fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6846 8 (647846) 69.0 kV to S914A 8 (647014) 69.0 kV Transmission Circuit #1 b.2. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_395 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_396 | Single Phase Fault with Stuck Breaker on G17-105TAP 161.00 (762069) 161 kV Bus a. Apply Fault at the G17-105TAP 161.00 (762069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to RAUN 5 (635201) 161.0 kV Transmission Circuit #1 b.2. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_397 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_398 | Single Phase Fault with Stuck Breaker on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply Fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-065-TAP (763031) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_399 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_400 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY4 (640102) 230.0 kV to C.CREEK4 (640093) 230.0 kV Transmission Circuit #1 b.2. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_401 | Single Phase Fault with Stuck Breaker on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply Fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_402 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_403 | Single Phase Fault with Stuck Breaker on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply Fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHN.LK7 (640244) 115.0 kV to JOHN.1 7 (640240) 115.0 kV Transmission Circuit #1 b.2. JOHN.LK7 (640244) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_404 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_405 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_406 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.2. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_407 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 b.2. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_408 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1210 5 (646210) 161.0 kV Transmission Circuit #1 b.2. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_409 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_410 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_411 | Single Phase Fault with Stuck Breaker on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply Fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&BLUFF 5 (650169) 161.0 kV to S1214 5 (646214) 161.0 kV Transmission Circuit #1 b.2. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_412 | Single Phase Fault with Stuck Breaker on CANADAY7 115.00 (640103) 115 kV Bus a. Apply Fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 b.2. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_413 | Single Phase Fault with Stuck Breaker on VALENTN7 115.00 (640392) 115 kV Bus a. Apply Fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALENTN7 (640392) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.2. VALENTN7 (640392) 115.0 kV to HARMONY7 (640210) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_414 | Single Phase Fault with Stuck Breaker on S909 8 69.000 (647909) 69 kV Bus a. Apply Fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_415 | Single Phase Fault with Stuck Breaker on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply Fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY-LNX3 (652864) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_416 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GR ISLD-LNX3 (653871) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_417 | Single Phase Fault with Stuck Breaker on 84&BLUFF 7 (650275) 115 kV Bus a. Apply Fault at the 84&BLUFF 7 (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_418 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_419 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_420 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_421 | Single Phase Fault with Stuck Breaker on AXTELL 7 (640066) 115 kV Bus a. Apply Fault at the AXTELL 7 (640066) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_422 | Single Phase Fault with Stuck Breaker on HOLDREG7 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_423 | Single Phase Fault with Stuck Breaker on JOHN.2 7 (640242) 115 kV Bus a. Apply Fault at the JOHN.2 7 (640242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHN.2 7 (640242) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_424 | Single Phase Fault with Stuck Breaker on S1281 5 (646281) 161 kV Bus a. Apply Fault at the S1281 5 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_425 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_426 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_427 | Single Phase Fault with Stuck Breaker on S3458 3 (645458) 345 kV Bus a. Apply Fault at the S3458 3 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_428 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_429 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_430 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_431 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_432 | Single Phase Fault with Stuck Breaker on S909 8 (647909) 69 kV Bus a. Apply Fault at the S909 8 (647909) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_433 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_434 | Single Phase Fault with Stuck Breaker on S1251 5 (646251) 161 kV Bus a. Apply Fault at the S1251 5 (646251) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_435 | Single Phase Fault with Stuck Breaker on AINSWRT7 (640051) 115 kV Bus a. Apply Fault at the AINSWRT7 (640051) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWRT7 (640051) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_436 | Single Phase Fault with Stuck Breaker on S1347 5 (646347) 161 kV Bus a. Apply Fault at the S1347 5 (646347) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1347 5 (646347) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_437 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_438 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_439 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_440 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_441 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES1 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES2 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES3 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.3. TBGS 1G (650001) 13.8 kV to Generator #1 b.4. TBGS 2G (650002) 13.8 kV to Generator #2 b.5. TBGS 3G (650003) 13.8 kV to Generator #3 b.6. TBGS 4G (650004) 13.8 kV to Generator #4 b.7. TBGS LFG G (650010) 4.2 kV to Generator #10 b.8. TBGS 1G (650001) 13.8 kV to Load #S1 b.9. TBGS 2G (650002) 13.8 kV to Load #S1 b.10. TBGS 3G (650003) 13.8 kV to Load #S1 b.11. TBGS 4G (650004) 13.8 kV to Load #S1 b.12. TBGS 1G (650001) 13.8 kV to remove bus # b.13. TBGS 2G (650002) 13.8 kV to remove bus # b.14. TBGS 3G (650003) 13.8 kV to remove bus # b.15. TBGS 4G (650004) 13.8 kV to remove bus # b.16. TBGS LFG G (650010) 4.2 kV to remove bus # b.17. TBGS_A 7 (650277) 115.0 kV to remove bus # b.18. TBGS_B 7 (650278) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES4 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES5 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.2. TBGS 1G (650001) 13.8 kV to Generator #1 b.3. TBGS 2G (650002) 13.8 kV to Generator #2 b.4. TBGS 3G (650003) 13.8 kV to Generator #3 b.5. TBGS 1G (650001) 13.8 kV to Load #S1 b.6. TBGS 2G (650002) 13.8 kV to Load #S1 b.7. TBGS 3G (650003) 13.8 kV to Load #S1 b.8. TBGS 1G (650001) 13.8 kV to remove bus # b.9. TBGS 2G (650002) 13.8 kV to remove bus # b.10. TBGS 3G (650003) 13.8 kV to remove bus # b.11. TBGS_B 7 (650278) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES6 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES7 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES8 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.2. TBGS 2G (650002) 13.8 kV to Generator #2 b.3. TBGS 3G (650003) 13.8 kV to Generator #3 b.4. TBGS 4G (650004) 13.8 kV to Generator #4 b.5. TBGS LFG G (650010) 4.2 kV to Generator #10 b.6. TBGS 1G (650001) 13.8 kV to Generator #1 b.7. TBGS 1G (650001) 13.8 kV to Load #S1 b.8. TBGS 2G (650002) 13.8 kV to Load #S1 b.9. TBGS 3G (650003) 13.8 kV to Load #S1 b.10. TBGS 1G (650001) 13.8 kV to remove bus # b.11. TBGS 2G (650002) 13.8 kV to remove bus # b.12. TBGS 3G (650003) 13.8 kV to remove bus # b.13. TBGS_B 7 (650278) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW1 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.3. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW10 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW11 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW12 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW13 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW14 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW15 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW16 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW17 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW2 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.3. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW3 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW4 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW5 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW6 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.4. BUCKE_WTG (530705) 0.7 kV to remove bus # b.5. BUCKW_WTG (530708) 0.7 kV to remove bus # b.6. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.7. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.8. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.9. BUCKW_TERT (530706) 13.8 kV to remove bus # b.10. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.11. BUCKE_TERT (530709) 13.8 kV to remove bus # b.12. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW7 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW8 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW9 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD1 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD2 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.3. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD3 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.3. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.4. COOPER1G (640009) 22.0 kV to Generator #1 b.5. COOPER1G (640009) 22.0 kV to Load #S1 b.6. COOPER1G (640009) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD4 | Single Phase Fault with Stuck Breaker on TWIN CH4 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 b.3. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.4. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD5 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD6 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD7 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD1 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD10 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD11 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD12 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to remove bus # b.2. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD13 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD14 | Single Phase Fault with Stuck Breaker on S1361 5 (646361) 161 kV Bus a. Apply Fault at the S1361 5 (646361) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD15 | Single Phase Fault with Stuck Breaker on S1217 5 (646217) 161 kV Bus a. Apply Fault at the S1217 5 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to remove bus # b.2. S1217T19 (648217) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD16 | Single Phase Fault with Stuck Breaker on S1244 5 (646244) 161 kV Bus a. Apply Fault at the S1244 5 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1244 5 (646244) 161.0 kV to Load #O0 b.4. S1244 5 (646244) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD17 | Single Phase Fault with Stuck Breaker on S1305 5 (646305) 161 kV Bus a. Apply Fault at the S1305 5 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1305 5 (646305) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 b.4. S1305 5 (646305) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD18 | Single Phase Fault with Stuck Breaker on S1210 5 (646210) 161 kV Bus a. Apply Fault at the S1210 5 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 b.4. S1210 5 (646210) 161.0 kV to Load #O0 b.5. S1210 5 (646210) 161.0 kV to Load #OW | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD19 | Single Phase Fault with Stuck Breaker on S1251 5 (646251) 161 kV Bus a. Apply Fault at the S1251 5 (646251) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.3. S1341 5 (646341) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.4. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.5. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.6. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.7. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.8. S3459 3 (645459) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.9. S1297 9 (649297) 13.8 kV to Load #O0 b.10. S1297 9 (649297) 13.8 kV to remove bus # b.11. S1297 9 (649297) 13.8 kV to Generator #1 b.12. S3451 3 (645451) 345.0 kV to remove bus # b.13. S3451T39 (648251) 13.8 kV to remove bus # b.14. S3451T49 (648351) 13.8 kV to remove bus # b.15. S1297 5 (646297) 161.0 kV to remove bus # b.16. S1305 5 (646305) 161.0 kV to remove bus # b.17. S1341 5 (646341) 161.0 kV to remove bus # b.18. S1298 5 (646298) 161.0 kV to remove bus # b.19. FC1A 5 (645100) 161.0 kV to remove bus # b.20. FC1A3 9 (645103) 4.2 kV to remove bus # b.21. FC1A4 9 (645104) 4.2 kV to remove bus # b.22. S1251 5 (646251) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD2 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD20 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S1297 9 (649297) 13.8 kV to Generator #1 b.3. S1297 9 (649297) 13.8 kV to Load #O0 b.4. S1297 9 (649297) 13.8 kV to remove bus # b.5. S3459 3 (645459) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.6. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.7. S1237 5 (646237) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.8. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.9. S1341 5 (646341) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.10. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.11. S3451T49 (648351) 13.8 kV to remove bus # b.12. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.13. S1297 5 (646297) 161.0 kV to remove bus # b.14. S3451T39 (648251) 13.8 kV to remove bus # b.15. S3451 3 (645451) 345.0 kV to remove bus # b.16. S1305 5 (646305) 161.0 kV to remove bus # b.17. S1341 5 (646341) 161.0 kV to remove bus # b.18. S1298 5 (646298) 161.0 kV to remove bus # b.19. FC1A 5 (645100) 161.0 kV to remove bus # b.20. FC1A3 9 (645103) 4.2 kV to remove bus # b.21. FC1A4 9 (645104) 4.2 kV to remove bus # b.22. S1251 5 (646251) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD21 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.3. S918 8 (647918) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 b.4. S939 8 (647939) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 b.5. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.6. S3459T39 (648259) 13.8 kV to remove bus # b.7. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.8. S1231 5 (646231) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 b.9. S1347 5 (646347) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 b.10. S1231 5 (646231) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #2 b.11. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.12. S1250 5 (646250) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 b.13. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.14. S1250 5 (646250) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #2 b.15. S921 8 (647921) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 b.16. S937 8 (647937) 69.0 kV to remove bus # b.17. S909 8 (647909) 69.0 kV to remove bus # b.18. S1209T19 (648209) 13.8 kV to remove bus # b.19. S3459 3 (645459) 345.0 kV to remove bus # b.20. S3459T69 (648359) 13.8 kV to remove bus # b.21. S1209 5 (646209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD22 | Single Phase Fault with Stuck Breaker on S1220 5 (646220) 161 kV Bus a. Apply Fault at the S1220 5 (646220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1220 5 (646220) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.3. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.4. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.5. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.6. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.7. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 b.8. S1211T19 (648211) 13.8 kV to remove bus # b.9. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.10. S950 8 (647950) 69.0 kV to remove bus # b.11. S1250T19 (648250) 13.8 kV to remove bus # b.12. N OMA 4G (645024) 15.0 kV to Generator #4 b.13. N OMA 4G (645024) 15.0 kV to remove bus # b.14. N OMA 5G (645025) 20.0 kV to Generator #5 b.15. N OMA 5G (645025) 20.0 kV to remove bus # b.16. S1299 5 (646299) 161.0 kV to remove bus # b.17. S1286 5 (646286) 161.0 kV to remove bus # b.18. S1211 5 (646211) 161.0 kV to remove bus # b.19. S1297 9 (649297) 13.8 kV to Generator #1 b.20. NO4 AUX9 (645124) 2.4 kV to Load #S1 b.21. NO5 AUX9 (645125) 4.2 kV to Load #S1 b.22. S1211T39 (645127) 13.8 kV to Load #S1 b.23. S1211T39 (645127) 13.8 kV to Load #S2 b.24. S1211T39 (645127) 13.8 kV to Load #S3 b.25. S1211T39 (645127) 13.8 kV to Load #S4 b.26. S1211T39 (645127) 13.8 kV to Load #S5 b.27. S1211T49 (645128) 13.8 kV to Load #S1 b.28. S1211T49 (645128) 13.8 kV to Load #S2 b.29. S1211T49 (645128) 13.8 kV to Load #S3 b.30. S1211T49 (645128) 13.8 kV to Load #S4 b.31. S1211T49 (645128) 13.8 kV to Load #S5 b.32. S1250 5 (646250) 161.0 kV to Load #O0 b.33. S1297 9 (649297) 13.8 kV to Load #O0 b.34. NO4 AUX9 (645124) 2.4 kV to remove bus # b.35. NO5 AUX9 (645125) 4.2 kV to remove bus # b.36. S1211T39 (645127) 13.8 kV to remove bus # b.37. S1211T49 (645128) 13.8 kV to remove bus # b.38. S1297 5 (646297) 161.0 kV to remove bus # b.39. S1297 9 (649297) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD23 | Single Phase Fault with Stuck Breaker on CBLUFFS5 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to CBLUFFS5 (635001) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.3. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.4. S1206T19 (648206) 13.8 kV to remove bus # b.5. S1216 5 (646216) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.6. S1232 5 (646232) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.7. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.8. S3456T49 (648256) 13.8 kV to remove bus # b.9. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.10. S938 8 (647938) 69.0 kV to S906 N 8 (647006) 69.0 kV Transmission Circuit #1 b.11. S924 8 (647924) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.12. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.13. S1206T29 (648306) 13.8 kV to remove bus # b.14. SARPY 3G (645033) 13.8 kV to Generator #3 b.15. SARPY 3G (645033) 13.8 kV to remove bus # b.16. SCBSD G (645030) 4.2 kV to remove bus # b.17. SARPY 4G (645034) 13.8 kV to Generator #4 b.18. SARPY 4G (645034) 13.8 kV to remove bus # b.19. SARPY 5G (645035) 13.8 kV to Generator #5 b.20. SARPY 5G (645035) 13.8 kV to remove bus # b.21. S1206 5 (646206) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD24 | Single Phase Fault with Stuck Breaker on S1216 5 (646216) 161 kV Bus a. Apply Fault at the S1216 5 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1216 5 (646216) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.3. S1206T19 (648206) 13.8 kV to remove bus # b.4. S1206 5 (646206) 161.0 kV to CBLUFFS5 (635001) 161.0 kV Transmission Circuit #1 b.5. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.6. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.7. S3456T49 (648256) 13.8 kV to remove bus # b.8. S1232 5 (646232) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.9. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.10. S916 8 (647916) 69.0 kV to S906 N 8 (647006) 69.0 kV Transmission Circuit #1 b.11. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.12. S1206T29 (648306) 13.8 kV to remove bus # b.13. SARPY 3G (645033) 13.8 kV to Generator #3 b.14. SARPY 3G (645033) 13.8 kV to remove bus # b.15. SCBSD G (645030) 4.2 kV to remove bus # b.16. SARPY 4G (645034) 13.8 kV to Generator #4 b.17. SARPY 4G (645034) 13.8 kV to remove bus # b.18. SARPY 5G (645035) 13.8 kV to Generator #5 b.19. SARPY 5G (645035) 13.8 kV to remove bus # b.20. S1206 5 (646206) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD25 | Single Phase Fault with Stuck Breaker on S1286 5 (646286) 161 kV Bus a. Apply Fault at the S1286 5 (646286) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1286 5 (646286) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.3. S1220 5 (646220) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.4. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 b.5. S1201T19 (648201) 13.8 kV to remove bus # b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.7. S1206T19 (648206) 13.8 kV to remove bus # b.8. S1229 5 (646229) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.9. S1201 5 (646201) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD26 | Single Phase Fault with Stuck Breaker on S1361 5 (646361) 161 kV Bus a. Apply Fault at the S1361 5 (646361) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1361 5 (646361) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.3. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.4. S1259 5 (646259) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.5. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 b.6. S3455T39 (648355) 13.8 kV to remove bus # b.7. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.8. S3455T19 (648255) 13.8 kV to remove bus # b.9. S1255 5 (646255) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD27 | Single Phase Fault with Stuck Breaker on S1221 5 (646221) 161 kV Bus a. Apply Fault at the S1221 5 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1221 5 (646221) 161.0 kV Transmission Circuit #1 b.2. S1255 5 (646255) 161.0 kV to S1221 5 (646221) 161.0 kV Transmission Circuit #1 b.3. S940 8 (647940) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD28 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.5. S1341 5 (646341) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.7. S3451T49 (648351) 13.8 kV to remove bus # b.8. S1251 5 (646251) 161.0 kV to S3451 3 (645451) 345.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 b.9. S3451T39 (648251) 13.8 kV to remove bus # b.10. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.11. S1297 5 (646297) 161.0 kV to remove bus # b.12. FC1A 5 (645100) 161.0 kV to remove bus # b.13. FC1A3 9 (645103) 4.2 kV to remove bus # b.14. FC1A4 9 (645104) 4.2 kV to remove bus # b.15. S1251 5 (646251) 161.0 kV to remove bus # b.16. S1297 9 (649297) 13.8 kV to Generator #1 b.17. S1297 9 (649297) 13.8 kV to Load #O0 b.18. S1297 9 (649297) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD3 | Single Phase Fault with Stuck Breaker on S3458 3 (645458) 345 kV Bus a. Apply Fault at the S3458 3 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD4 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD5 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to Load #O0 b.3. S1206 5 (646206) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.4. S1206 5 (646206) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD6 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD7 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD8 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to Load #O0 b.3. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD9 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.3. S1216 5 (646216) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FALLOW 3 (635590) 345.0 kV to ARBR HL 3 (635580) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. ARBR HL 3 (635580) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. to AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Open # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_001 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_002 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_003 | 3 Phase fault on LEMARST5 161.00 (635260) 161 kV Bus a. Apply fault at the LEMARST5 161.00 (635260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_004 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_005 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_006 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_007 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_008 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_009 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_010 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_011 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_012 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_013 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_014 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_015 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_016 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_017 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_018 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_019 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_020 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_021 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to ROCK CO5 (602039) 161.0 kV Transmission Circuit #1 b.2. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_022 | 3 Phase fault on CAYLER5 161.00 (631183) 161 kV Bus a. Apply fault at the CAYLER5 161.00 (631183) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_023 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_024 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_025 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_026 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_027 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_028 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_029 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_030 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_031 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_032 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_033 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_034 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_035 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_036 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_038 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_039 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_040 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_041 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_042 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_043 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_044 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_045 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_046 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_047 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_048 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_049 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_050 | 3 Phase fault on BVISTA 5 161.00 (635280) 161 kV Bus a. Apply fault at the BVISTA 5 161.00 (635280) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_051 | 3 Phase fault on VICTORY5 161.00 (635310) 161 kV Bus a. Apply fault at the VICTORY5 161.00 (635310) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_052 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_053 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_054 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_055 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_056 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_057 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_058 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_059 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_060 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_061 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_062 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_063 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_064 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_065 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_066 | 3 Phase fault on DENISON5 161.00 (652561) 161 kV Bus a. Apply fault at the DENISON5 161.00 (652561) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_067 | 3 Phase fault on OSGOOD5 161.00 (656527) 161 kV Bus a. Apply fault at the OSGOOD5 161.00 (656527) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_068 | 3 Phase fault on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_069 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_070 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_071 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_072 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_073 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_074 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_075 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_076 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_077 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_078 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_079 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_080 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT_REACT7 (541517) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_081 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_082 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_083 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_084 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_085 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_086 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_087 | 3 Phase fault on E7THST 7 115.00 (641085) 115 kV Bus a. Apply fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_088 | 3 Phase fault on NW5&BENTON7 115.00 (650212) 115 kV Bus a. Apply fault at the NW5&BENTON7 115.00 (650212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4&MORTON 7 (650205) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.2. W LINCOLN 7 (650208) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.3. NW5&BENTON7 (650212) 115.0 kV to NW5BENTN 9 (650312) 12.5 kV to 121TERTIARY (650512) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_089 | 3 Phase fault on 4&MORTON 7 115.00 (650205) 115 kV Bus a. Apply fault at the 4&MORTON 7 115.00 (650205) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4&MORTON 7 (650205) 115.0 kV to 19&ALVO 7 (650215) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_090 | 3 Phase fault on W LINCOLN 7 115.00 (650208) 115 kV Bus a. Apply fault at the W LINCOLN 7 115.00 (650208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_091 | 3 Phase fault on NW12&ARBOR7 115.00 (650226) 115 kV Bus a. Apply fault at the NW12&ARBOR7 115.00 (650226) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.3. NW12&ARBOR7 (650226) 115.0 kV to NW12&AR 9 (650326) 12.5 kV to 261TERTIARY (650526) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_092 | 3 Phase fault on 27FLETCHER7 115.00 (650228) 115 kV Bus a. Apply fault at the 27FLETCHER7 115.00 (650228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 27FLETCHER7 (650228) 115.0 kV Transmission Circuit #1 b.2. 27FLETCHER7 (650228) 115.0 kV to 33SUPERIOR7 (650233) 115.0 kV Transmission Circuit #1 b.3. 27FLETCHER7 (650228) 115.0 kV to 27&FL 9 (650328) 12.5 kV to 281TERTIARY (650528) 9.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_093 | 3 Phase fault on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.2. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.3. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_094 | 3 Phase fault on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 29LEIGHTON7 (650240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_095 | 3 Phase fault on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.2. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.6. 33SUPERIOR7 (650233) 115.0 kV Fixed Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_096 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_097 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_098 | 3 Phase fault on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_099 | 3 Phase fault on 84LEIGHTON7 115.00 (650267) 115 kV Bus a. Apply fault at the 84LEIGHTON7 115.00 (650267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_100 | 3 Phase fault on 70&BLUFF 7 115.00 (650269) 115 kV Bus a. Apply fault at the 70&BLUFF 7 115.00 (650269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_101 | 3 Phase fault on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_102 | 3 Phase fault on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_103 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_104 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_105 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_106 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_107 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_108 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_109 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_110 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_111 | 3 Phase fault on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.2. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 b.4. 70&BLUFF 9 (650369) 13.8 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 5 (650169) 161.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_112 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_113 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_114 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_115 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_116 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_117 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_118 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_119 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_120 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_121 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_122 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_123 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_124 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_125 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_126 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_127 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_128 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_129 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_130 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_131 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_132 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_133 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_134 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_135 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_136 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_137 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_138 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_139 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_140 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_141 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_142 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_143 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_144 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_145 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_146 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_147 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_148 | 3 Phase fault on HARMONY7 115.00 (640210) 115 kV Bus a. Apply fault at the HARMONY7 115.00 (640210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARMONY7 (640210) 115.0 kV to ST.FRANC (640351) 115.0 kV Transmission Circuit #1 b.2. HARMONY7 (640210) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.3. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_149 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_150 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_151 | 3 Phase fault on GOTHNBG7 115.00 (640196) 115 kV Bus a. Apply fault at the GOTHNBG7 115.00 (640196) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 b.2. GOTHNBG7 (640196) 115.0 kV to JEFFREY7 (640238) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_152 | 3 Phase fault on WESTMIN7 115.00 (640407) 115 kV Bus a. Apply fault at the WESTMIN7 115.00 (640407) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_153 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_154 | 3 Phase fault on ATKINSN7 115.00 (640058) 115 kV Bus a. Apply fault at the ATKINSN7 115.00 (640058) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLECREEK 7 (640465) 115.0 kV to EMMET 7 (640165) 115.0 kV Transmission Circuit #1 b.2. ATKINSN7 (640058) 115.0 kV to EMMET 7 (640165) 115.0 kV Transmission Circuit #1 b.3. ATKINSN7 (640058) 115.0 kV to STUART 7 (640367) 115.0 kV Transmission Circuit #1 b.4. STUART 7 (640367) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_155 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_156 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_157 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_158 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_159 | 3 Phase fault on DAVEY 7 115.00 (640155) 115 kV Bus a. Apply fault at the DAVEY 7 115.00 (640155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVEY 7 (640155) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 b.2. DAVEY 7 (640155) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_160 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_161 | 3 Phase fault on WINSLOW7 115.00 (640409) 115 kV Bus a. Apply fault at the WINSLOW7 115.00 (640409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_162 | 3 Phase fault on W.POINT7 115.00 (640400) 115 kV Bus a. Apply fault at the W.POINT7 115.00 (640400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_163 | 3 Phase fault on STANTON7 115.00 (640357) 115 kV Bus a. Apply fault at the STANTON7 115.00 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_164 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 b.2. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_165 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_166 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_167 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_168 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_169 | 3 Phase fault on CANADAY4 230.00 (640102) 230 kV Bus a. Apply fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_170 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_171 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_172 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_173 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_174 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_175 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_176 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_177 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_178 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_179 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_180 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_181 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_182 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_183 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_184 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_185 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_186 | 3 Phase fault on HASTING4 230.00 (640214) 230 kV Bus a. Apply fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_187 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_188 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_189 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_190 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_191 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_192 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_193 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_194 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_195 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_196 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_197 | 3 Phase fault on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_198 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_199 | 3 Phase fault on ORLEANS8 69.000 (640311) 69 kV Bus a. Apply fault at the ORLEANS8 69.000 (640311) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS8 (640311) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_200 | 3 Phase fault on VALENTN7 115.00 (640392) 115 kV Bus a. Apply fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALENTN7 (640392) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_201 | 3 Phase fault on COOPER 869.000 (640446) 69 kV Bus a. Apply fault at the COOPER 869.000 (640446) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_202 | 3 Phase fault on HILDRTH8 69.000 (640223) 69 kV Bus a. Apply fault at the HILDRTH8 69.000 (640223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_203 | 3 Phase fault on BASSETT 7115.00 (640580) 115 kV Bus a. Apply fault at the BASSETT 7115.00 (640580) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 7 (640580) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_204 | 3 Phase fault on BASSETT 869.000 (640581) 69 kV Bus a. Apply fault at the BASSETT 869.000 (640581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 8 (640581) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_205 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_206 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_207 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_208 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_209 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_210 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_211 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips: SVWF3 1 (539120). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_212 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_213 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_214 | 3 Phase fault on VETAL_TP-RM7115.00 (659153) 115 kV Bus a. Apply fault at the VETAL_TP-RM7115.00 (659153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.2. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_215 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_216 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_217 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_218 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_219 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_220 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_221 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_222 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_223 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_224 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_225 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_226 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_227 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_228 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_229 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_230 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_231 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_232 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_233 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_234 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_235 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_236 | 3 Phase fault on WINNER 7 115.00 (652494) 115 kV Bus a. Apply fault at the WINNER 7 115.00 (652494) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREGORY7 (652478) 115.0 kV to WINNER 7 (652494) 115.0 kV Transmission Circuit #1 b.2. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.3. WINNER 7 (652494) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_237 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_238 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_239 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_240 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_241 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_242 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_243 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_244 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_245 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_246 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_247 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_248 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_249 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_250 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_251 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_252 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_253 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_254 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_255 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1299 5 (646299) 161.0 kV Load #O0 b.4. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_256 | 3 Phase fault on S1299 5 161.00 (646299) 161 kV Bus a. Apply fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-037-TAP (762712) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1299 5 (646299) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_257 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_258 | 3 Phase fault on S1222 5 161.00 (646222) 161 kV Bus a. Apply fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_259 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_260 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_261 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_262 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_263 | 3 Phase fault on S1227 5 161.00 (646227) 161 kV Bus a. Apply fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_264 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_265 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_266 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_267 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_268 | 3 Phase fault on S1234 5 161.00 (646234) 161 kV Bus a. Apply fault at the S1234 5 161.00 (646234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_269 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_270 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_271 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_272 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_273 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_274 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_275 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_276 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_277 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_278 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_279 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1278 5 (646278) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_280 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_281 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_282 | 3 Phase fault on S1286 5 161.00 (646286) 161 kV Bus a. Apply fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_283 | 3 Phase fault on S1298 5 161.00 (646298) 161 kV Bus a. Apply fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_284 | 3 Phase fault on S1305 5 161.00 (646305) 161 kV Bus a. Apply fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_285 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_286 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_287 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_288 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_289 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_290 | 3 Phase fault on S1361 5 161.00 (646361) 161 kV Bus a. Apply fault at the S1361 5 161.00 (646361) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1361 5 (646361) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_291 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_292 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_293 | 3 Phase fault on 991TP 8 69.000 (647091) 69 kV Bus a. Apply fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 991TP 8 (647091) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 b.2. 991TP 8 (647091) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.3. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_294 | 3 Phase fault on JCT205 8 69.000 (647105) 69 kV Bus a. Apply fault at the JCT205 8 69.000 (647105) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.3. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_295 | 3 Phase fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_296 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_297 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S972 8 (647972) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_298 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_299 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_300 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_301 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_302 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_303 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_304 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_305 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_306 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_307 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_308 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_309 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_310 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_311 | 3 Phase fault on S910 8 69.000 (647910) 69 kV Bus a. Apply fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_312 | 3 Phase fault on S911 8 69.000 (647911) 69 kV Bus a. Apply fault at the S911 8 69.000 (647911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_313 | 3 Phase fault on S916 8 69.000 (647916) 69 kV Bus a. Apply fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_314 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_315 | 3 Phase fault on S916 8 69.000 (647916) 69 kV Bus a. Apply fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_316 | 3 Phase fault on S917 8 69.000 (647917) 69 kV Bus a. Apply fault at the S917 8 69.000 (647917) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_317 | 3 Phase fault on S918 8 69.000 (647918) 69 kV Bus a. Apply fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_318 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_319 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_320 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_321 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_322 | 3 Phase fault on S928 8 69.000 (647928) 69 kV Bus a. Apply fault at the S928 8 69.000 (647928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S928 8 (647928) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_323 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_324 | 3 Phase fault on S938 8 69.000 (647938) 69 kV Bus a. Apply fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_325 | 3 Phase fault on FREM F 8 69.000 (647426) 69 kV Bus a. Apply fault at the FREM F 8 69.000 (647426) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM F 8 (647426) 69.0 kV to S992 8 (647992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_326 | 3 Phase fault on FREM D 8 69.000 (647424) 69 kV Bus a. Apply fault at the FREM D 8 69.000 (647424) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM D 8 (647424) 69.0 kV to FREM E 8 (647425) 69.0 kV Transmission Circuit #1 b.2. FREM D 8 (647424) 69.0 kV to S976 8 (647976) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_327 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_328 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_329 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM C 8 (647423) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_330 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_331 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_332 | 3 Phase fault on FREM C 8 69.000 (647423) 69 kV Bus a. Apply fault at the FREM C 8 69.000 (647423) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM C 8 (647423) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_333 | 3 Phase fault on FREM E 8 69.000 (647425) 69 kV Bus a. Apply fault at the FREM E 8 69.000 (647425) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM E 8 (647425) 69.0 kV to FREM F 8 (647426) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_334 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.2. S991 E 8 (647291) 69.0 kV to S1291 5 (646291) 161.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_335 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_336 | 3 Phase fault on 6815TP98 69.000 (647017) 69 kV Bus a. Apply fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_337 | 3 Phase fault on S939 8 69.000 (647939) 69 kV Bus a. Apply fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_338 | 3 Phase fault on ASH GRV8 69.000 (647100) 69 kV Bus a. Apply fault at the ASH GRV8 69.000 (647100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_339 | 3 Phase fault on 979TP 8 69.000 (647079) 69 kV Bus a. Apply fault at the 979TP 8 69.000 (647079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 979TP 8 (647079) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.2. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 b.3. 979TP 8 (647079) 69.0 kV to S979 8 (647979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_340 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_341 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_342 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_343 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_344 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_345 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_346 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_347 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_348 | 3 Phase fault on S3761 3 345.00 (645761) 345 kV Bus a. Apply fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_349 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_350 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_351 | 3 Phase fault on S1210 5 161.00 (646210) 161 kV Bus a. Apply fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_352 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_353 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_354 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_355 | 3 Phase fault on S1217 5 161.00 (646217) 161 kV Bus a. Apply fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_356 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_357 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_358 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_359 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_360 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_361 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_362 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_363 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_364 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_365 | 3 Phase fault on S942 8 69.000 (647942) 69 kV Bus a. Apply fault at the S942 8 69.000 (647942) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S942 8 (647942) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_366 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT_REACT7 (541517) 345.0 kV remove bus # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_367 | 3 Phase fault on RENNER 7 115.00 (603274) 115 kV Bus a. Apply fault at the RENNER 7 115.00 (603274) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERRYC7 (603008) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 b.2. SPLT RK7 (603016) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_368 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_369 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_370 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_371 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to SMITHLD8 (635303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_372 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_373 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to EASTSID8 (635247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_374 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to SLOAN 8 (635237) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_375 | 3 Phase fault on SBRIDGE T8 69.000 (635227) 69 kV Bus a. Apply fault at the SBRIDGE T8 69.000 (635227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SBRIDGE T8 (635227) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_376 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_377 | 3 Phase fault on KELLOGG8 69.000 (635222) 69 kV Bus a. Apply fault at the KELLOGG8 69.000 (635222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG8 (635222) 69.0 kV to STSTEEL8 (635240) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_378 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to DANBURY8 (635304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_379 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_380 | 3 Phase fault on STSTEEL8 69.000 (635240) 69 kV Bus a. Apply fault at the STSTEEL8 69.000 (635240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STSTEEL8 (635240) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_381 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to MERRIL 8 (635393) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_382 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to MAPLTN 8 (635302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_383 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_384 | 3 Phase fault on IRETONT8 69.000 (635391) 69 kV Bus a. Apply fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_385 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_386 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_387 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_388 | 3 Phase fault on J1620 POI 115.00 (46207) 115 kV Bus a. Apply fault at the J1620 POI 115.00 (46207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1620 POI (46207) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_389 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_390 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_391 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_392 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_393 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to K318MEC -NI8 (659855) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_394 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_395 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_396 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_397 | 3 Phase fault on N HAYS3 115.00 (530581) 115 kV Bus a. Apply fault at the N HAYS3 115.00 (530581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_398 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_399 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_400 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_401 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_402 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips: SVWF3 1 (539120). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_403 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_404 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_405 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_406 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_407 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_408 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_409 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_410 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_411 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_412 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_413 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_414 | 3 Phase fault on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_415 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_416 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_417 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_418 | 3 Phase fault on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_419 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to SIOUXCY8 (652574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_420 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10215A_-NI8 (659922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_421 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10225A_-NI8 (659923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_422 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to K121MPLM-NI8 (659990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_423 | 3 Phase fault on AINSWND7 115.00 (640050) 115 kV Bus a. Apply fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_424 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_425 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_426 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_427 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_428 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_429 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_430 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_431 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_432 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_433 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_434 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_435 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_436 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_437 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_438 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_439 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_440 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_441 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_442 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_443 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_444 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_445 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_446 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_447 | 3 Phase fault on CODY 7 115.00 (640117) 115 kV Bus a. Apply fault at the CODY 7 115.00 (640117) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CODY 7 (640117) 115.0 kV to G20-069-TAP (764475) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_448 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_449 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_450 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_451 | 3 Phase fault on COOPER_ESST869.000 (640141) 69 kV Bus a. Apply fault at the COOPER_ESST869.000 (640141) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_ESST8 (640141) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_452 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_453 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_454 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_455 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_456 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_457 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_458 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_459 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_460 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_461 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_462 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_463 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_464 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_465 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_466 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_467 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_468 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_469 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_470 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_471 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_472 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_473 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_474 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_475 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_476 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_477 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_478 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_479 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to JOHN.1 7 (640240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_480 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_481 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_482 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_483 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LXNGTN 7 (640256) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_484 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_485 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to PROSSER7 (640321) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_486 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_487 | 3 Phase fault on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_488 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_489 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_490 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_491 | 3 Phase fault on RIVERDL7 115.00 (640331) 115 kV Bus a. Apply fault at the RIVERDL7 115.00 (640331) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_492 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_493 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_494 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_495 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_496 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_497 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_498 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_499 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_500 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_501 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_502 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_503 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 3 (640520) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_504 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_505 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_506 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_507 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_508 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_509 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_510 | 3 Phase fault on S1220 5 161.00 (646220) 161 kV Bus a. Apply fault at the S1220 5 161.00 (646220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1220 5 (646220) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_511 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_512 | 3 Phase fault on S1236 5 161.00 (646236) 161 kV Bus a. Apply fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_513 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_514 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_515 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_516 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_517 | 3 Phase fault on S1299 5 161.00 (646299) 161 kV Bus a. Apply fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1299 5 (646299) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_518 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_519 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_520 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM F 8 (647426) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_521 | 3 Phase fault on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_522 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_523 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_524 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_525 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_526 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_527 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_528 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_529 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_530 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_531 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_532 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_533 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K216LIBE-NI8 (659946) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_534 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_535 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K301HINT-NI8 (659971) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_536 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K135CONC-NI8 (659980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_537 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_538 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_539 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_540 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_541 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_542 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_543 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_544 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_545 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_546 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_547 | 3 Phase fault on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_548 | 3 Phase fault on K10215A_-NI869.000 (659922) 69 kV Bus a. Apply fault at the K10215A_-NI869.000 (659922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10215A_-NI8 (659922) 69.0 kV to K144LWTN-NI8 (659979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_549 | 3 Phase fault on K10225A_-NI869.000 (659923) 69 kV Bus a. Apply fault at the K10225A_-NI869.000 (659923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10225A_-NI8 (659923) 69.0 kV to K127WHTG-NI8 (659981) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_550 | 3 Phase fault on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_551 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_552 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_553 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_554 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_555 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT8 (640052) 69.0 kV to AINSWRT7 (640051) 115.0 kV to AINSWORTHT29 (643002) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_556 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_557 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT19 (643023) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_558 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT29 (643024) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_559 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG8 (640101) 69.0 kV to CAMBRIG7 (640100) 115.0 kV to CAMBRIDGET19 (643028) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_560 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 8 (640145) 69.0 kV to COZAD 7 (640144) 115.0 kV to COZAD T2 9 (643174) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_561 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK 8 (640162) 69.0 kV to ELMCRK_7 (640161) 115.0 kV to ELMCREEK T19 (643053) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_562 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV to HILDRTH7 (640222) 115.0 kV to HILDRETH T19 (643079) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_563 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_564 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.LK8 (640245) 69.0 kV to JOHN.LK7 (640244) 115.0 kV to JOHNSONLKT19 (643089) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_565 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNGTN8 (640257) 69.0 kV to LXNGTN 7 (640256) 115.0 kV to LEXINGTONT29 (643093) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_566 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 8 (640262) 69.0 kV to LOWELL 7 (640261) 115.0 kV to LOWELL T1 9 (643096) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_567 | 3 Phase fault on ORLEANS7 115.00 (640310) 115 kV Bus a. Apply fault at the ORLEANS7 115.00 (640310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS8 (640311) 69.0 kV to ORLEANS7 (640310) 115.0 kV to ORLEANS T1 9 (643120) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_568 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_569 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_570 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T1 9 (643157) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_571 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T2 9 (643158) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_572 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_573 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_574 | 3 Phase fault on BASSETT 7115.00 (640580) 115 kV Bus a. Apply fault at the BASSETT 7115.00 (640580) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 8 (640581) 69.0 kV to BASSETT 7 (640580) 115.0 kV to BASSETT T1 9 (643180) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_575 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_576 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_577 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_578 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_579 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_580 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_581 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_582 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_583 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_584 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_585 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_586 | 3 Phase fault on MISSION7 115.00 (652482) 115 kV Bus a. Apply fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MISSION7 (652482) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_587 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_001 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_002 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_003 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_004 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_005 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_006 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_007 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_008 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_009 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_010 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_011 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_012 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_014 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_015 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_017 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_018 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_019 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_020 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_021 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_022 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_023 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_024 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_025 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_026 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_027 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_028 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_029 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_030 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_031 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_032 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_033 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_036 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_037 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_040 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_041 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_042 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_043 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_044 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_045 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_046 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_047 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_048 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply Fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 b.2. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SALIX 5 161.00 (635235) 161 kV Bus a. Apply Fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.3. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CRWFRD 5 161.00 (635330) 161 kV Bus a. Apply Fault at the CRWFRD 5 161.00 (635330) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.2. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.3. CRWFRD 5 (635330) 161.0 kV to NEWHRVST 9 (635331) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.4. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 b.3. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.4. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.6. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.7. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.8. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 b.9. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. HOSK.T89 (640230) 34.5 kV to HOSKINS4 (640227) 230.0 kV Two Winding #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 b.5. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply Fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.3. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT19 (643039) 13.8 kV Three Winding #1 b.4. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT29 (643040) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.3. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.4. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply Fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.2. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.3. AINSWRT7 (640051) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 b.4. AINSWRT9 (640053) 34.5 kV to AINSWRT7 (640051) 115.0 kV Two Winding #1 b.5. AINSWRT7 (640051) 115.0 kV to AINSWRT8 (640052) 69.0 kV to AINSWORTHT29 (643002) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on AINSWND7 115.00 (640050) 115 kV Bus a. Apply Fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWND.PLTD (640025) 34.5 kV Two Winding #1 b.2. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.3. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.4. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.4. BELDEN 7 (640080) 115.0 kV to BELDEN 8 (640081) 69.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to CANADY1G (640005) 13.8 kV Two Winding #1 b.2. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 b.3. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.4. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #2 b.5. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 b.6. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on COZAD 7 115.00 (640144) 115 kV Bus a. Apply Fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COZAD 7 (640144) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 b.2. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 b.3. COZAD 7 (640144) 115.0 kV to COZAD 8 (640145) 69.0 kV to COZAD T2 9 (643174) 13.8 kV Three Winding #1 b.4. COZAD 7 (640144) 115.0 kV to COZAD 9 (640146) 34.5 kV to COZAD T1 9 (643043) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CRETE__7 115.00 (640153) 115 kV Bus a. Apply Fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.3. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T1 9 (643048) 13.8 kV Three Winding #1 b.4. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T2 9 (643049) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply Fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 b.2. LXNGTN 7 (640256) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 b.3. LXNGTN 7 (640256) 115.0 kV to LEXNGTN8 (640257) 69.0 kV to LEXINGTONT29 (643093) 13.8 kV Three Winding #1 b.4. LXNGTN 7 (640256) 115.0 kV to LEXNGTN9 (640258) 34.5 kV to LEXINGTONT19 (643094) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply Fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. LOWELL 7 (640261) 115.0 kV to PROSSER7 (640321) 115.0 kV Transmission Circuit #1 b.4. LOWELL 7 (640261) 115.0 kV to LOWELL 8 (640262) 69.0 kV to LOWELL T1 9 (643096) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on MINDEN 7 115.00 (640275) 115 kV Bus a. Apply Fault at the MINDEN 7 115.00 (640275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. MINDEN 7 (640275) 115.0 kV to MINDEN 9 (640276) 34.5 kV to MINDEN T1 9 (643102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T1 9 (643112) 13.8 kV Three Winding #1 b.5. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T2 9 (643113) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply Fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT19 (643110) 13.8 kV Three Winding #1 b.5. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT29 (643111) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.3. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.4. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.5. OAKLAND7 (640300) 115.0 kV to OAKLAND9 (640301) 34.5 kV to OAKLAND T1 9 (643114) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on PAULINE7 115.00 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.4. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 b.5. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.6. PAULINE7 (640313) 115.0 kV to PAULINE8 (640314) 69.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on STNTN.N7 115.00 (640363) 115 kV Bus a. Apply Fault at the STNTN.N7 115.00 (640363) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. STNTN.N7 (640363) 115.0 kV to STNTN.N9 (640364) 34.5 kV to STANTN.N T19 (643145) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on TEKAMAH7 115.00 (640378) 115 kV Bus a. Apply Fault at the TEKAMAH7 115.00 (640378) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.2. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 b.3. TEKAMAH7 (640378) 115.0 kV to TEKAMAH9 (640379) 34.5 kV to TEKAMAH T2 9 (643152) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on TOWER 7 115.00 (640383) 115 kV Bus a. Apply Fault at the TOWER 7 115.00 (640383) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.2. RIVERDL7 (640331) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.3. TOWER 9 (640385) 12.5 kV to TOWER 7 (640383) 115.0 kV Two Winding #1 b.4. TOWER 7 (640383) 115.0 kV to TOWER A9 (640384) 34.5 kV to TOWER T2 9 (643154) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on VALENTN7 115.00 (640392) 115 kV Bus a. Apply Fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.2. HARMONY7 (640210) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.3. VALENTN7 (640392) 115.0 kV to VALTN.W7 (640394) 115.0 kV Transmission Circuit #1 b.4. VALENTN7 (640392) 115.0 kV to VALENTN9 (640393) 34.5 kV to VALENTINET19 (643160) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.3. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.5. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET29 (643081) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.3. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to G20-013-TAP (764445) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.3. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET29 (643081) 13.8 kV Three Winding #1 b.9. HOLDREG7 (640224) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.3. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREGE 8 (640448) 69.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 b.9. HOLDREG7 (640224) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.8. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.6. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on MISSION7 115.00 (652482) 115 kV Bus a. Apply Fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARMONY7 (640210) 115.0 kV to ST.FRANC (640351) 115.0 kV Transmission Circuit #1 b.2. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 b.3. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #1 b.4. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #2 b.5. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.6. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.7. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.8. WINNER 7 (652494) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.3. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply Fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. ROCKRPDMUNI8 (658122) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.3. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 b.4. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.5. RKRPDTAP-LO8 (659714) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.6. LESTERSS-LO8 (659722) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.7. STEEN -LO8 (659726) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.8. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.3. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.4. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.5. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.6. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.7. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on SPENCER5 161.00 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.2. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.3. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.4. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.5. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.6. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on MISSION7 115.00 (652482) 115 kV Bus a. Apply Fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 b.2. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #1 b.3. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #2 b.4. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.5. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.6. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.7. MISSION7 (652482) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on NEBCTY1G 18.000 (645011) 18 kV Bus a. Apply Fault at the NEBCTY1G 18.000 (645011) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEBCTY1G (645011) 18.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on NEBCTY2G 23.000 (645012) 23 kV Bus a. Apply Fault at the NEBCTY2G 23.000 (645012) 23 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEBCTY2G (645012) 23.0 kV to Generator #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on S1367 5 161.00 (646367) 161 kV Bus a. Apply Fault at the S1367 5 161.00 (646367) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on S1256 5 161.00 (646256) 161 kV Bus a. Apply Fault at the S1256 5 161.00 (646256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on S1255 5 161.00 (646255) 161 kV Bus a. Apply Fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1341 5 (646341) 161.0 kV to Load #O0 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on S1361 5 161.00 (646361) 161 kV Bus a. Apply Fault at the S1361 5 161.00 (646361) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1361 5 (646361) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.2. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on SARPY 5G 13.800 (645035) 13.80000019 kV Bus a. Apply Fault at the SARPY 5G 13.800 (645035) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to Generator #4 b.3. SARPY 5G (645035) 13.8 kV to Generator #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.2. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1211T39 (645127) 13.8 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.4. S1211 5 (646211) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 b.2. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.4. S1299 5 (646299) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1211T49 (645128) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on S1227 5 161.00 (646227) 161 kV Bus a. Apply Fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on S1232 5 161.00 (646232) 161 kV Bus a. Apply Fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on S1233 5 161.00 (646233) 161 kV Bus a. Apply Fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 b.2. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.3. S1235 5 (646235) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on S1236 5 161.00 (646236) 161 kV Bus a. Apply Fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on S1249 5 161.00 (646249) 161 kV Bus a. Apply Fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 b.5. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.3. S1211 5 (646211) 161.0 kV to Load #O0 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1211 5 (646211) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FC1A 5 (645100) 161.0 kV to FC1A3 9 (645103) 4.2 kV Two Winding #1 b.2. FC1A 5 (645100) 161.0 kV to FC1A4 9 (645104) 4.2 kV Two Winding #1 b.3. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.4. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.5. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.6. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.3. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.4. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1278 5 (646278) 161.0 kV to Load #O0 b.2. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1278 5 (646278) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.3. S1278 5 (646278) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 b.9. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.6. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.7. S1260 5 (646260) 161.0 kV to load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to Load #O0 b.2. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on S1287 5 161.00 (646287) 161 kV Bus a. Apply Fault at the S1287 5 161.00 (646287) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1298 5 (646298) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.2. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on S1291 5 161.00 (646291) 161 kV Bus a. Apply Fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on S1345 5 161.00 (646345) 161 kV Bus a. Apply Fault at the S1345 5 161.00 (646345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply Fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 b.2. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.3. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.4. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.4. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.2. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.3. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.4. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.5. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.6. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.7. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. SUB701 5 (635003) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply Fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on MONONA 5 161.00 (635300) 161 kV Bus a. Apply Fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to IDA GRV B1 9 (635207) 34.5 kV Two Winding #1 b.2. IDA CO 3 (635206) 345.0 kV to IDA GRV B2 9 (635208) 34.5 kV Two Winding #1 b.3. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to IDA GRV B1 9 (635207) 34.5 kV Two Winding #1 b.2. IDA CO 3 (635206) 345.0 kV to IDA GRV B2 9 (635208) 34.5 kV Two Winding #1 b.3. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FALLOW 3 (635590) 345.0 kV to ARBR HL 3 (635580) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to GLACIAL EDGE (637009) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. ARBR HL 3 (635580) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B1 9 (635401) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply Fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. GARD AVE 3 (635219) 345.0 kV to RICHLAND W (637024) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B2 9 (635402) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to Load #M2 b.2. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on SHAYS_230 230.00 (530610) 230 kV Bus a. Apply Fault at the SHAYS_230 230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.5. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply Fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 27FLETCHER7 (650228) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.3. 27FLETCHER7 (650228) 115.0 kV to 33SUPERIOR7 (650233) 115.0 kV Transmission Circuit #1 b.4. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.5. 27FLETCHER7 (650228) 115.0 kV to 27&FL 9 (650328) 12.5 kV to 281TERTIARY (650528) 9.2 kV Three Winding #1 b.6. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply Fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAVEY 7 (640155) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.3. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.4. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.5. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 b.6. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on TBGS_A 7 115.00 (650277) 115 kV Bus a. Apply Fault at the TBGS_A 7 115.00 (650277) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TBGS 4G (650004) 13.8 kV to TBGS LFG G (650010) 4.2 kV Two Winding #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.4. TBGS_A 7 (650277) 115.0 kV to TBGS 4G (650004) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply Fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on TBGS_B 7 115.00 (650278) 115 kV Bus a. Apply Fault at the TBGS_B 7 115.00 (650278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TBGS 4G (650004) 13.8 kV to TBGS LFG G (650010) 4.2 kV Two Winding #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.4. TBGS_A 7 (650277) 115.0 kV to TBGS 4G (650004) 13.8 kV Two Winding #1 b.5. TBGS_B 7 (650278) 115.0 kV to TBGS 1G (650001) 13.8 kV Two Winding #1 b.6. TBGS_B 7 (650278) 115.0 kV to TBGS 2G (650002) 13.8 kV Two Winding #1 b.7. TBGS_B 7 (650278) 115.0 kV to TBGS 3G (650003) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. TBGS_B 7 (650278) 115.0 kV to TBGS 1G (650001) 13.8 kV Two Winding #1 b.5. TBGS_B 7 (650278) 115.0 kV to TBGS 2G (650002) 13.8 kV Two Winding #1 b.6. TBGS_B 7 (650278) 115.0 kV to TBGS 3G (650003) 13.8 kV Two Winding #1 b.7. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply Fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 120&ALVO 7 (650279) 115.0 kV to 120&ALVO 9 (650379) 12.5 kV to 791TERTIARY (650579) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on WAVERLY 7 115.00 (650283) 115 kV Bus a. Apply Fault at the WAVERLY 7 115.00 (650283) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.3. WAVERLY 7 (650283) 115.0 kV to WAVERLY A9 (650383) 13.2 kV to 831TERTIARY (650583) 7.2 kV Three Winding #1 b.4. WAVERLY 7 (650283) 115.0 kV to WAVERLY B9 (650483) 12.5 kV to 832TERTIARY (650683) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on WAGENER 7 115.00 (650285) 115 kV Bus a. Apply Fault at the WAGENER 7 115.00 (650285) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to HALLAM3G (640021) 13.8 kV Two Winding #1 b.2. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to SHELDN1G (640019) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SHELDN2G (640020) 13.8 kV Two Winding #1 b.2. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLM1G (640010) 23.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.3. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.3. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 b.2. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 8 (640446) 69.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 b.5. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on S900 8 69.000 (647900) 69 kV Bus a. Apply Fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 979TP 8 (647079) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.2. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 b.3. 979TP 8 (647079) 69.0 kV to S979 8 (647979) 69.0 kV Transmission Circuit #1 b.4. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.5. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.6. S900 8 (647900) 69.0 kV to S972 8 (647972) 69.0 kV Transmission Circuit #1 b.7. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on S902 8 69.000 (647902) 69 kV Bus a. Apply Fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 b.3. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.5. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.9. S906 N 8 (647006) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.2. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.4. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.9. S906 S 8 (647906) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on S907 8 69.000 (647907) 69 kV Bus a. Apply Fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.2. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.5. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.6. S909 8 (647909) 69.0 kV to S1209 5 (646209) 161.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.5. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.5. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 1G (645021) 13.8 kV to NO1 AUX9 (645121) 2.4 kV Two Winding #1 b.2. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.3. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.4. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 b.5. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.6. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on S914 8 69.000 (647914) 69 kV Bus a. Apply Fault at the S914 8 69.000 (647914) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.2. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.2. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.2. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_363 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.2. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.3. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.5. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on S918 8 69.000 (647918) 69 kV Bus a. Apply Fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.3. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on S919 8 69.000 (647919) 69 kV Bus a. Apply Fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 b.2. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.3. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.2. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.3. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 b.4. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on S930 8 69.000 (647930) 69 kV Bus a. Apply Fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on S930 8 69.000 (647930) 69 kV Bus a. Apply Fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.2. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on S939 8 69.000 (647939) 69 kV Bus a. Apply Fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on S939 8 69.000 (647939) 69 kV Bus a. Apply Fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on S983 8 69.000 (647983) 69 kV Bus a. Apply Fault at the S983 8 69.000 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on 991TP 8 69.000 (647091) 69 kV Bus a. Apply Fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 991TP 8 (647091) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 b.2. 991TP 8 (647091) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.3. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 b.4. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on FREM B 8 69.000 (647422) 69 kV Bus a. Apply Fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.2. FREM A 8 (647421) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.3. FREM B 8 (647422) 69.0 kV to FREM C 8 (647423) 69.0 kV Transmission Circuit #1 b.4. FREM B 8 (647422) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 b.5. FREM B 8 (647422) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on S937 8 69.000 (647937) 69 kV Bus a. Apply Fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S937 8 (647937) 69.0 kV to S902 8 (647902) 69.0 kV Transmission Circuit #1 b.2. S937 8 (647937) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on SBRIDGE T8 69.000 (635227) 69 kV Bus a. Apply Fault at the SBRIDGE T8 69.000 (635227) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SBRIDGE T8 (635227) 69.0 kV to NEAL N 8 (635204) 69.0 kV Transmission Circuit #1 b.2. SBRIDGE T8 (635227) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply Fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply Fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_381 | Single Phase Fault with Stuck Breaker on GOSPER 7 115.00 (640194) 115 kV Bus a. Apply Fault at the GOSPER 7 115.00 (640194) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GOSPER 7 (640194) 115.0 kV to CAMBRIG7 (640100) 115.0 kV Transmission Circuit #1 b.2. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_382 | Single Phase Fault with Stuck Breaker on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply Fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEFFREY7 (640238) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 b.2. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_383 | Single Phase Fault with Stuck Breaker on JOHN.1 7 115.00 (640240) 115 kV Bus a. Apply Fault at the JOHN.1 7 115.00 (640240) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHN.1 7 (640240) 115.0 kV to JEFFREY7 (640238) 115.0 kV Transmission Circuit #1 b.2. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_384 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.2. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_385 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to COLMB.E3 (640125) 345.0 kV Transmission Circuit #1 b.2. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_386 | Single Phase Fault with Stuck Breaker on STUART 7 115.00 (640367) 115 kV Bus a. Apply Fault at the STUART 7 115.00 (640367) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STUART 7 (640367) 115.0 kV to ATKINSN7 (640058) 115.0 kV Transmission Circuit #1 b.2. STUART 7 (640367) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_387 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_388 | Single Phase Fault with Stuck Breaker on TOBIAS 3345.00 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3345.00 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. TOBIAS 3 (640525) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_389 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_390 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_391 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_392 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.2. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_393 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_394 | Single Phase Fault with Stuck Breaker on S6846 8 69.000 (647846) 69 kV Bus a. Apply Fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6846 8 (647846) 69.0 kV to S914A 8 (647014) 69.0 kV Transmission Circuit #1 b.2. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_395 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_396 | Single Phase Fault with Stuck Breaker on G17-105TAP 161.00 (762069) 161 kV Bus a. Apply Fault at the G17-105TAP 161.00 (762069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to RAUN 5 (635201) 161.0 kV Transmission Circuit #1 b.2. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_397 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_398 | Single Phase Fault with Stuck Breaker on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply Fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-065-TAP (763031) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_399 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_400 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY4 (640102) 230.0 kV to C.CREEK4 (640093) 230.0 kV Transmission Circuit #1 b.2. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_401 | Single Phase Fault with Stuck Breaker on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply Fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_402 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_403 | Single Phase Fault with Stuck Breaker on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply Fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHN.LK7 (640244) 115.0 kV to JOHN.1 7 (640240) 115.0 kV Transmission Circuit #1 b.2. JOHN.LK7 (640244) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_404 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_405 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_406 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.2. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_407 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 b.2. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_408 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1210 5 (646210) 161.0 kV Transmission Circuit #1 b.2. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_409 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_410 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_411 | Single Phase Fault with Stuck Breaker on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply Fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&BLUFF 5 (650169) 161.0 kV to S1214 5 (646214) 161.0 kV Transmission Circuit #1 b.2. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_412 | Single Phase Fault with Stuck Breaker on CANADAY7 115.00 (640103) 115 kV Bus a. Apply Fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 b.2. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_413 | Single Phase Fault with Stuck Breaker on VALENTN7 115.00 (640392) 115 kV Bus a. Apply Fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALENTN7 (640392) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.2. VALENTN7 (640392) 115.0 kV to HARMONY7 (640210) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_414 | Single Phase Fault with Stuck Breaker on S909 8 69.000 (647909) 69 kV Bus a. Apply Fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_415 | Single Phase Fault with Stuck Breaker on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply Fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY-LNX3 (652864) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_416 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GR ISLD-LNX3 (653871) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_417 | Single Phase Fault with Stuck Breaker on 84&BLUFF 7 (650275) 115 kV Bus a. Apply Fault at the 84&BLUFF 7 (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_418 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_419 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_420 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_421 | Single Phase Fault with Stuck Breaker on AXTELL 7 (640066) 115 kV Bus a. Apply Fault at the AXTELL 7 (640066) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_422 | Single Phase Fault with Stuck Breaker on HOLDREG7 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_423 | Single Phase Fault with Stuck Breaker on JOHN.2 7 (640242) 115 kV Bus a. Apply Fault at the JOHN.2 7 (640242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHN.2 7 (640242) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_424 | Single Phase Fault with Stuck Breaker on S1281 5 (646281) 161 kV Bus a. Apply Fault at the S1281 5 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_425 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_426 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_427 | Single Phase Fault with Stuck Breaker on S3458 3 (645458) 345 kV Bus a. Apply Fault at the S3458 3 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_428 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_429 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_430 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_431 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_432 | Single Phase Fault with Stuck Breaker on S909 8 (647909) 69 kV Bus a. Apply Fault at the S909 8 (647909) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_433 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_434 | Single Phase Fault with Stuck Breaker on S1251 5 (646251) 161 kV Bus a. Apply Fault at the S1251 5 (646251) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_435 | Single Phase Fault with Stuck Breaker on AINSWRT7 (640051) 115 kV Bus a. Apply Fault at the AINSWRT7 (640051) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWRT7 (640051) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_436 | Single Phase Fault with Stuck Breaker on S1347 5 (646347) 161 kV Bus a. Apply Fault at the S1347 5 (646347) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1347 5 (646347) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_437 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_438 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_439 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_440 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_441 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES1 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES2 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES3 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.3. TBGS 1G (650001) 13.8 kV to Generator #1 b.4. TBGS 2G (650002) 13.8 kV to Generator #2 b.5. TBGS 3G (650003) 13.8 kV to Generator #3 b.6. TBGS 4G (650004) 13.8 kV to Generator #4 b.7. TBGS LFG G (650010) 4.2 kV to Generator #10 b.8. TBGS 1G (650001) 13.8 kV to Load #S1 b.9. TBGS 2G (650002) 13.8 kV to Load #S1 b.10. TBGS 3G (650003) 13.8 kV to Load #S1 b.11. TBGS 4G (650004) 13.8 kV to Load #S1 b.12. TBGS 1G (650001) 13.8 kV to remove bus # b.13. TBGS 2G (650002) 13.8 kV to remove bus # b.14. TBGS 3G (650003) 13.8 kV to remove bus # b.15. TBGS 4G (650004) 13.8 kV to remove bus # b.16. TBGS LFG G (650010) 4.2 kV to remove bus # b.17. TBGS_A 7 (650277) 115.0 kV to remove bus # b.18. TBGS_B 7 (650278) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES4 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES5 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.2. TBGS 1G (650001) 13.8 kV to Generator #1 b.3. TBGS 2G (650002) 13.8 kV to Generator #2 b.4. TBGS 3G (650003) 13.8 kV to Generator #3 b.5. TBGS 1G (650001) 13.8 kV to Load #S1 b.6. TBGS 2G (650002) 13.8 kV to Load #S1 b.7. TBGS 3G (650003) 13.8 kV to Load #S1 b.8. TBGS 1G (650001) 13.8 kV to remove bus # b.9. TBGS 2G (650002) 13.8 kV to remove bus # b.10. TBGS 3G (650003) 13.8 kV to remove bus # b.11. TBGS_B 7 (650278) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES6 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES7 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES8 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.2. TBGS 2G (650002) 13.8 kV to Generator #2 b.3. TBGS 3G (650003) 13.8 kV to Generator #3 b.4. TBGS 4G (650004) 13.8 kV to Generator #4 b.5. TBGS LFG G (650010) 4.2 kV to Generator #10 b.6. TBGS 1G (650001) 13.8 kV to Generator #1 b.7. TBGS 1G (650001) 13.8 kV to Load #S1 b.8. TBGS 2G (650002) 13.8 kV to Load #S1 b.9. TBGS 3G (650003) 13.8 kV to Load #S1 b.10. TBGS 1G (650001) 13.8 kV to remove bus # b.11. TBGS 2G (650002) 13.8 kV to remove bus # b.12. TBGS 3G (650003) 13.8 kV to remove bus # b.13. TBGS_B 7 (650278) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW1 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.3. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW10 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW11 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW12 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW13 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW14 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW15 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW16 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW17 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW2 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.3. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW3 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW4 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW5 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW6 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.4. BUCKE_WTG (530705) 0.7 kV to remove bus # b.5. BUCKW_WTG (530708) 0.7 kV to remove bus # b.6. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.7. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.8. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.9. BUCKW_TERT (530706) 13.8 kV to remove bus # b.10. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.11. BUCKE_TERT (530709) 13.8 kV to remove bus # b.12. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW7 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW8 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW9 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD1 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD2 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.3. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD3 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.3. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.4. COOPER1G (640009) 22.0 kV to Generator #1 b.5. COOPER1G (640009) 22.0 kV to Load #S1 b.6. COOPER1G (640009) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD4 | Single Phase Fault with Stuck Breaker on TWIN CH4 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 b.3. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.4. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD5 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD6 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD7 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD1 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD10 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD11 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD12 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to remove bus # b.2. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD13 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD14 | Single Phase Fault with Stuck Breaker on S1361 5 (646361) 161 kV Bus a. Apply Fault at the S1361 5 (646361) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD15 | Single Phase Fault with Stuck Breaker on S1217 5 (646217) 161 kV Bus a. Apply Fault at the S1217 5 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to remove bus # b.2. S1217T19 (648217) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD16 | Single Phase Fault with Stuck Breaker on S1244 5 (646244) 161 kV Bus a. Apply Fault at the S1244 5 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1244 5 (646244) 161.0 kV to Load #O0 b.4. S1244 5 (646244) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD17 | Single Phase Fault with Stuck Breaker on S1305 5 (646305) 161 kV Bus a. Apply Fault at the S1305 5 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1305 5 (646305) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 b.4. S1305 5 (646305) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD18 | Single Phase Fault with Stuck Breaker on S1210 5 (646210) 161 kV Bus a. Apply Fault at the S1210 5 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 b.4. S1210 5 (646210) 161.0 kV to Load #O0 b.5. S1210 5 (646210) 161.0 kV to Load #OW | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD19 | Single Phase Fault with Stuck Breaker on S1251 5 (646251) 161 kV Bus a. Apply Fault at the S1251 5 (646251) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.3. S1341 5 (646341) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.4. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.5. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.6. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.7. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.8. S3459 3 (645459) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.9. S1297 9 (649297) 13.8 kV to Load #O0 b.10. S1297 9 (649297) 13.8 kV to remove bus # b.11. S1297 9 (649297) 13.8 kV to Generator #1 b.12. S3451 3 (645451) 345.0 kV to remove bus # b.13. S3451T39 (648251) 13.8 kV to remove bus # b.14. S3451T49 (648351) 13.8 kV to remove bus # b.15. S1297 5 (646297) 161.0 kV to remove bus # b.16. S1305 5 (646305) 161.0 kV to remove bus # b.17. S1341 5 (646341) 161.0 kV to remove bus # b.18. S1298 5 (646298) 161.0 kV to remove bus # b.19. FC1A 5 (645100) 161.0 kV to remove bus # b.20. FC1A3 9 (645103) 4.2 kV to remove bus # b.21. FC1A4 9 (645104) 4.2 kV to remove bus # b.22. S1251 5 (646251) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD2 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD20 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S1297 9 (649297) 13.8 kV to Generator #1 b.3. S1297 9 (649297) 13.8 kV to Load #O0 b.4. S1297 9 (649297) 13.8 kV to remove bus # b.5. S3459 3 (645459) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.6. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.7. S1237 5 (646237) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.8. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.9. S1341 5 (646341) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.10. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.11. S3451T49 (648351) 13.8 kV to remove bus # b.12. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.13. S1297 5 (646297) 161.0 kV to remove bus # b.14. S3451T39 (648251) 13.8 kV to remove bus # b.15. S3451 3 (645451) 345.0 kV to remove bus # b.16. S1305 5 (646305) 161.0 kV to remove bus # b.17. S1341 5 (646341) 161.0 kV to remove bus # b.18. S1298 5 (646298) 161.0 kV to remove bus # b.19. FC1A 5 (645100) 161.0 kV to remove bus # b.20. FC1A3 9 (645103) 4.2 kV to remove bus # b.21. FC1A4 9 (645104) 4.2 kV to remove bus # b.22. S1251 5 (646251) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD21 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.3. S918 8 (647918) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 b.4. S939 8 (647939) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 b.5. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.6. S3459T39 (648259) 13.8 kV to remove bus # b.7. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.8. S1231 5 (646231) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 b.9. S1347 5 (646347) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 b.10. S1231 5 (646231) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #2 b.11. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.12. S1250 5 (646250) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 b.13. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.14. S1250 5 (646250) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #2 b.15. S921 8 (647921) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 b.16. S937 8 (647937) 69.0 kV to remove bus # b.17. S909 8 (647909) 69.0 kV to remove bus # b.18. S1209T19 (648209) 13.8 kV to remove bus # b.19. S3459 3 (645459) 345.0 kV to remove bus # b.20. S3459T69 (648359) 13.8 kV to remove bus # b.21. S1209 5 (646209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD22 | Single Phase Fault with Stuck Breaker on S1220 5 (646220) 161 kV Bus a. Apply Fault at the S1220 5 (646220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1220 5 (646220) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.3. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.4. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.5. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.6. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.7. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 b.8. S1211T19 (648211) 13.8 kV to remove bus # b.9. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.10. S950 8 (647950) 69.0 kV to remove bus # b.11. S1250T19 (648250) 13.8 kV to remove bus # b.12. N OMA 4G (645024) 15.0 kV to Generator #4 b.13. N OMA 4G (645024) 15.0 kV to remove bus # b.14. N OMA 5G (645025) 20.0 kV to Generator #5 b.15. N OMA 5G (645025) 20.0 kV to remove bus # b.16. S1299 5 (646299) 161.0 kV to remove bus # b.17. S1286 5 (646286) 161.0 kV to remove bus # b.18. S1211 5 (646211) 161.0 kV to remove bus # b.19. S1297 9 (649297) 13.8 kV to Generator #1 b.20. NO4 AUX9 (645124) 2.4 kV to Load #S1 b.21. NO5 AUX9 (645125) 4.2 kV to Load #S1 b.22. S1211T39 (645127) 13.8 kV to Load #S1 b.23. S1211T39 (645127) 13.8 kV to Load #S2 b.24. S1211T39 (645127) 13.8 kV to Load #S3 b.25. S1211T39 (645127) 13.8 kV to Load #S4 b.26. S1211T39 (645127) 13.8 kV to Load #S5 b.27. S1211T49 (645128) 13.8 kV to Load #S1 b.28. S1211T49 (645128) 13.8 kV to Load #S2 b.29. S1211T49 (645128) 13.8 kV to Load #S3 b.30. S1211T49 (645128) 13.8 kV to Load #S4 b.31. S1211T49 (645128) 13.8 kV to Load #S5 b.32. S1250 5 (646250) 161.0 kV to Load #O0 b.33. S1297 9 (649297) 13.8 kV to Load #O0 b.34. NO4 AUX9 (645124) 2.4 kV to remove bus # b.35. NO5 AUX9 (645125) 4.2 kV to remove bus # b.36. S1211T39 (645127) 13.8 kV to remove bus # b.37. S1211T49 (645128) 13.8 kV to remove bus # b.38. S1297 5 (646297) 161.0 kV to remove bus # b.39. S1297 9 (649297) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD23 | Single Phase Fault with Stuck Breaker on CBLUFFS5 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to CBLUFFS5 (635001) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.3. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.4. S1206T19 (648206) 13.8 kV to remove bus # b.5. S1216 5 (646216) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.6. S1232 5 (646232) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.7. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.8. S3456T49 (648256) 13.8 kV to remove bus # b.9. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.10. S938 8 (647938) 69.0 kV to S906 N 8 (647006) 69.0 kV Transmission Circuit #1 b.11. S924 8 (647924) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.12. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.13. S1206T29 (648306) 13.8 kV to remove bus # b.14. SARPY 3G (645033) 13.8 kV to Generator #3 b.15. SARPY 3G (645033) 13.8 kV to remove bus # b.16. SCBSD G (645030) 4.2 kV to remove bus # b.17. SARPY 4G (645034) 13.8 kV to Generator #4 b.18. SARPY 4G (645034) 13.8 kV to remove bus # b.19. SARPY 5G (645035) 13.8 kV to Generator #5 b.20. SARPY 5G (645035) 13.8 kV to remove bus # b.21. S1206 5 (646206) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD24 | Single Phase Fault with Stuck Breaker on S1216 5 (646216) 161 kV Bus a. Apply Fault at the S1216 5 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1216 5 (646216) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.3. S1206T19 (648206) 13.8 kV to remove bus # b.4. S1206 5 (646206) 161.0 kV to CBLUFFS5 (635001) 161.0 kV Transmission Circuit #1 b.5. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.6. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.7. S3456T49 (648256) 13.8 kV to remove bus # b.8. S1232 5 (646232) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.9. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.10. S916 8 (647916) 69.0 kV to S906 N 8 (647006) 69.0 kV Transmission Circuit #1 b.11. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.12. S1206T29 (648306) 13.8 kV to remove bus # b.13. SARPY 3G (645033) 13.8 kV to Generator #3 b.14. SARPY 3G (645033) 13.8 kV to remove bus # b.15. SCBSD G (645030) 4.2 kV to remove bus # b.16. SARPY 4G (645034) 13.8 kV to Generator #4 b.17. SARPY 4G (645034) 13.8 kV to remove bus # b.18. SARPY 5G (645035) 13.8 kV to Generator #5 b.19. SARPY 5G (645035) 13.8 kV to remove bus # b.20. S1206 5 (646206) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD25 | Single Phase Fault with Stuck Breaker on S1286 5 (646286) 161 kV Bus a. Apply Fault at the S1286 5 (646286) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1286 5 (646286) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.3. S1220 5 (646220) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.4. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 b.5. S1201T19 (648201) 13.8 kV to remove bus # b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.7. S1206T19 (648206) 13.8 kV to remove bus # b.8. S1229 5 (646229) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.9. S1201 5 (646201) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD26 | Single Phase Fault with Stuck Breaker on S1361 5 (646361) 161 kV Bus a. Apply Fault at the S1361 5 (646361) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1361 5 (646361) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.3. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.4. S1259 5 (646259) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.5. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 b.6. S3455T39 (648355) 13.8 kV to remove bus # b.7. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.8. S3455T19 (648255) 13.8 kV to remove bus # b.9. S1255 5 (646255) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD27 | Single Phase Fault with Stuck Breaker on S1221 5 (646221) 161 kV Bus a. Apply Fault at the S1221 5 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1221 5 (646221) 161.0 kV Transmission Circuit #1 b.2. S1255 5 (646255) 161.0 kV to S1221 5 (646221) 161.0 kV Transmission Circuit #1 b.3. S940 8 (647940) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD28 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.5. S1341 5 (646341) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.7. S3451T49 (648351) 13.8 kV to remove bus # b.8. S1251 5 (646251) 161.0 kV to S3451 3 (645451) 345.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 b.9. S3451T39 (648251) 13.8 kV to remove bus # b.10. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.11. S1297 5 (646297) 161.0 kV to remove bus # b.12. FC1A 5 (645100) 161.0 kV to remove bus # b.13. FC1A3 9 (645103) 4.2 kV to remove bus # b.14. FC1A4 9 (645104) 4.2 kV to remove bus # b.15. S1251 5 (646251) 161.0 kV to remove bus # b.16. S1297 9 (649297) 13.8 kV to Generator #1 b.17. S1297 9 (649297) 13.8 kV to Load #O0 b.18. S1297 9 (649297) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD3 | Single Phase Fault with Stuck Breaker on S3458 3 (645458) 345 kV Bus a. Apply Fault at the S3458 3 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD4 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD5 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to Load #O0 b.3. S1206 5 (646206) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.4. S1206 5 (646206) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD6 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD7 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD8 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to Load #O0 b.3. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD9 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.3. S1216 5 (646216) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FALLOW 3 (635590) 345.0 kV to ARBR HL 3 (635580) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. ARBR HL 3 (635580) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. to AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Open # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_001 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_002 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_003 | 3 Phase fault on 5ADAIR1 161.00 (344004) 161 kV Bus a. Apply fault at the 5ADAIR1 161.00 (344004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR1 (344004) 161.0 kV to 2ADAIR 1 (346005) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_004 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_005 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.2. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_006 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_007 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_008 | 3 Phase fault on 5COMPTN 161.00 (300719) 161 kV Bus a. Apply fault at the 5COMPTN 161.00 (300719) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_009 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.3. BUFORD 5 (504440) 161.0 kV to NORFORK5 (505448) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_010 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.2. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_011 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_012 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_013 | 3 Phase fault on 5GRANDVIEW% 161.00 (338099) 161 kV Bus a. Apply fault at the 5GRANDVIEW% 161.00 (338099) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_014 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and Osborn (541503) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_015 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_016 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_017 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_018 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_019 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_020 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_021 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_022 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_023 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_024 | 3 Phase fault on CONCRDTP2 69.000 (541523) 69 kV Bus a. Apply fault at the CONCRDTP2 69.000 (541523) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to CONCRDTP2 (541523) 69.0 kV Transmission Circuit #1 b.2. CONCORD2 (541319) 69.0 kV to CONCRDTP2 (541523) 69.0 kV Transmission Circuit #1 b.3. CONCORD2 (541319) 69.0 kV to ENBRIDGE PS2 (541542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_025 | 3 Phase fault on FAYETVLTP2 69.000 (541383) 69 kV Bus a. Apply fault at the FAYETVLTP2 69.000 (541383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to FAYETVLTP2 (541383) 69.0 kV Transmission Circuit #1 b.2. WBURGP 2 (541268) 69.0 kV to FAYETVLTP2 (541383) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on GRDVWTP2 69.000 (541284) 69 kV Bus a. Apply fault at the GRDVWTP2 69.000 (541284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 b.3. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.4. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.5. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.6. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_028 | 3 Phase fault on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 b.3. FREEMAN2 (541291) 69.0 kV to FREEMAN_SP2 (541540) 69.0 kV Transmission Circuit #1 b.4. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.5. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 b.6. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_029 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 b.2. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_030 | 3 Phase fault on HLDENTP2 69.000 (541386) 69 kV Bus a. Apply fault at the HLDENTP2 69.000 (541386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to CNTRVIEW2 (541385) 69.0 kV Transmission Circuit #1 b.2. HOLDEN 2 (541278) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.3. RGREEN 2 (541279) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 b.4. CNTRVIEW2 (541385) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.5. HLDENTP2 (541386) 69.0 kV to KNGSVIL 2 (541387) 69.0 kV Transmission Circuit #1 b.6. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_031 | 3 Phase fault on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.3. POSTOAK2 (541300) 69.0 kV to POSTOAK1 (541373) 34.5 kV to POSTOAK_TER1 (541374) 2.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_032 | 3 Phase fault on CLNTPLT_CAP269.000 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP269.000 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_033 | 3 Phase fault on LEXNTON2 69.000 (541265) 69 kV Bus a. Apply fault at the LEXNTON2 69.000 (541265) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNTON2 (541265) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_034 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_035 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_036 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_037 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_038 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_039 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_040 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_041 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_042 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_043 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_044 | 3 Phase fault on NAVY 5 161.00 (542989) 161 kV Bus a. Apply fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_045 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_046 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_047 | 3 Phase fault on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_048 | 3 Phase fault on NORTON 5 161.00 (543064) 161 kV Bus a. Apply fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 b.2. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. NORTON 5 (543064) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_049 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_050 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_051 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. MERRIAM_CAP5 (542947) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_052 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_053 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_054 | 3 Phase fault on SWAVCAP2 69.000 (543012) 69 kV Bus a. Apply fault at the SWAVCAP2 69.000 (543012) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.2. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.3. SWAVCAP2 (543012) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips A20-001 (765236, 765241) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_055 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_056 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_057 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_058 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_059 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_060 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_061 | 3 Phase fault on CORDER 2 69.000 (543097) 69 kV Bus a. Apply fault at the CORDER 2 69.000 (543097) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.2. CORDER 2 (543097) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.3. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.4. DOVER2 (543101) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.5. CORDERTP2 (543657) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.6. CORDER 2 (543097) 69.0 kV to CORDER1 (543150) 12.5 kV to CORDER_TER1 (543151) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips A20-001 (765236, 765241) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_062 | 3 Phase fault on WHGNSVL2 69.000 (543102) 69 kV Bus a. Apply fault at the WHGNSVL2 69.000 (543102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNTON2 (541265) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.2. 13&40 2 (541266) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.3. MAYVWTP2 (543096) 69.0 kV to AMOCOPL2 (543100) 69.0 kV Transmission Circuit #1 b.4. CTY HIG2 (543098) 69.0 kV to HIGNSVL2 (543099) 69.0 kV Transmission Circuit #1 b.5. HIGNSVL2 (543099) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 b.6. AMOCOPL2 (543100) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 b.7. HIGNSVL2 (543099) 69.0 kV to HGNSVL1 (543152) 12.5 kV to HGNSVL_TER1 (543153) 2.4 kV Three Winding #1 b.8. WHGNSVL2 (543102) 69.0 kV to WHGNSVL1 (543154) 12.5 kV to WHGNSVL_TER1 (543155) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_063 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_064 | 3 Phase fault on KCSOUTH5 161.00 (541245) 161 kV Bus a. Apply fault at the KCSOUTH5 161.00 (541245) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCSOUTH5 (541245) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_065 | 3 Phase fault on OSAWTM_CAP5 161.00 (543135) 161 kV Bus a. Apply fault at the OSAWTM_CAP5 161.00 (543135) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWTM_CAP5 (543135) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_066 | 3 Phase fault on SWAVCAP5 161.00 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 161.00 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_067 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_068 | 3 Phase fault on COLLEG 2 69.000 (530574) 69 kV Bus a. Apply fault at the COLLEG 2 69.000 (530574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 b.2. COLLEG 2 (530574) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_069 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_070 | 3 Phase fault on BKHLTAP2 69.000 (530589) 69 kV Bus a. Apply fault at the BKHLTAP2 69.000 (530589) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.2. SUSANK 2 (530571) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.3. BNK HL 2 (530572) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.4. HITHMN 2 (530573) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_071 | 3 Phase fault on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_072 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_073 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_074 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_075 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_076 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_077 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_078 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_079 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_080 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_081 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_082 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_083 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_084 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips RUBART (531201, 531202) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_085 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_086 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_087 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_088 | 3 Phase fault on SETAB 3 115.00 (531464) 115 kV Bus a. Apply fault at the SETAB 3 115.00 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_089 | 3 Phase fault on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_090 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_091 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_092 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_093 | 3 Phase fault on GRANTTP3 115.00 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 115.00 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_094 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_095 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_096 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_097 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_098 | 3 Phase fault on SAT-TAP3 115.00 (531442) 115 kV Bus a. Apply fault at the SAT-TAP3 115.00 (531442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASKELL3 (531374) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.2. HASKELL3 (531374) 115.0 kV to SEWARD-3 (531467) 115.0 kV Transmission Circuit #1 b.3. PIONTAP3 (531392) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.4. SAT-TAP3 (531442) 115.0 kV to SATMKEC3 (539691) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_099 | 3 Phase fault on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_100 | 3 Phase fault on WILLIAM3 115.00 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 115.00 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_101 | 3 Phase fault on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.3. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_102 | 3 Phase fault on GANO 3 115.00 (531493) 115 kV Bus a. Apply fault at the GANO 3 115.00 (531493) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.3. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_103 | 3 Phase fault on KSAVWTP3 115.00 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 115.00 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_104 | 3 Phase fault on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_105 | 3 Phase fault on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.2. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.3. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_106 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_107 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_108 | 3 Phase fault on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_109 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_110 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_111 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_112 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_113 | 3 Phase fault on WALDO 3 115.00 (539698) 115 kV Bus a. Apply fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_114 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_115 | 3 Phase fault on PHLBURG3 115.00 (539685) 115 kV Bus a. Apply fault at the PHLBURG3 115.00 (539685) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_116 | 3 Phase fault on GLENELD3 115.00 (539663) 115 kV Bus a. Apply fault at the GLENELD3 115.00 (539663) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.2. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_117 | 3 Phase fault on JEWELL 3 115.00 (539669) 115 kV Bus a. Apply fault at the JEWELL 3 115.00 (539669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.2. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.4. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_118 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_119 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_120 | 3 Phase fault on 5LOGAN 161.00 (301161) 161 kV Bus a. Apply fault at the 5LOGAN 161.00 (301161) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MANSFDMN (300095) 161.0 kV to 5LOGAN (301161) 161.0 kV Transmission Circuit #1 b.2. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_121 | 3 Phase fault on WAVERLY3 115.00 (533278) 115 kV Bus a. Apply fault at the WAVERLY3 115.00 (533278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.2. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_122 | 3 Phase fault on MNTCLLO3 115.00 (533281) 115 kV Bus a. Apply fault at the MNTCLLO3 115.00 (533281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_123 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_124 | 3 Phase fault on MUND 3 115.00 (533282) 115 kV Bus a. Apply fault at the MUND 3 115.00 (533282) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_125 | 3 Phase fault on 166TH 3 115.00 (533233) 115 kV Bus a. Apply fault at the 166TH 3 115.00 (533233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.3. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_126 | 3 Phase fault on MIDLADN3 115.00 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 115.00 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_127 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_128 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_129 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_130 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_131 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_132 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_133 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_134 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_135 | 3 Phase fault on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_136 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_137 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_138 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_139 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_140 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_141 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_142 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_143 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_144 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_145 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_146 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | 1- Protection disabled without any impact on stability. 2- Acceleration factor was reduced to 0.1.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_147 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G16-153 (588363), G17-086 (589243) and G17-221 (760307) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_148 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_149 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_150 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_151 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_152 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_153 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_154 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips JEC units (532651, 532652, 532653), G18-057 (762925), LEC units (532662, 532663), EMPEC (532740, 532741, 532742, 532743), Alcyone (542955), MRWY-WG2 (539105), WELLING2 (533560), G17-068 (589063), G17-226 (760644), G17-220 (760287) and G17-195 (762282) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_155 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips EMPEC (532740, 532741, 532742, 532743) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_156 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips EMPEC (532740, 532741, 532742, 532743) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_157 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_158 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_159 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_160 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_161 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_162 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_163 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_164 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_165 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_166 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_167 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_168 | 3 Phase fault on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.3. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_169 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_170 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 b.2. SC3MILL2 (533552) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 b.3. SC3MILL2 (533552) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 b.4. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_171 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC7CRES2 (533555) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_172 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_173 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_174 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_175 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_176 | 3 Phase fault on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_177 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_178 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_179 | 3 Phase fault on STROTHR2 69.000 (533556) 69 kV Bus a. Apply fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_180 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_181 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_182 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_183 | 3 Phase fault on EDWARVL3 115.00 (533238) 115 kV Bus a. Apply fault at the EDWARVL3 115.00 (533238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_184 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_185 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_186 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_187 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_188 | 3 Phase fault on UDALL 2 69.000 (533559) 69 kV Bus a. Apply fault at the UDALL 2 69.000 (533559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UDALL 2 (533559) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_189 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_190 | 3 Phase fault on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_191 | 3 Phase fault on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_192 | 3 Phase fault on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.4. NICHOL XF1 1 (549940) 13.2 kV to NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_193 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.3. MILL XF1 1 (549946) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_194 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 b.3. MILL XF2 1 (549948) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_195 | 3 Phase fault on HAWTHRN4 138.00 (510413) 138 kV Bus a. Apply fault at the HAWTHRN4 138.00 (510413) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 (510396) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.2. CHELSA4 (510410) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.3. CHELSA4 (510410) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 b.4. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_196 | 3 Phase fault on GROVE 5 161.00 (510411) 161 kV Bus a. Apply fault at the GROVE 5 161.00 (510411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 5 (510411) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_197 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_198 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_199 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_200 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_201 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_202 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_203 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_204 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_205 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_206 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 (510418) 69.0 kV to VINTAJC4 (510417) 138.0 kV to VINJT1-1 (510367) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_207 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_208 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_209 | 3 Phase fault on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_210 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_211 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_212 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_213 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_214 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_215 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_216 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_217 | 3 Phase fault on LOCSTGVKM 5 161.00 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 161.00 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_218 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_219 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_220 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_221 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_222 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_223 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_224 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_225 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_226 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_227 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_228 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_229 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_230 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_231 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_232 | 3 Phase fault on TONECE7 345.00 (512750) 345 kV Bus a. Apply fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_233 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_234 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.3. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_235 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.3. OCHILTREE 3 (523154) 115.0 kV to OCHILTREE 6 (523155) 230.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_236 | 3 Phase fault on TEXAS_CNTY 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_237 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_238 | 3 Phase fault on TEXAS_CNTY 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_239 | 3 Phase fault on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_240 | 3 Phase fault on COLE 3115.00 (523120) 115 kV Bus a. Apply fault at the COLE 3115.00 (523120) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 3 (523120) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_241 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. TXFARMS 3 (523140) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 b.3. SPEARMAN 3 (523186) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_242 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_243 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_244 | 3 Phase fault on WADE_TP 3115.00 (523145) 115 kV Bus a. Apply fault at the WADE_TP 3115.00 (523145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIPSCOMB 3 (523135) 115.0 kV to WADE_TP 3 (523145) 115.0 kV Transmission Circuit #1 b.2. WADE_TP 3 (523145) 115.0 kV to WADE 3 (523147) 115.0 kV Transmission Circuit #1 b.3. WADE_TP 3 (523145) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_245 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.5. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.7. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.8. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.9. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.10. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.11. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_246 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_247 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_248 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_249 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_250 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_251 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_252 | 3 Phase fault on BOL431 5 161.00 (547493) 161 kV Bus a. Apply fault at the BOL431 5 161.00 (547493) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_253 | 3 Phase fault on JOP391 5 161.00 (547593) 161 kV Bus a. Apply fault at the JOP391 5 161.00 (547593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.2. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_254 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. HOC404A1 (547715) 12.5 kV to HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_255 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_256 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_257 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_258 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_259 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_260 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_261 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MPLTAP (300036) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 b.3. 5MPLTAP (300036) 161.0 kV to 5LATHROP (344923) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_262 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_263 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_264 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.3. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.4. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_265 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_266 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_267 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_268 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_269 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_270 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_271 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_272 | 3 Phase fault on 5HIGBEEB1 161.00 (300066) 161 kV Bus a. Apply fault at the 5HIGBEEB1 161.00 (300066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HIGBEEB1 (300066) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_273 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_274 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_275 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_276 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_277 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_278 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_279 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_280 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_281 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_282 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5BTLFD (300348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_283 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_284 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5RIVRDL (300726) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_285 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_286 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_287 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_288 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to 5MORGANXF2 (301622) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_289 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_290 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_291 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_292 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_293 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_294 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_295 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOL (301040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_296 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_297 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_298 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_299 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_300 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_301 | 3 Phase fault on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STKAEC (300118) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_302 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5THMHLB2 (300132) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_303 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5THMHILTFERB (301511) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_304 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HOLDENB2 (300124) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_305 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB3 (300133) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_306 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5BEVIER (300381) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_307 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_308 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THOMHLXF1 (301508) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_309 | 3 Phase fault on 5THMHLB3 161.00 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 161.00 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5MEADVLB1 (300207) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_310 | 3 Phase fault on 5THMHLB3 161.00 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 161.00 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5THOMHLXF3 (301506) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_311 | 3 Phase fault on 5THMHLB3 161.00 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 161.00 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5THOMHLU3SU (301507) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_312 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2MOCITY (300304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_313 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_314 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_315 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_316 | 3 Phase fault on 2ELM 69.000 (300327) 69 kV Bus a. Apply fault at the 2ELM 69.000 (300327) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELM (300327) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_317 | 3 Phase fault on 5BTLFD 161.00 (300348) 161 kV Bus a. Apply fault at the 5BTLFD 161.00 (300348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_318 | 3 Phase fault on 2BEAMAN 69.000 (300527) 69 kV Bus a. Apply fault at the 2BEAMAN 69.000 (300527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEAMAN (300527) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_319 | 3 Phase fault on 2DRESDN 69.000 (300528) 69 kV Bus a. Apply fault at the 2DRESDN 69.000 (300528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DRESDN (300528) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_320 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_321 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_322 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_323 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_324 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_325 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_326 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_327 | 3 Phase fault on 2MALTAJ 69.000 (300536) 69 kV Bus a. Apply fault at the 2MALTAJ 69.000 (300536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAJ (300536) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_328 | 3 Phase fault on 2NAPTON 69.000 (300538) 69 kV Bus a. Apply fault at the 2NAPTON 69.000 (300538) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NAPTON (300538) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_329 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Instantaneous frequency relay trips GI91 (99915) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_330 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_331 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2FLORNC (300553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_332 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_333 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2MEDOC (300653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_334 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_335 | 3 Phase fault on 2ASHGRV 69.000 (300657) 69 kV Bus a. Apply fault at the 2ASHGRV 69.000 (300657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_336 | 3 Phase fault on 2BOWRML 69.000 (300659) 69 kV Bus a. Apply fault at the 2BOWRML 69.000 (300659) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOWRML (300659) 69.0 kV to 2REEDS (300751) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_337 | 3 Phase fault on 2CRANE 69.000 (300667) 69 kV Bus a. Apply fault at the 2CRANE 69.000 (300667) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CRANE (300667) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_338 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_339 | 3 Phase fault on 2ELWOOD 69.000 (300669) 69 kV Bus a. Apply fault at the 2ELWOOD 69.000 (300669) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_340 | 3 Phase fault on 5NIXA-1 161.00 (300678) 161 kV Bus a. Apply fault at the 5NIXA-1 161.00 (300678) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_341 | 3 Phase fault on 2PRDYTP 69.000 (300679) 69 kV Bus a. Apply fault at the 2PRDYTP 69.000 (300679) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PRDYTP (300679) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_342 | 3 Phase fault on 2VERONA 69.000 (300680) 69 kV Bus a. Apply fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_343 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_344 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_345 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_346 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_347 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_348 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_349 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_350 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_351 | 3 Phase fault on 2DMNDGR 69.000 (300744) 69 kV Bus a. Apply fault at the 2DMNDGR 69.000 (300744) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDGR (300744) 69.0 kV to 2DMNDTP (300745) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_352 | 3 Phase fault on 2DMNDTP 69.000 (300745) 69 kV Bus a. Apply fault at the 2DMNDTP 69.000 (300745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDTP (300745) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_353 | 3 Phase fault on 2DMNDTP 69.000 (300745) 69 kV Bus a. Apply fault at the 2DMNDTP 69.000 (300745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_354 | 3 Phase fault on 2NEOSAC 69.000 (300748) 69 kV Bus a. Apply fault at the 2NEOSAC 69.000 (300748) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to 2NEOSHO (300750) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_355 | 3 Phase fault on 2NEOSAC 69.000 (300748) 69 kV Bus a. Apply fault at the 2NEOSAC 69.000 (300748) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to 2SWTWT (300758) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_356 | 3 Phase fault on 2REEDS 69.000 (300751) 69 kV Bus a. Apply fault at the 2REEDS 69.000 (300751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_357 | 3 Phase fault on 2ELKTON 69.000 (300773) 69 kV Bus a. Apply fault at the 2ELKTON 69.000 (300773) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELKTON (300773) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_358 | 3 Phase fault on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2EUDORA (300774) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_359 | 3 Phase fault on 2FRSTOE 69.000 (300776) 69 kV Bus a. Apply fault at the 2FRSTOE 69.000 (300776) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FRSTOE (300776) 69.0 kV to 2WARSAW (300790) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_360 | 3 Phase fault on 2KNOBBY 69.000 (300780) 69 kV Bus a. Apply fault at the 2KNOBBY 69.000 (300780) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KNOBBY (300780) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_361 | 3 Phase fault on 2WARSAW 69.000 (300790) 69 kV Bus a. Apply fault at the 2WARSAW 69.000 (300790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WARSAW (300790) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_362 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_363 | 3 Phase fault on 2DAMSCUS 69.000 (300804) 69 kV Bus a. Apply fault at the 2DAMSCUS 69.000 (300804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DAMSCUS (300804) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_364 | 3 Phase fault on 2ICONTP 69.000 (300809) 69 kV Bus a. Apply fault at the 2ICONTP 69.000 (300809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ICONTP (300809) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_365 | 3 Phase fault on 2OSCEOL 69.000 (300811) 69 kV Bus a. Apply fault at the 2OSCEOL 69.000 (300811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_366 | 3 Phase fault on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_367 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_368 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_369 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_370 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_371 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_372 | 3 Phase fault on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOKC (301522) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_373 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_374 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_375 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_376 | 3 Phase fault on BEAVER 5 161.00 (505480) 161 kV Bus a. Apply fault at the BEAVER 5 161.00 (505480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_377 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_378 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_379 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_380 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_381 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_382 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_383 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_384 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_385 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_386 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_387 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_388 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_389 | 3 Phase fault on NIXA 2 69.000 (505501) 69 kV Bus a. Apply fault at the NIXA 2 69.000 (505501) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_390 | 3 Phase fault on NIXA DT2 69.000 (505541) 69 kV Bus a. Apply fault at the NIXA DT2 69.000 (505541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA DT2 (505541) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_391 | 3 Phase fault on NIXA NE2 69.000 (505544) 69 kV Bus a. Apply fault at the NIXA NE2 69.000 (505544) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA NE2 (505544) 69.0 kV to JRPS 69B-2 2 (549903) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_392 | 3 Phase fault on DELWARE4 138.00 (510379) 138 kV Bus a. Apply fault at the DELWARE4 138.00 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_393 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_394 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_395 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_396 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_397 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_398 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_399 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_400 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_401 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_402 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_403 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_404 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_405 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_406 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_407 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_408 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_409 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_410 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_411 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_412 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_413 | 3 Phase fault on MOSCOW 2 69.000 (531384) 69 kV Bus a. Apply fault at the MOSCOW 2 69.000 (531384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOW 2 (531384) 69.0 kV to MOSCOWT2 (531385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_414 | 3 Phase fault on MOSCOWT2 69.000 (531385) 69 kV Bus a. Apply fault at the MOSCOWT2 69.000 (531385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOWT2 (531385) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_415 | 3 Phase fault on NORTH6 2 69.000 (531388) 69 kV Bus a. Apply fault at the NORTH6 2 69.000 (531388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6 2 (531388) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_416 | 3 Phase fault on NORTH6T2 69.000 (531389) 69 kV Bus a. Apply fault at the NORTH6T2 69.000 (531389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6T2 (531389) 69.0 kV to WALKMYR2 (531404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_417 | 3 Phase fault on ROLLA 2 115.00 (531395) 115 kV Bus a. Apply fault at the ROLLA 2 115.00 (531395) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLA 2 (531395) 115.0 kV to ABBK 2 (531494) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_418 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WOODS 2 (531406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_419 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_420 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_421 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Instantaneous frequency relay trips JEC units (532651, 532652, 532653), LEC (532662, 532663), EMPEC (532740, 532741, 532742, 532743) and MRWY-WG2 (539105) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_422 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_423 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_424 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_425 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips WAVERGEN1 (532957) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_426 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_427 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_428 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_429 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_430 | 3 Phase fault on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_431 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_432 | 3 Phase fault on EUDORA 3 115.00 (533240) 115 kV Bus a. Apply fault at the EUDORA 3 115.00 (533240) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_433 | 3 Phase fault on ARKCTYW2 69.000 (533540) 69 kV Bus a. Apply fault at the ARKCTYW2 69.000 (533540) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to ARKCTYE2 (533542) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_434 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_435 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_436 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_437 | 3 Phase fault on FLORAL 2 69.000 (533545) 69 kV Bus a. Apply fault at the FLORAL 2 69.000 (533545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORAL 2 (533545) 69.0 kV to FLORALJ2 (533546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_438 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_439 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to TIMBER 2 (533557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_440 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_441 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_442 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_443 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_444 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_445 | 3 Phase fault on PRAIRIE2 69.000 (533562) 69 kV Bus a. Apply fault at the PRAIRIE2 69.000 (533562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAIRIE2 (533562) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_446 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to BURLIND2 (533625) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_447 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to CC1BURL2 (533628) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_448 | 3 Phase fault on NEOSHON2 69.000 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 69.000 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_449 | 3 Phase fault on EAST SUB 2 69.000 (533990) 69 kV Bus a. Apply fault at the EAST SUB 2 69.000 (533990) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_450 | 3 Phase fault on WEST SUB 2 69.000 (533991) 69 kV Bus a. Apply fault at the WEST SUB 2 69.000 (533991) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_451 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and frequency protection relays trip G18-116 (763335) and G19-051 (763826) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_452 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_453 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_454 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_455 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G19-068 (763970) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_456 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_457 | 3 Phase fault on CLNTPLT_CAP269.000 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP269.000 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_458 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_459 | 3 Phase fault on WSTELEC_CAP5161.00 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5161.00 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_460 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_461 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_462 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_463 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_464 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_465 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_466 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_467 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_468 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_469 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_470 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_471 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_472 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_473 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_474 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_475 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_476 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_477 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_478 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to GRDVWE 5 (541223) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_479 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_480 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_481 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_482 | 3 Phase fault on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_483 | 3 Phase fault on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_484 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_485 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_486 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_487 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_488 | 3 Phase fault on NRAYMORETP 5161.00 (541231) 161 kV Bus a. Apply fault at the NRAYMORETP 5161.00 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORETP 5 (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_489 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_490 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_491 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_492 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_493 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_494 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_495 | 3 Phase fault on LEX69 2 69.000 (541264) 69 kV Bus a. Apply fault at the LEX69 2 69.000 (541264) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX69 2 (541264) 69.0 kV to LEXNTON2 (541265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_496 | 3 Phase fault on 13&40 2 69.000 (541266) 69 kV Bus a. Apply fault at the 13&40 2 69.000 (541266) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to ODESSA 2 (541267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_497 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to KELHYS 2 (541273) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_498 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_499 | 3 Phase fault on SEDS 2 69.000 (541272) 69 kV Bus a. Apply fault at the SEDS 2 69.000 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_500 | 3 Phase fault on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_501 | 3 Phase fault on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_502 | 3 Phase fault on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_503 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_504 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_505 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_506 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to HSNVLN 2 (541297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_507 | 3 Phase fault on LNGVW 2 69.000 (541282) 69 kV Bus a. Apply fault at the LNGVW 2 69.000 (541282) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to BRMALL 2 (541283) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_508 | 3 Phase fault on HSNVL 2 69.000 (541295) 69 kV Bus a. Apply fault at the HSNVL 2 69.000 (541295) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVLSW2 (541296) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_509 | 3 Phase fault on HSNVLSW2 69.000 (541296) 69 kV Bus a. Apply fault at the HSNVLSW2 69.000 (541296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLSW2 (541296) 69.0 kV to HSNVLN 2 (541297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_510 | 3 Phase fault on HSNVLSW2 69.000 (541296) 69 kV Bus a. Apply fault at the HSNVLSW2 69.000 (541296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLSW2 (541296) 69.0 kV to GRDNCTY2 (541298) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_511 | 3 Phase fault on GRDNCTY2 69.000 (541298) 69 kV Bus a. Apply fault at the GRDNCTY2 69.000 (541298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY2 (541298) 69.0 kV to GUNNPS2 (541299) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_512 | 3 Phase fault on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_513 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBW5 (541336) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_514 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_515 | 3 Phase fault on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161.0 kV to WAFBE5 (541338) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_516 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_517 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_518 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_519 | 3 Phase fault on PECULR 5 161.00 (541342) 161 kV Bus a. Apply fault at the PECULR 5 161.00 (541342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECULR 5 (541342) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_520 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_521 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-058 (764382, 764376, 764379) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_522 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-058 (764379) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_523 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_524 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_525 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-196 (762303) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_526 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-196 (762303) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_527 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_528 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_529 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-073 (764394, 764391) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_530 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_531 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_532 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_533 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_534 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_535 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_536 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_537 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_538 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_539 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_540 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_541 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_542 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_543 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_544 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_545 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_546 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_547 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_548 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_549 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_550 | 3 Phase fault on PFLUMM 5 161.00 (542979) 161 kV Bus a. Apply fault at the PFLUMM 5 161.00 (542979) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_551 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_552 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_553 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-007 (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283) and G20-079 (764311) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_554 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-007 (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283), and G20-079 (764311) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_555 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | No | Voltage relay trips G20-007 (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283), G20-079 (764311) units. After disabling voltage relay, instantaneous frequency relays trips G20-007 units. Disabling the relay demonstrates that there are slow dampening oscillations in the angle of WCGS U1 (532751). | Protection disabled at G20-007 and G20-079 units and reduce clearing time to 4.75 cycles. TO submitted fault sheet states the clearing time to be 4.75 cycles.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_556 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_557 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_558 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_559 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_560 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_561 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_562 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_563 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_564 | 3 Phase fault on SWAVCAP5 161.00 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 161.00 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_565 | 3 Phase fault on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_566 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_567 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_568 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_569 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_570 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_571 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_572 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_573 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_574 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_575 | 3 Phase fault on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LENEXA 5 (543038) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_576 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_577 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-073 (764394, 764391) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_578 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to NEASTOTTW5 (543166) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_579 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-073 (764394, 764391) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_580 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_581 | 3 Phase fault on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_582 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_583 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_584 | 3 Phase fault on S.OTTWA5 161.00 (543066) 161 kV Bus a. Apply fault at the S.OTTWA5 161.00 (543066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.OTTWA5 (543066) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-073 (764394, 764391) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_585 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_586 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_587 | 3 Phase fault on S EAST 5 161.00 (543071) 161 kV Bus a. Apply fault at the S EAST 5 161.00 (543071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S EAST 5 (543071) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_588 | 3 Phase fault on MRSHLJT5 161.00 (543072) 161 kV Bus a. Apply fault at the MRSHLJT5 161.00 (543072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRSHLJT5 (543072) 161.0 kV to MIAMI_ 5 (543073) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_589 | 3 Phase fault on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSTVAL5 (543077) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-073 (764394, 764391) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_590 | 3 Phase fault on OSAWAT 5 161.00 (543112) 161 kV Bus a. Apply fault at the OSAWAT 5 161.00 (543112) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWAT 5 (543112) 161.0 kV to OSAWTM_CAP5 (543135) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_591 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON416J2 (547402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_592 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_593 | 3 Phase fault on MON376 2 69.000 (547401) 69 kV Bus a. Apply fault at the MON376 2 69.000 (547401) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376 2 (547401) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_594 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON352 2 (547406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_595 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_596 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_597 | 3 Phase fault on MON311J2 69.000 (547407) 69 kV Bus a. Apply fault at the MON311J2 69.000 (547407) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON311J2 (547407) 69.0 kV to MON311 2 (547408) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_598 | 3 Phase fault on SCAM66 2 69.000 (547409) 69 kV Bus a. Apply fault at the SCAM66 2 69.000 (547409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCAM66 2 (547409) 69.0 kV to SCM66T 2 (547455) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_599 | 3 Phase fault on COL282 2 69.000 (547411) 69 kV Bus a. Apply fault at the COL282 2 69.000 (547411) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL282 2 (547411) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_600 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_601 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_602 | 3 Phase fault on WEB105 2 69.000 (547431) 69 kV Bus a. Apply fault at the WEB105 2 69.000 (547431) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB105 2 (547431) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_603 | 3 Phase fault on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUPTAP 2 (547436) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_604 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to EXP4492 (547439) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_605 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_606 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_607 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_608 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_609 | 3 Phase fault on JAS344T2 69.000 (547450) 69 kV Bus a. Apply fault at the JAS344T2 69.000 (547450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAS344T2 (547450) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_610 | 3 Phase fault on SCM66T 2 69.000 (547455) 69 kV Bus a. Apply fault at the SCM66T 2 69.000 (547455) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCM66T 2 (547455) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_611 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_612 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_613 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_614 | 3 Phase fault on KOD471 2 69.000 (547463) 69 kV Bus a. Apply fault at the KOD471 2 69.000 (547463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOD471 2 (547463) 69.0 kV to DIA131 2 (547538) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_615 | 3 Phase fault on KOD471 2 69.000 (547463) 69 kV Bus a. Apply fault at the KOD471 2 69.000 (547463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOD471 2 (547463) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_616 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_617 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_618 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_619 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_620 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_621 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_622 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_623 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_624 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_625 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_626 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_627 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_628 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_629 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_630 | 3 Phase fault on ASB349 5 161.00 (547476) 161 kV Bus a. Apply fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204) and frequency relay trips G17-188 (760245, 760248) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_631 | 3 Phase fault on ASB349 5 161.00 (547476) 161 kV Bus a. Apply fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204) and frequency relay trips G17-188 (760245, 760248) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_632 | 3 Phase fault on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_633 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_634 | 3 Phase fault on LAR382 5 161.00 (547479) 161 kV Bus a. Apply fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-088 (764316) and G17-060 (588984, 588983) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_635 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_636 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_637 | 3 Phase fault on DEC392 5 161.00 (547484) 161 kV Bus a. Apply fault at the DEC392 5 161.00 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 (547484) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_638 | 3 Phase fault on CAR395 5 161.00 (547485) 161 kV Bus a. Apply fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_639 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_640 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_641 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_642 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_643 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_644 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_645 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_646 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_647 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to ORO110 2 (547534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_648 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_649 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_650 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_651 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_652 | 3 Phase fault on CAR108 2 69.000 (547532) 69 kV Bus a. Apply fault at the CAR108 2 69.000 (547532) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAR108 2 (547532) 69.0 kV to ATL109 2 (547533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_653 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_654 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to JOP360 2 (547581) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_655 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_656 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_657 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_658 | 3 Phase fault on NIX114 2 69.000 (547535) 69 kV Bus a. Apply fault at the NIX114 2 69.000 (547535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIX114 2 (547535) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_659 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_660 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MON152 2 (547540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_661 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_662 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_663 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_664 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_665 | 3 Phase fault on MON152 2 69.000 (547540) 69 kV Bus a. Apply fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_666 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_667 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_668 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to REP345 2 (547576) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_669 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_670 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_671 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to ROC296 2 (547560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_672 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to LIN314 2 (547563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_673 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to AND322 2 (547566) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_674 | 3 Phase fault on FRP217 2 69.000 (547545) 69 kV Bus a. Apply fault at the FRP217 2 69.000 (547545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRP217 2 (547545) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_675 | 3 Phase fault on GAT258 2 69.000 (547551) 69 kV Bus a. Apply fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_676 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_677 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_678 | 3 Phase fault on GAL278 2 69.000 (547555) 69 kV Bus a. Apply fault at the GAL278 2 69.000 (547555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAL278 2 (547555) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_679 | 3 Phase fault on TIP292 2 69.000 (547559) 69 kV Bus a. Apply fault at the TIP292 2 69.000 (547559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 2 (547559) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_680 | 3 Phase fault on COM381T2 69.000 (547579) 69 kV Bus a. Apply fault at the COM381T2 69.000 (547579) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COM381T2 (547579) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_681 | 3 Phase fault on JOP360 2 69.000 (547581) 69 kV Bus a. Apply fault at the JOP360 2 69.000 (547581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP360 2 (547581) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_682 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_683 | 3 Phase fault on JOP389 2 69.000 (547592) 69 kV Bus a. Apply fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_684 | 3 Phase fault on RNM393 2 69.000 (547595) 69 kV Bus a. Apply fault at the RNM393 2 69.000 (547595) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 2 (547595) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_685 | 3 Phase fault on GLF339 2 69.000 (547690) 69 kV Bus a. Apply fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_686 | 3 Phase fault on JRPS 69B-2 269.000 (549903) 69 kV Bus a. Apply fault at the JRPS 69B-2 269.000 (549903) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JRPS 69B-2 2 (549903) 69.0 kV to PLAINVIEW 2 (549905) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_687 | 3 Phase fault on JRPS 69B-2 269.000 (549903) 69 kV Bus a. Apply fault at the JRPS 69B-2 269.000 (549903) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JRPS 69B-2 2 (549903) 69.0 kV to TWIN OAKS 2 (549933) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_688 | 3 Phase fault on JRPS 69B-2 269.000 (549903) 69 kV Bus a. Apply fault at the JRPS 69B-2 269.000 (549903) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JRPS 69B-2 2 (549903) 69.0 kV to SEMINOLE 2 (549934) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_689 | 3 Phase fault on JAMES RIVER269.000 (549904) 69 kV Bus a. Apply fault at the JAMES RIVER269.000 (549904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER2 (549904) 69.0 kV to S HWY 65 2 (549908) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_690 | 3 Phase fault on JAMES RIVER269.000 (549904) 69 kV Bus a. Apply fault at the JAMES RIVER269.000 (549904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER2 (549904) 69.0 kV to HIGHWAY M 2 (549909) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_691 | 3 Phase fault on KICKAPOO 269.000 (549906) 69 kV Bus a. Apply fault at the KICKAPOO 269.000 (549906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KICKAPOO 2 (549906) 69.0 kV to SUNSET 2 (549907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_692 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to S HWY 65 2 (549908) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_693 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to FORT 2 (549914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_694 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to MONROE 2 (549923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_695 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to SEMINOLE 2 (549934) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_696 | 3 Phase fault on COX 269.000 (549910) 69 kV Bus a. Apply fault at the COX 269.000 (549910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_697 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to LAUREL 2 (549924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_698 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_699 | 3 Phase fault on DAYTON 269.000 (549913) 69 kV Bus a. Apply fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_700 | 3 Phase fault on MILL 269.000 (549918) 69 kV Bus a. Apply fault at the MILL 269.000 (549918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 2 (549918) 69.0 kV to CHAD 2 (549919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_701 | 3 Phase fault on CHAD 269.000 (549919) 69 kV Bus a. Apply fault at the CHAD 269.000 (549919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAD 2 (549919) 69.0 kV to HARGISS 2 (549920) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_702 | 3 Phase fault on HARGISS 269.000 (549920) 69 kV Bus a. Apply fault at the HARGISS 269.000 (549920) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARGISS 2 (549920) 69.0 kV to MAIN STREET2 (549921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_703 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to GRAND 2 (549922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_704 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_705 | 3 Phase fault on GRAND 269.000 (549922) 69 kV Bus a. Apply fault at the GRAND 269.000 (549922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 2 (549922) 69.0 kV to MONROE 2 (549923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_706 | 3 Phase fault on LAUREL 269.000 (549924) 69 kV Bus a. Apply fault at the LAUREL 269.000 (549924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAUREL 2 (549924) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_707 | 3 Phase fault on NICHOLS 269.000 (549925) 69 kV Bus a. Apply fault at the NICHOLS 269.000 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 2 (549925) 69.0 kV to FRISCO 2 (549926) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_708 | 3 Phase fault on FRISCO 269.000 (549926) 69 kV Bus a. Apply fault at the FRISCO 269.000 (549926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRISCO 2 (549926) 69.0 kV to N HWY13 2 (549927) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_709 | 3 Phase fault on N HWY13 269.000 (549927) 69 kV Bus a. Apply fault at the N HWY13 269.000 (549927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HWY13 2 (549927) 69.0 kV to NORTON 2 (549928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_710 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_711 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to NEERGARD 2 (549930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_712 | 3 Phase fault on NEERGARD 269.000 (549930) 69 kV Bus a. Apply fault at the NEERGARD 269.000 (549930) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEERGARD 2 (549930) 69.0 kV to LECOMPTE 2 (549931) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_713 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_714 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_715 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_716 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_717 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_718 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_719 | 3 Phase fault on MENTOR 5161.00 (549963) 161 kV Bus a. Apply fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_720 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_721 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_722 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_723 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 7HUBEN (300042) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_724 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_725 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF3 (301506) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_726 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF4 (301510) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_727 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_728 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_729 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_730 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_731 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_732 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHRP (300302) 69.0 kV to 5LATHRP (300091) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_733 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MORGAN (300782) 69.0 kV to 5MORGAN (300101) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_734 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NORTON (300540) 69.0 kV to 5NORTON (300105) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_735 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_736 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_737 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 5THMHILB1 (300120) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_738 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HOLDEN (300336) 69.0 kV to 5HOLDENB2 (300124) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_739 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_740 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_741 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_742 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_743 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_744 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to NEO184 5 (547471) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_745 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WASHBRN (300763) 69.0 kV to WASHBURN5 (505485) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_746 | 3 Phase fault on 5OSCEOL 161.00 (301040) 161 kV Bus a. Apply fault at the 5OSCEOL 161.00 (301040) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 5OSCEOL (301040) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_747 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_748 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TURKEYCRK (301401) 69.0 kV to 5TURKEYCRK (301370) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_749 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_750 | 3 Phase fault on 5LATHROP 161.00 (344923) 161 kV Bus a. Apply fault at the 5LATHROP 161.00 (344923) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHROP (346093) 69.0 kV to 5LATHROP (344923) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_751 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_752 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_753 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_754 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_755 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_756 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_757 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_758 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_759 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_760 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_761 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_762 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_763 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_764 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_765 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_766 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_767 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY2 (512741) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_768 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR41 (523098) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_769 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR11 (523092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_770 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_771 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_772 | 3 Phase fault on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_773 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to G06-44 (560577) 115.0 kV to NOVUS1_TR2 2 (560578) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_774 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_775 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_776 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_777 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_778 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 2 1 (525538) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_779 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to HUGOTON3 (531481) 115.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_780 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_781 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_782 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_783 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_784 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_785 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_786 | 3 Phase fault on SEWARD-3 115.00 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 115.00 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMSSWRD2 (531466) 69.0 kV to SEWARD-3 (531467) 115.0 kV to SEWARD 1 (531260) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_787 | 3 Phase fault on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_788 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_789 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_790 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_791 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_792 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_793 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_794 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_795 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_796 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_797 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_798 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_799 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_800 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_801 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_802 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_803 | 3 Phase fault on EDWRDVL5 161.00 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 161.00 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to EDWARVL3 (533238) 115.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_804 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_805 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_806 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_807 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_808 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_809 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_810 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_811 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_812 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_813 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_814 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_815 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_816 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_817 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_818 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_819 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to LNGVW 5 (541224) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_820 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_821 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_822 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_823 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_824 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_825 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN S2 (541320) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_826 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to LBRTYST5 (541248) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_827 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_828 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_829 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS2 (541290) 69.0 kV to BELTONS5 (541340) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_830 | 3 Phase fault on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_831 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_832 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-196 (762303) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_833 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_834 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_835 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_836 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_837 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_838 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_839 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_840 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_841 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH 12 (400) 13.8 kV Three Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_842 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-007 (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_843 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-007 (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_844 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_845 | 3 Phase fault on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to SWAVRLY5 (543063) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_846 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_847 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_848 | 3 Phase fault on ATL109 5 161.00 (547466) 161 kV Bus a. Apply fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_849 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_850 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_851 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_852 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_853 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 (547471) 161.0 kV to NEO184 2 (547543) 69.0 kV to NEO184B1 (547709) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_854 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_855 | 3 Phase fault on MON383 5 161.00 (547480) 161 kV Bus a. Apply fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_856 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_857 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_858 | 3 Phase fault on NOL435 5 161.00 (547496) 161 kV Bus a. Apply fault at the NOL435 5 161.00 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 5 (547496) 161.0 kV to NOL435 2 (547610) 69.0 kV to NOL435 1 (547720) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_859 | 3 Phase fault on CPK446 5 161.00 (547499) 161 kV Bus a. Apply fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_860 | 3 Phase fault on RNM393 5 161.00 (547500) 161 kV Bus a. Apply fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_861 | 3 Phase fault on SUB N-161 161.00 (548820) 161 kV Bus a. Apply fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_862 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_863 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_864 | 3 Phase fault on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_865 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to JAMES RIVER2 (549904) 69.0 kV to JRPS XF1 1 (549944) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_866 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to JRPS 69B-2 2 (549903) 69.0 kV to JRPS XF2 1 (549945) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_867 | 3 Phase fault on NORTON 5161.00 (549967) 161 kV Bus a. Apply fault at the NORTON 5161.00 (549967) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (549967) 161.0 kV to NORTON 2 (549928) 69.0 kV to NORTON XF1 1 (549942) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_868 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_869 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_870 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Instantaneous frequency relay trips GI91 (99915) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_871 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_872 | 3 Phase fault on 2WARSAW 69.000 (300790) 69 kV Bus a. Apply fault at the 2WARSAW 69.000 (300790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WARSAW (300790) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_873 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_874 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_875 | 3 Phase fault on MON383 2 69.000 (547591) 69 kV Bus a. Apply fault at the MON383 2 69.000 (547591) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 2 (547591) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_876 | 3 Phase fault on JOP430 2 69.000 (547608) 69 kV Bus a. Apply fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP430 2 (547608) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_877 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_878 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_879 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_880 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_001 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_002 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_003 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_004 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_005 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_006 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_007 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_008 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_009 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_010 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_011 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips RUBART (531201, 531202) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) and G17-221 (760307) units . | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_013 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | 1- Protection disabled without any impact on stability. 2- Acceleration factor was reduced to 0.1.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_014 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_015 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_016 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_017 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_018 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_019 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_020 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_021 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_022 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_023 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_024 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_025 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_026 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_027 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_028 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_029 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_030 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_031 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_032 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Instantaneous frequency relay trips G11-008 (539858), G19-058 (763895), G19-063 (763926) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_033 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Instantaneous frequency relay trips G11-008 (539858), G19-058 (763895), G19-063 (763926) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550), ROCKCK (541514) and LAKERD (541171) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550), ROCKCK (541514) and LAKERD (541171) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_036 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550), ROCKCK (541514) and LAKERD (541171) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_037 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_038 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_039 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_040 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_041 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_042 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_043 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_044 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_045 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_046 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_048 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_049 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Instantaneous frequency relay trips G17-018 (588633, 588637) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550), ROCKCK (541514) and LAKERD (541171) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_051 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550), ROCKCK (541514) and LAKERD (541171) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 b.3. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply Fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 b.2. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 b.3. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 b.4. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply Fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.3. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.4. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on KCSOUTH5 161.00 (541245) 161 kV Bus a. Apply Fault at the KCSOUTH5 161.00 (541245) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 b.2. NRAYMORETP 5 (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on STROTHR2 69.000 (533556) 69 kV Bus a. Apply Fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.2. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.3. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.4. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.5. EAST SUB 2 (533990) 69.0 kV to GEN-2020-003 (765085) 69.0 kV Transmission Circuit #1 b.6. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on OAK 2 69.000 (533547) 69 kV Bus a. Apply Fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.3. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.4. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.5. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.3. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on NORTON 5 161.00 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply Fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.4. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-007 units (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283). Disabling the relay demonstrates that there are slow dampening oscillations in the angle of WCGS U1 within the dampening factor requirements of SPP. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-007 units (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283). Disabling the relay demonstrates that there are slow dampening oscillations in the angle of WCGS U1 within the dampening factor requirements of SPP. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to ATLNTIC7 (542940) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to ATLNTIC7 (542940) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on PIONEER3 115.00 (531391) 115 kV Bus a. Apply Fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. HICKOCK3 (531378) 115.0 kV to PIONEER3 (531391) 115.0 kV Transmission Circuit #1 b.3. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.4. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.5. PIONEER3 (531391) 115.0 kV to ULYSPLT3 (531490) 115.0 kV Transmission Circuit #1 b.6. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 b.7. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.8. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 b.9. PIONEER3 (531391) 115.0 kV to PIONEER2 (531390) 69.0 kV to PIONEER1 (531251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply Fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to Trip Bus # b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.5. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.6. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.7. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.8. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.9. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 b.10. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.11. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.12. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.13. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.14. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WALDO 3 115.00 (539698) 115 kV Bus a. Apply Fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.3. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.4. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.5. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.6. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.7. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.8. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.9. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.10. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 b.11. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 b.12. SMITH-C3 (539693) 115.0 kV to SMITH-C1 (539731) 34.5 kV to SMITHC-T (539934) 7.2 kV Three Winding #1 b.13. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply Fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWNDTAP3 (531476) 115.0 kV to Trip Bus # b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. GRDNCTY3 (531445) 115.0 kV to S2 GEN 1 (531459) 13.8 kV Two Winding #1 b.4. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.5. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.6. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.3. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 b.4. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on JONES3 115.00 (531379) 115 kV Bus a. Apply Fault at the JONES3 115.00 (531379) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.3. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CIM-PLT3 (539654) 115.0 kV to CIM-PLT (539780) 13.8 kV Two Winding #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply Fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. GRDNCTY3 (531445) 115.0 kV to S2 GEN 1 (531459) 13.8 kV Two Winding #1 b.4. GRDNCTY3 (531445) 115.0 kV to S4 GEN 1 (531461) 13.2 kV Two Winding #1 b.5. GRDNCTY3 (531445) 115.0 kV to S5 GEN 1 (531462) 13.2 kV Two Winding #1 b.6. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.7. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.8. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.9. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.10. GRDNCTY3 (531445) 115.0 kV to GC-C 1 (531421) 34.5 kV to GC-CITY (531254) 13.8 kV Three Winding #1 b.11. GRDNCTY3 (531445) 115.0 kV to GARDNCY2 (531423) 69.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.4. SPF X3 1 (505495) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 b.4. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on AVOCA 5 161.00 (504000) 161 kV Bus a. Apply Fault at the AVOCA 5 161.00 (504000) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVOCA 5 (504000) 161.0 kV to BEAVER 5 (505480) 161.0 kV Transmission Circuit #1 b.2. AVOCA 5 (504000) 161.0 kV to EROGERS5 (506931) 161.0 kV Transmission Circuit #1 b.3. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 b.4. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on BEAVER 5 161.00 (505480) 161 kV Bus a. Apply Fault at the BEAVER 5 161.00 (505480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 b.2. BEAVER 5 (505480) 161.0 kV to EUREKA 5 (506932) 161.0 kV Transmission Circuit #1 b.3. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on STOCKTN5 161.00 (505498) 161 kV Bus a. Apply Fault at the STOCKTN5 161.00 (505498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 b.2. STOCKTN5 (505498) 161.0 kV to STK #1 1 (505500) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on TABLE R5 161.00 (505472) 161 kV Bus a. Apply Fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5RENOHLWTP (300130) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 b.2. 5RENOHLWTP (300130) 161.0 kV to 5RIVERSIDE (300805) 161.0 kV Transmission Circuit #1 b.3. 5RENOHLWTP (300130) 161.0 kV to 5RENOHLW (301129) 161.0 kV Transmission Circuit #1 b.4. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.5. 5COMPTN (300719) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 b.6. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.7. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.8. TABLE R5 (505472) 161.0 kV to TBR1&2 1 (505476) 13.8 kV Two Winding #1 b.9. TABLE R5 (505472) 161.0 kV to TBR3&4 1 (505478) 13.8 kV Two Winding #1 b.10. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.11. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.12. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.13. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on TABLE R5 161.00 (505472) 161 kV Bus a. Apply Fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.3. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.4. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.5. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.6. TABLE R5 (505472) 161.0 kV to TBR1&2 1 (505476) 13.8 kV Two Winding #1 b.7. TABLE R5 (505472) 161.0 kV to TBR3&4 1 (505478) 13.8 kV Two Winding #1 b.8. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.9. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.10. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.11. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply Fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2WASHBRN (300763) 69.0 kV to WASHBURN5 (505485) 161.0 kV Two Winding #1 b.2. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 b.3. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 b.4. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.5. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 b.6. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.2. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.3. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.5. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.6. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.7. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.8. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 b.2. 2JASPER (300649) 69.0 kV to 2MEDOC (300653) 69.0 kV Transmission Circuit #1 b.3. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.4. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.6. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.7. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.2. 2BOWRML (300659) 69.0 kV to 2REEDS (300751) 69.0 kV Transmission Circuit #1 b.3. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.4. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.6. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.2. 2DMNDGR (300744) 69.0 kV to 2DMNDTP (300745) 69.0 kV Transmission Circuit #1 b.3. 2DMNDTP (300745) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 b.4. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. 2NEOSHO (300750) 69.0 kV to 2SPGCTP (300754) 69.0 kV Transmission Circuit #1 b.6. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.7. 2SPGCTP (300754) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 b.8. 2SPGCTP (300754) 69.0 kV to 2SPURGNTP (300764) 69.0 kV Transmission Circuit #1 b.9. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.10. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 b.2. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.5. SPF X1 1 (505491) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ASHGRV (300657) 69.0 kV to 2CAVESP (300664) 69.0 kV Transmission Circuit #1 b.2. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 b.3. 2ASHGRV (300657) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 b.4. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 b.5. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 b.6. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #2 b.7. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply Fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.4. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.5. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 b.7. TRUMAN 5 (505502) 161.0 kV to TRU123 1 (505504) 13.8 kV Two Winding #1 b.8. TRUMAN 5 (505502) 161.0 kV to TRU456 1 (505506) 13.8 kV Two Winding #1 b.9. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.5. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.6. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.7. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. NXA X1 1 (505497) 13.8 kV to NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. NXA X2 1 (505499) 13.8 kV to NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on SPRINGH3 115.00 (533267) 115 kV Bus a. Apply Fault at the SPRINGH3 115.00 (533267) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.4. SPRINGH3 (533267) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply Fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on JTEC 5161.00 (549954) 161 kV Bus a. Apply Fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 b.2. JTEC GEN#1 1 (549890) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.3. JTEC CTS 1 (549891) 12.5 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.4. JTEC GEN#2 1 (549893) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.5. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.6. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.7. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply Fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 b.4. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.4. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply Fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JRPS GT1 1 (549900) 13.8 kV to JAMES RIVER5 (549961) 161.0 kV Two Winding #1 b.2. JRPS GT2 1 (549901) 13.8 kV to JAMES RIVER5 (549961) 161.0 kV Two Winding #1 b.3. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.4. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 b.5. JAMES RIVER5 (549961) 161.0 kV to JRPS 69B-2 2 (549903) 69.0 kV to JRPS XF2 1 (549945) 13.2 kV Three Winding #1 b.6. JAMES RIVER5 (549961) 161.0 kV to JAMES RIVER2 (549904) 69.0 kV to JRPS XF1 1 (549944) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on MILL 5161.00 (549962) 161 kV Bus a. Apply Fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.3. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.4. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on MENTOR 5161.00 (549963) 161 kV Bus a. Apply Fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 b.2. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.3. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on NORTON 5161.00 (549967) 161 kV Bus a. Apply Fault at the NORTON 5161.00 (549967) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 b.2. NORTON 5 (549967) 161.0 kV to NORTON 2 (549928) 69.0 kV to NORTON XF1 1 (549942) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on MC CARTNEY 5161.00 (549968) 161 kV Bus a. Apply Fault at the MC CARTNEY 5161.00 (549968) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCCARTNEY (301568) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #z1 b.2. MAC GT1&2 1 (549892) 13.8 kV to MC CARTNEY 5 (549968) 161.0 kV Two Winding #1 b.3. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.4. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.5. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.6. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on CLAY 5161.00 (549970) 161 kV Bus a. Apply Fault at the CLAY 5161.00 (549970) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.3. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.4. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on PIC WEST 5161.00 (549971) 161 kV Bus a. Apply Fault at the PIC WEST 5161.00 (549971) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit # b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on AFTON 5 161.00 (512632) 161 kV Bus a. Apply Fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.4. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 b.2. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 b.4. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.5. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.6. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 b.7. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 b.8. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 b.2. G20-072-TAP (764355) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 b.4. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 b.5. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.7. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 b.8. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 b.9. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON (345409) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.3. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply Fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.5. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply Fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 b.2. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z b.3. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.4. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 b.5. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply Fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.2. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.3. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.4. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.5. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.3. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.4. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on RIV167 5 161.00 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on NEO184 5 161.00 (547471) 161 kV Bus a. Apply Fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2NEOSAC (300748) 69.0 kV to NEO184 5 (547471) 161.0 kV Two Winding #1 b.2. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 b.3. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.4. NEO184 5 (547471) 161.0 kV to NEO184 2 (547543) 69.0 kV to NEO184B1 (547709) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.4. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply Fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.4. DAD368 5 (547478) 161.0 kV to GEN-2019-016 (763560) 161.0 kV Transmission Circuit #1 b.5. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.4. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on FIR417 5 161.00 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 161.00 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on OAK432 5 161.00 (547494) 161 kV Bus a. Apply Fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on NOL435 5 161.00 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 161.00 (547496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROVE 5 (510411) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.2. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.3. DEC392 5 (547484) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.4. NOL435 5 (547496) 161.0 kV to NOL435 2 (547610) 69.0 kV to NOL435 1 (547720) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on CPK446 5 161.00 (547499) 161 kV Bus a. Apply Fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.3. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply Fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.4. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.5. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.6. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-079-TAP (764310) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit # b.2. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-079-TAP (764310) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit # b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to A2G349 1 (547650) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 b.2. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.4. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.5. DAD368 5 (547478) 161.0 kV to GEN-2019-016 (763560) 161.0 kV Transmission Circuit #1 b.6. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 b.4. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on JOP422 5 161.00 (547607) 161 kV Bus a. Apply Fault at the JOP422 5 161.00 (547607) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to L3G3821 (547653) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to L2G382 1 (547652) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to L1G382 1 (547651) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.6. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.7. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 b.8. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 b.9. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.6. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 b.7. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply Fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.2. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 b.3. 5MAURER 2 (344558) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.3. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.4. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.5. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.6. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.7. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.8. EAST SUB 2 (533990) 69.0 kV to GEN-2020-003 (765085) 69.0 kV Transmission Circuit #1 b.9. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply Fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on NESCTY 3 115.00 (530607) 115 kV Bus a. Apply Fault at the NESCTY 3 115.00 (530607) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NESCTY 3 (530607) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NESCTY 3 (530607) 115.0 kV to NESS-CT1 (539722) 34.5 kV to NES-CT-T (539924) 13.8 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.9. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.10. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 b.2. HITCHLD_TR11 (523092) 13.2 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV Three Winding #1 b.3. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply Fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.3. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.4. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.5. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.6. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.7. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.8. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.9. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.10. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.11. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.12. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.13. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.14. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPNSPUR_COL1 (524298) 34.5 kV to SPNSPUR_TR11 (524297) 13.2 kV to SPNSPUR_COL7 (524299) 345.0 kV Three Winding #1 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #1 b.4. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 b.5. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.7. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.8. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on WEST SUB 2 69.000 (533991) 69 kV Bus a. Apply Fault at the WEST SUB 2 69.000 (533991) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEST SUB 2 (533991) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 b.2. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply Fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LATHRP (300091) 161.0 kV to 2LATHRP (300302) 69.0 kV Two Winding #1 b.2. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply Fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.2. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply Fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on 2VERONA 69.000 (300680) 69 kV Bus a. Apply Fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2VERONA (300680) 69.0 kV to 2PRDYTP (300679) 69.0 kV Transmission Circuit #1 b.2. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply Fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 b.2. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply Fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply Fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SHARSNV (301515) 161.0 kV to 2SHARSNV (300709) 69.0 kV Two Winding #1 b.2. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on GEN-2011-022345.00 (523215) 345 kV Bus a. Apply Fault at the GEN-2011-022345.00 (523215) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2011-022 (523215) 345.0 kV to G11-022XFMR1 (523211) 34.5 kV Two Winding #1 b.2. GEN-2011-022 (523215) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply Fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply Fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.2. NEOSHOS4 (533020) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on ARKCTYE2 69.000 (533542) 69 kV Bus a. Apply Fault at the ARKCTYE2 69.000 (533542) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARKCTYE2 (533542) 69.0 kV to ARKCTYW2 (533540) 69.0 kV Transmission Circuit #z1 b.2. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on PARIS 2 69.000 (533548) 69 kV Bus a. Apply Fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARIS 2 (533548) 69.0 kV to ARKCTYW2 (533540) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply Fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.2. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply Fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SC5SILV2 (533554) 69.0 kV to ARKCTYE2 (533542) 69.0 kV Transmission Circuit #1 b.2. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on BURLJCT2 69.000 (533626) 69 kV Bus a. Apply Fault at the BURLJCT2 69.000 (533626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on CC2SHAR2 69.000 (533629) 69 kV Bus a. Apply Fault at the CC2SHAR2 69.000 (533629) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC2SHAR2 (533629) 69.0 kV to CC5SHAR1 (533888) 12.5 kV Two Winding #1 b.2. CC2SHAR2 (533629) 69.0 kV to CC6SHAR1 (533889) 12.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply Fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROLLHLS3 (539643) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on CIM-PLT3 115.00 (539654) 115 kV Bus a. Apply Fault at the CIM-PLT3 115.00 (539654) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIM-PLT3 (539654) 115.0 kV to WALKMYR3 (531405) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to HAYNE3 (539640) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply Fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDSR 5 (541217) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply Fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WSTELEC5 (541222) 161.0 kV to WSTELEC_CAP5 (541149) 161.0 kV Transmission Circuit #r b.2. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply Fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDVWE 5 (541223) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 b.2. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply Fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LKWINBG5 (541243) 161.0 kV to PHILL 5 (541225) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on LEXNTON2 69.000 (541265) 69 kV Bus a. Apply Fault at the LEXNTON2 69.000 (541265) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEXNTON2 (541265) 69.0 kV to LEX69 2 (541264) 69.0 kV Transmission Circuit #1 b.2. LEXNTON2 (541265) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on 13&40 2 69.000 (541266) 69 kV Bus a. Apply Fault at the 13&40 2 69.000 (541266) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 13&40 2 (541266) 69.0 kV to ODESSA 2 (541267) 69.0 kV Transmission Circuit #1 b.2. 13&40 2 (541266) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on PHILL 5 161.00 (541225) 161 kV Bus a. Apply Fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 b.2. PHILL 2 (541280) 69.0 kV to RGREEN 2 (541279) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply Fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on ANCONDA2 69.000 (541292) 69 kV Bus a. Apply Fault at the ANCONDA2 69.000 (541292) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANCONDA2 (541292) 69.0 kV to FREEMAN2 (541291) 69.0 kV Transmission Circuit #1 b.2. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on HSNVLW 2 69.000 (541293) 69 kV Bus a. Apply Fault at the HSNVLW 2 69.000 (541293) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVLW 2 (541293) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on HSNVLS 2 69.000 (541294) 69 kV Bus a. Apply Fault at the HSNVLS 2 69.000 (541294) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVLS 2 (541294) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.2. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply Fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 b.2. HSNVL 2 (541295) 69.0 kV to HSNVLSW2 (541296) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply Fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTOAK2 (541300) 69.0 kV to WBURGP 2 (541268) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply Fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on BELTONS5 161.00 (541340) 161 kV Bus a. Apply Fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELTONS5 (541340) 161.0 kV to TURNER_RD5 (541259) 161.0 kV Transmission Circuit #1 b.2. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to PECULR 7 (541198) 345.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 5 (541342) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on RAYMORE 69.000 (541347) 69 kV Bus a. Apply Fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAYMORE (541347) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 b.2. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on KNGSVIL 2 69.000 (541387) 69 kV Bus a. Apply Fault at the KNGSVIL 2 69.000 (541387) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNGSVIL 2 (541387) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.2. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply Fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply Fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 b.2. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply Fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply Fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCYRUS5 (543057) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on MALTABN5 161.00 (543059) 161 kV Bus a. Apply Fault at the MALTABN5 161.00 (543059) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 b.2. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALSBRY5 (543062) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on PAOLA 5 161.00 (543069) 161 kV Bus a. Apply Fault at the PAOLA 5 161.00 (543069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAOLA 5 (543069) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 b.2. PAOLA 5 (543069) 161.0 kV to CENTENL5 (543067) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply Fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWAVRLY2 (543094) 69.0 kV to SWAVRLY5 (543063) 161.0 kV Two Winding #1 b.2. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on MAYVWTP2 69.000 (543096) 69 kV Bus a. Apply Fault at the MAYVWTP2 69.000 (543096) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAYVWTP2 (543096) 69.0 kV to LEXNTON2 (541265) 69.0 kV Transmission Circuit #1 b.2. MAYVWTP2 (543096) 69.0 kV to 13&40 2 (541266) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on HIGNSVL2 69.000 (543099) 69 kV Bus a. Apply Fault at the HIGNSVL2 69.000 (543099) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGNSVL2 (543099) 69.0 kV to CTY HIG2 (543098) 69.0 kV Transmission Circuit #1 b.2. HIGNSVL2 (543099) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on AMOCOPL2 69.000 (543100) 69 kV Bus a. Apply Fault at the AMOCOPL2 69.000 (543100) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AMOCOPL2 (543100) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.2. AMOCOPL2 (543100) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on CORDERTP2 69.000 (543657) 69 kV Bus a. Apply Fault at the CORDERTP2 69.000 (543657) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORDERTP2 (543657) 69.0 kV to CTY HIG2 (543098) 69.0 kV Transmission Circuit #1 b.2. CORDERTP2 (543657) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on EXP449T2 69.000 (547438) 69 kV Bus a. Apply Fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXP449T2 (547438) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 b.2. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on PRC460 2 69.000 (547449) 69 kV Bus a. Apply Fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 b.2. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on WEB436 2 69.000 (547527) 69 kV Bus a. Apply Fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEB436 2 (547527) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 b.2. WEB436 2 (547527) 69.0 kV to ORO110 2 (547534) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on COL 94 2 69.000 (547530) 69 kV Bus a. Apply Fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on NIX114 2 69.000 (547535) 69 kV Bus a. Apply Fault at the NIX114 2 69.000 (547535) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NIX114 2 (547535) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 b.2. NIX114 2 (547535) 69.0 kV to BHJ415 2 (547604) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on AUR124 2 69.000 (547537) 69 kV Bus a. Apply Fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 b.2. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on MON152 2 69.000 (547540) 69 kV Bus a. Apply Fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON152 2 (547540) 69.0 kV to AUR124 2 (547537) 69.0 kV Transmission Circuit #1 b.2. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on GAT258 2 69.000 (547551) 69 kV Bus a. Apply Fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GAT258 2 (547551) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 b.2. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on BAX271 2 69.000 (547554) 69 kV Bus a. Apply Fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAX271 2 (547554) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 b.2. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on TIP292 2 69.000 (547559) 69 kV Bus a. Apply Fault at the TIP292 2 69.000 (547559) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 2 (547559) 69.0 kV to NEO332 2 (547571) 69.0 kV Transmission Circuit #1 b.2. TIP292 2 (547559) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on JOP360 2 69.000 (547581) 69 kV Bus a. Apply Fault at the JOP360 2 69.000 (547581) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP360 2 (547581) 69.0 kV to ATL109 2 (547533) 69.0 kV Transmission Circuit #1 b.2. JOP360 2 (547581) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on JOP389 2 69.000 (547592) 69 kV Bus a. Apply Fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 2 (547592) 69.0 kV to EXP449T2 (547438) 69.0 kV Transmission Circuit #1 b.2. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNM393 2 (547595) 69.0 kV to KOD471 2 (547463) 69.0 kV Transmission Circuit #1 b.2. RNM393 2 (547595) 69.0 kV to RNM393 5 (547500) 161.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on COX 269.000 (549910) 69 kV Bus a. Apply Fault at the COX 269.000 (549910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COX 2 (549910) 69.0 kV to PLAINVIEW 2 (549905) 69.0 kV Transmission Circuit #1 b.2. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on DAYTON 269.000 (549913) 69 kV Bus a. Apply Fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAYTON 2 (549913) 69.0 kV to FORT 2 (549914) 69.0 kV Transmission Circuit #1 b.2. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on LAUREL 269.000 (549924) 69 kV Bus a. Apply Fault at the LAUREL 269.000 (549924) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAUREL 2 (549924) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 b.2. LAUREL 2 (549924) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 2 (549925) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 b.2. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on FRISCO 269.000 (549926) 69 kV Bus a. Apply Fault at the FRISCO 269.000 (549926) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRISCO 2 (549926) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 b.2. FRISCO 2 (549926) 69.0 kV to N HWY13 2 (549927) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on GEN-2010-014345.00 (576395) 345 kV Bus a. Apply Fault at the GEN-2010-014345.00 (576395) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2010-014 (576395) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 b.2. GEN-2010-014 (576395) 345.0 kV to G10-014XFMR2 (576398) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on GEN-2017-108161.00 (761271) 161 kV Bus a. Apply Fault at the GEN-2017-108161.00 (761271) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-108 (761271) 161.0 kV to G17-108-XFM1 (761272) 34.5 kV Two Winding #1 b.2. GEN-2017-108 (761271) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on GEN-2017-195345.00 (762279) 345 kV Bus a. Apply Fault at the GEN-2017-195345.00 (762279) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-195 (762279) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-195 (762279) 345.0 kV to G17-195XFM1 (762280) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on GEN-2020-007345.00 (766260) 345 kV Bus a. Apply Fault at the GEN-2020-007345.00 (766260) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-007 (766260) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-007 (766260) 345.0 kV to G20-007-XFM1 (766264) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 7 (531465) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR7 (531512) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEOSHON4 (533022) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDLIAW_CAP5 (541146) 161.0 kV Transmission Circuit #r b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply Fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWAVRLY5 (543063) 161.0 kV to MALTABN5 (543059) 161.0 kV Transmission Circuit #1 b.2. SWAVRLY5 (543063) 161.0 kV to SWAVRLY2 (543094) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.2. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on NEO184 5 161.00 (547471) 161 kV Bus a. Apply Fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO184 5 (547471) 161.0 kV to 2NEOSAC (300748) 69.0 kV Two Winding #1 b.2. NEO184 5 (547471) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAD368 5 (547478) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON383 5 (547480) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 5 (547483) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.2. NICHOLS 5 (549956) 161.0 kV to JUNCTION 5 (549955) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on OAK 2 69.000 (533547) 69 kV Bus a. Apply Fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to CRESWLN2 (533543) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on UDALL 2 69.000 (533559) 69 kV Bus a. Apply Fault at the UDALL 2 69.000 (533559) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UDALL 2 (533559) 69.0 kV to RICHLAN2 (533550) 69.0 kV Transmission Circuit #1 b.2. UDALL 2 (533559) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON383 2 (547591) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 b.2. MON383 2 (547591) 69.0 kV to MON383 5 (547480) 161.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on JOP430 2 69.000 (547608) 69 kV Bus a. Apply Fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP430 2 (547608) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 b.2. JOP430 2 (547608) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on NORTON 5 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTON 5 (543064) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on 5NORTON (300105) 161 kV Bus a. Apply Fault at the 5NORTON (300105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on CORDERTP2 (543657) 69 kV Bus a. Apply Fault at the CORDERTP2 (543657) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORDERTP2 (543657) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on CTY HIG2 (543098) 69 kV Bus a. Apply Fault at the CTY HIG2 (543098) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTY HIG2 (543098) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on HIGNSVL2 (543099) 69 kV Bus a. Apply Fault at the HIGNSVL2 (543099) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGNSVL2 (543099) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on WHGNSVL2 (543102) 69 kV Bus a. Apply Fault at the WHGNSVL2 (543102) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHGNSVL2 (543102) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on MAYVWTP2 (543096) 69 kV Bus a. Apply Fault at the MAYVWTP2 (543096) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAYVWTP2 (543096) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on SALSBRY5 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALSBRY5 (543062) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on 5THMHILB1 (300120) 161 kV Bus a. Apply Fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on 5THMHLB2 (300132) 161 kV Bus a. Apply Fault at the 5THMHLB2 (300132) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB2 (300132) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on 5THMHLB4 (301443) 161 kV Bus a. Apply Fault at the 5THMHLB4 (301443) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on 5MAURER 2 (344558) 161 kV Bus a. Apply Fault at the 5MAURER 2 (344558) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MAURER 2 (344558) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on WINFLD 2 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINFLD 2 (533561) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on TIMBJCT2 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on OAK 2 (533547) 69 kV Bus a. Apply Fault at the OAK 2 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on FINNEY 7 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on HOLCOMB3 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on CIM-PLT3 (539654) 115 kV Bus a. Apply Fault at the CIM-PLT3 (539654) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIM-PLT3 (539654) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on NORTH6T2 (531389) 69 kV Bus a. Apply Fault at the NORTH6T2 (531389) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTH6T2 (531389) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on GRTBEND3 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on CRAIG 5 (542978) 161 kV Bus a. Apply Fault at the CRAIG 5 (542978) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on LENEXA 5 (543038) 161 kV Bus a. Apply Fault at the LENEXA 5 (543038) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LENEXA 5 (543038) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_381 | Single Phase Fault with Stuck Breaker on WGARDNR5 (542966) 161 kV Bus a. Apply Fault at the WGARDNR5 (542966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_382 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_383 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_384 | Single Phase Fault with Stuck Breaker on LNGVW 5 (541224) 161 kV Bus a. Apply Fault at the LNGVW 5 (541224) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 5 (541224) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_385 | Single Phase Fault with Stuck Breaker on KETCHEM7 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_386 | Single Phase Fault with Stuck Breaker on HAWTH 7 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_387 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G18-031 (762672) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_388 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_389 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_390 | Single Phase Fault with Stuck Breaker on HSNVL 2 (541295) 69 kV Bus a. Apply Fault at the HSNVL 2 (541295) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVL 2 (541295) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_391 | Single Phase Fault with Stuck Breaker on ORO110 5 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_392 | Single Phase Fault with Stuck Breaker on JOP389 5 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 5 (547483) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_393 | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_394 | Single Phase Fault with Stuck Breaker on SEDALIA5 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_395 | Single Phase Fault with Stuck Breaker on S.OTTWA5 (543066) 161 kV Bus a. Apply Fault at the S.OTTWA5 (543066) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.OTTWA5 (543066) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_396 | Single Phase Fault with Stuck Breaker on PAOLA 5 (543069) 161 kV Bus a. Apply Fault at the PAOLA 5 (543069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAOLA 5 (543069) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_397 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_398 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_399 | Single Phase Fault with Stuck Breaker on RIV167 2 (547541) 69 kV Bus a. Apply Fault at the RIV167 2 (547541) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_400 | Single Phase Fault with Stuck Breaker on JOP 59 2 (547525) 69 kV Bus a. Apply Fault at the JOP 59 2 (547525) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 59 2 (547525) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_401 | Single Phase Fault with Stuck Breaker on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_402 | Single Phase Fault with Stuck Breaker on SPRGFLD2 (505494) 69 kV Bus a. Apply Fault at the SPRGFLD2 (505494) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD2 (505494) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_403 | Single Phase Fault with Stuck Breaker on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 5 (549969) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_404 | Single Phase Fault with Stuck Breaker on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_405 | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_406 | Single Phase Fault with Stuck Breaker on DAD368 5 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAD368 5 (547478) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_407 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_408 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_409 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_410 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_EDE1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_EDE2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_EDE3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_EDE4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_EDE5 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_EDE6 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy10 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy11 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy12 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy13 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy14 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy15 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy16 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy17 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy18 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy19 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy20 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy21 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy22 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy23 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy24 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy25 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy26 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy27 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy28 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy29 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy30 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy31 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy32 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy33 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy34 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy35 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy36 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy37 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy38 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy39 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy40 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy41 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy42 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy43 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy44 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy45 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy46 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy47 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy48 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy49 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy5 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy50 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy51 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy52 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy53 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy54 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy55 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy56 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy57 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy58 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy59 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy6 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy60 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy7 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy8 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy9 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_GRDA1 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_GRDA2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_INDN1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_INDN2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_INDN3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_OKGE1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_OKGE2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPRM1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPS1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPS2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPS3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPS4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPS5 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPS6 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SUNC1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SUNC2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SWPA1 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SWPA2 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G16-153 (588363) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_001 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_002 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_003 | 3 Phase fault on 5ADAIR1 161.00 (344004) 161 kV Bus a. Apply fault at the 5ADAIR1 161.00 (344004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR1 (344004) 161.0 kV to 2ADAIR 1 (346005) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_004 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_005 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.2. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_006 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_007 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_008 | 3 Phase fault on 5COMPTN 161.00 (300719) 161 kV Bus a. Apply fault at the 5COMPTN 161.00 (300719) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_009 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.3. BUFORD 5 (504440) 161.0 kV to NORFORK5 (505448) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_010 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.2. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_011 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_012 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_013 | 3 Phase fault on 5GRANDVIEW% 161.00 (338099) 161 kV Bus a. Apply fault at the 5GRANDVIEW% 161.00 (338099) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_014 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_015 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of OUTLAW (541546, 541549,541550) units. The issue was also observed in the base case. | Disabling the Drive Train at Outlaw (541546, 541549,541550) resolves the issue. This action is also required in the base case.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_016 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of OUTLAW (541546, 541549,541550) units. The issue was also observed in the base case. | Disabling the Drive Train at Outlaw (541546, 541549,541550) resolves the issue. This action is also required in the base case.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_017 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_018 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_019 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_020 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_021 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_022 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_023 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_024 | 3 Phase fault on CONCRDTP2 69.000 (541523) 69 kV Bus a. Apply fault at the CONCRDTP2 69.000 (541523) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to CONCRDTP2 (541523) 69.0 kV Transmission Circuit #1 b.2. CONCORD2 (541319) 69.0 kV to CONCRDTP2 (541523) 69.0 kV Transmission Circuit #1 b.3. CONCORD2 (541319) 69.0 kV to ENBRIDGE PS2 (541542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_025 | 3 Phase fault on FAYETVLTP2 69.000 (541383) 69 kV Bus a. Apply fault at the FAYETVLTP2 69.000 (541383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to FAYETVLTP2 (541383) 69.0 kV Transmission Circuit #1 b.2. WBURGP 2 (541268) 69.0 kV to FAYETVLTP2 (541383) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on GRDVWTP2 69.000 (541284) 69 kV Bus a. Apply fault at the GRDVWTP2 69.000 (541284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 b.3. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.4. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.5. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.6. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_028 | 3 Phase fault on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 b.3. FREEMAN2 (541291) 69.0 kV to FREEMAN_SP2 (541540) 69.0 kV Transmission Circuit #1 b.4. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.5. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 b.6. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_029 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 b.2. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_030 | 3 Phase fault on HLDENTP2 69.000 (541386) 69 kV Bus a. Apply fault at the HLDENTP2 69.000 (541386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to CNTRVIEW2 (541385) 69.0 kV Transmission Circuit #1 b.2. HOLDEN 2 (541278) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.3. RGREEN 2 (541279) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 b.4. CNTRVIEW2 (541385) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.5. HLDENTP2 (541386) 69.0 kV to KNGSVIL 2 (541387) 69.0 kV Transmission Circuit #1 b.6. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_031 | 3 Phase fault on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.3. POSTOAK2 (541300) 69.0 kV to POSTOAK1 (541373) 34.5 kV to POSTOAK_TER1 (541374) 2.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_032 | 3 Phase fault on CLNTPLT_CAP269.000 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP269.000 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_033 | 3 Phase fault on LEXNTON2 69.000 (541265) 69 kV Bus a. Apply fault at the LEXNTON2 69.000 (541265) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNTON2 (541265) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_034 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_035 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_036 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_037 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_038 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_039 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_040 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_041 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_042 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_043 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_044 | 3 Phase fault on NAVY 5 161.00 (542989) 161 kV Bus a. Apply fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_045 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_046 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_047 | 3 Phase fault on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_048 | 3 Phase fault on NORTON 5 161.00 (543064) 161 kV Bus a. Apply fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 b.2. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. NORTON 5 (543064) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_049 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_050 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_051 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. MERRIAM_CAP5 (542947) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_052 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_053 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_054 | 3 Phase fault on SWAVCAP2 69.000 (543012) 69 kV Bus a. Apply fault at the SWAVCAP2 69.000 (543012) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.2. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.3. SWAVCAP2 (543012) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_055 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_056 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_057 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_058 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_059 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_060 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_061 | 3 Phase fault on CORDER 2 69.000 (543097) 69 kV Bus a. Apply fault at the CORDER 2 69.000 (543097) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.2. CORDER 2 (543097) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.3. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.4. DOVER2 (543101) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.5. CORDERTP2 (543657) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.6. CORDER 2 (543097) 69.0 kV to CORDER1 (543150) 12.5 kV to CORDER_TER1 (543151) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_062 | 3 Phase fault on WHGNSVL2 69.000 (543102) 69 kV Bus a. Apply fault at the WHGNSVL2 69.000 (543102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNTON2 (541265) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.2. 13&40 2 (541266) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.3. MAYVWTP2 (543096) 69.0 kV to AMOCOPL2 (543100) 69.0 kV Transmission Circuit #1 b.4. CTY HIG2 (543098) 69.0 kV to HIGNSVL2 (543099) 69.0 kV Transmission Circuit #1 b.5. HIGNSVL2 (543099) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 b.6. AMOCOPL2 (543100) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 b.7. HIGNSVL2 (543099) 69.0 kV to HGNSVL1 (543152) 12.5 kV to HGNSVL_TER1 (543153) 2.4 kV Three Winding #1 b.8. WHGNSVL2 (543102) 69.0 kV to WHGNSVL1 (543154) 12.5 kV to WHGNSVL_TER1 (543155) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_063 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_064 | 3 Phase fault on KCSOUTH5 161.00 (541245) 161 kV Bus a. Apply fault at the KCSOUTH5 161.00 (541245) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCSOUTH5 (541245) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_065 | 3 Phase fault on OSAWTM_CAP5 161.00 (543135) 161 kV Bus a. Apply fault at the OSAWTM_CAP5 161.00 (543135) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWTM_CAP5 (543135) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_066 | 3 Phase fault on SWAVCAP5 161.00 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 161.00 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_067 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_068 | 3 Phase fault on COLLEG 2 69.000 (530574) 69 kV Bus a. Apply fault at the COLLEG 2 69.000 (530574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 b.2. COLLEG 2 (530574) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_069 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_070 | 3 Phase fault on BKHLTAP2 69.000 (530589) 69 kV Bus a. Apply fault at the BKHLTAP2 69.000 (530589) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.2. SUSANK 2 (530571) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.3. BNK HL 2 (530572) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.4. HITHMN 2 (530573) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_071 | 3 Phase fault on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_072 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_073 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_074 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_075 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_076 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_077 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_078 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_079 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_080 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_081 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_082 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of HOLCGEN (531447), BUFF_DUNES (523061, 523062) and G20-008 (764981) units. | 1- Operational steady state fixes (existing caps/taps/gen set points) 2- Change acceleration factor to 0.7
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_083 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_084 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of HOLCGEN (531447),Tolk (525562), HARRNGTON3 (523973) and G20-008 (764981, 764984) units and observed voltage issues at BUFF_DUNES (523118), LAMAR7 (599950) and FINNEY 7 (523853). | 1- Operational steady state fixes (existing caps/taps/gen set points) 2- Change acceleration factor to 0.7
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_085 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_086 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G08-124 (579483, 579486) units. | 1- Operational steady state fixes (existing caps/taps/gen set points) 2- Change acceleration factor to 0.7
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_087 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_088 | 3 Phase fault on SETAB 3 115.00 (531464) 115 kV Bus a. Apply fault at the SETAB 3 115.00 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_089 | 3 Phase fault on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_090 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_091 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_092 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_093 | 3 Phase fault on GRANTTP3 115.00 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 115.00 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_094 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_095 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_096 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_097 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_098 | 3 Phase fault on SAT-TAP3 115.00 (531442) 115 kV Bus a. Apply fault at the SAT-TAP3 115.00 (531442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASKELL3 (531374) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.2. HASKELL3 (531374) 115.0 kV to SEWARD-3 (531467) 115.0 kV Transmission Circuit #1 b.3. PIONTAP3 (531392) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.4. SAT-TAP3 (531442) 115.0 kV to SATMKEC3 (539691) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_099 | 3 Phase fault on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_100 | 3 Phase fault on WILLIAM3 115.00 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 115.00 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_101 | 3 Phase fault on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.3. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_102 | 3 Phase fault on GANO 3 115.00 (531493) 115 kV Bus a. Apply fault at the GANO 3 115.00 (531493) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.3. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_103 | 3 Phase fault on KSAVWTP3 115.00 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 115.00 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_104 | 3 Phase fault on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_105 | 3 Phase fault on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.2. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.3. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_106 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_107 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_108 | 3 Phase fault on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_109 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_110 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_111 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_112 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_113 | 3 Phase fault on WALDO 3 115.00 (539698) 115 kV Bus a. Apply fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_114 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_115 | 3 Phase fault on PHLBURG3 115.00 (539685) 115 kV Bus a. Apply fault at the PHLBURG3 115.00 (539685) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_116 | 3 Phase fault on GLENELD3 115.00 (539663) 115 kV Bus a. Apply fault at the GLENELD3 115.00 (539663) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.2. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_117 | 3 Phase fault on JEWELL 3 115.00 (539669) 115 kV Bus a. Apply fault at the JEWELL 3 115.00 (539669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.2. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.4. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_118 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_119 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_120 | 3 Phase fault on 5LOGAN 161.00 (301161) 161 kV Bus a. Apply fault at the 5LOGAN 161.00 (301161) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MANSFDMN (300095) 161.0 kV to 5LOGAN (301161) 161.0 kV Transmission Circuit #1 b.2. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_121 | 3 Phase fault on WAVERLY3 115.00 (533278) 115 kV Bus a. Apply fault at the WAVERLY3 115.00 (533278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.2. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_122 | 3 Phase fault on MNTCLLO3 115.00 (533281) 115 kV Bus a. Apply fault at the MNTCLLO3 115.00 (533281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_123 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_124 | 3 Phase fault on MUND 3 115.00 (533282) 115 kV Bus a. Apply fault at the MUND 3 115.00 (533282) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_125 | 3 Phase fault on 166TH 3 115.00 (533233) 115 kV Bus a. Apply fault at the 166TH 3 115.00 (533233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.3. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_126 | 3 Phase fault on MIDLADN3 115.00 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 115.00 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_127 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_128 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_129 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-086 (589243) and G16-153 (588363) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_130 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) and G18-057 (762925) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_131 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) and G16-153 (588363) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_132 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_133 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_134 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | 1- Protection disabled without any impact on stability. 2- Change acceleration factor to 0.7
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_135 | 3 Phase fault on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_136 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_137 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_138 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_139 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_140 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_141 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_142 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_143 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_144 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_145 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_146 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G16-153 (588363), G17-086 (589243) and G17-221 (760307) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_147 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G16-153 (588363), G17-086 (589243) and G17-221 (760307) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_148 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_149 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G16-153 (588363) and G17-086 (589243) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_150 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G16-153 (588363) and G17-086 (589243) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_151 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G16-153 (588363) and G17-086 (589243) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_152 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_153 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_154 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_155 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_156 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_157 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_158 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_159 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_160 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_161 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_162 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_163 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS (532751), LEC U5 (532663) IAT G2 (542962) and COOPER (640009) units. | Reduce clearing time to 3.75 cycles. TO submitted fault sheet states the clearing time to be 3.75 cycles.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_164 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G17-227 (760664), G17-221 (760307), G17-086 (589243) and G16-153 (588363) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_165 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_166 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_167 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_168 | 3 Phase fault on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.3. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_169 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_170 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 b.2. SC3MILL2 (533552) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 b.3. SC3MILL2 (533552) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 b.4. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_171 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC7CRES2 (533555) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_172 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_173 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_174 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_175 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_176 | 3 Phase fault on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_177 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_178 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_179 | 3 Phase fault on STROTHR2 69.000 (533556) 69 kV Bus a. Apply fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_180 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_181 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_182 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_183 | 3 Phase fault on EDWARVL3 115.00 (533238) 115 kV Bus a. Apply fault at the EDWARVL3 115.00 (533238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_184 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_185 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_186 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_187 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_188 | 3 Phase fault on UDALL 2 69.000 (533559) 69 kV Bus a. Apply fault at the UDALL 2 69.000 (533559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UDALL 2 (533559) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_189 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_190 | 3 Phase fault on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_191 | 3 Phase fault on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_192 | 3 Phase fault on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.4. NICHOL XF1 1 (549940) 13.2 kV to NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_193 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.3. MILL XF1 1 (549946) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_194 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 b.3. MILL XF2 1 (549948) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_195 | 3 Phase fault on HAWTHRN4 138.00 (510413) 138 kV Bus a. Apply fault at the HAWTHRN4 138.00 (510413) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 (510396) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.2. CHELSA4 (510410) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.3. CHELSA4 (510410) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 b.4. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_196 | 3 Phase fault on GROVE 5 161.00 (510411) 161 kV Bus a. Apply fault at the GROVE 5 161.00 (510411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 5 (510411) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_197 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_198 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_199 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_200 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_201 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_202 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_203 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_204 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_205 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_206 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 (510418) 69.0 kV to VINTAJC4 (510417) 138.0 kV to VINJT1-1 (510367) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_207 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_208 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_209 | 3 Phase fault on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_210 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_211 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_212 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_213 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_214 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_215 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_216 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_217 | 3 Phase fault on LOCSTGVKM 5 161.00 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 161.00 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_218 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_219 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_220 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_221 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_222 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_223 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_224 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_225 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_226 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_227 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_228 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_229 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_230 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_231 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_232 | 3 Phase fault on TONECE7 345.00 (512750) 345 kV Bus a. Apply fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_233 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_234 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.3. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_235 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.3. OCHILTREE 3 (523154) 115.0 kV to OCHILTREE 6 (523155) 230.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_236 | 3 Phase fault on TEXAS_CNTY 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_237 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_238 | 3 Phase fault on TEXAS_CNTY 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_239 | 3 Phase fault on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_240 | 3 Phase fault on COLE 3115.00 (523120) 115 kV Bus a. Apply fault at the COLE 3115.00 (523120) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 3 (523120) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_241 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. TXFARMS 3 (523140) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 b.3. SPEARMAN 3 (523186) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_242 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_243 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_244 | 3 Phase fault on WADE_TP 3115.00 (523145) 115 kV Bus a. Apply fault at the WADE_TP 3115.00 (523145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIPSCOMB 3 (523135) 115.0 kV to WADE_TP 3 (523145) 115.0 kV Transmission Circuit #1 b.2. WADE_TP 3 (523145) 115.0 kV to WADE 3 (523147) 115.0 kV Transmission Circuit #1 b.3. WADE_TP 3 (523145) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_245 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.5. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.7. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.8. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.9. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.10. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.11. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_246 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_247 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_248 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_249 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_250 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_251 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_252 | 3 Phase fault on BOL431 5 161.00 (547493) 161 kV Bus a. Apply fault at the BOL431 5 161.00 (547493) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_253 | 3 Phase fault on JOP391 5 161.00 (547593) 161 kV Bus a. Apply fault at the JOP391 5 161.00 (547593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.2. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_254 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. HOC404A1 (547715) 12.5 kV to HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_255 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_256 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_257 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_258 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_259 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_260 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_261 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MPLTAP (300036) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 b.3. 5MPLTAP (300036) 161.0 kV to 5LATHROP (344923) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_262 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_263 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_264 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.3. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.4. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_265 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_266 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_267 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_268 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_269 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_270 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_271 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_272 | 3 Phase fault on 5HIGBEEB1 161.00 (300066) 161 kV Bus a. Apply fault at the 5HIGBEEB1 161.00 (300066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HIGBEEB1 (300066) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_273 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_274 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_275 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_276 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_277 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_278 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_279 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_280 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_281 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_282 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5BTLFD (300348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_283 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_284 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5RIVRDL (300726) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_285 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_286 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_287 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_288 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to 5MORGANXF2 (301622) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_289 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_290 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_291 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_292 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_293 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_294 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_295 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOL (301040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_296 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_297 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_298 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_299 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_300 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_301 | 3 Phase fault on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STKAEC (300118) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_302 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5THMHLB2 (300132) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_303 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5THMHILTFERB (301511) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_304 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HOLDENB2 (300124) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_305 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB3 (300133) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_306 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5BEVIER (300381) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_307 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_308 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THOMHLXF1 (301508) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_309 | 3 Phase fault on 5THMHLB3 161.00 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 161.00 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5MEADVLB1 (300207) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_310 | 3 Phase fault on 5THMHLB3 161.00 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 161.00 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5THOMHLXF3 (301506) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_311 | 3 Phase fault on 5THMHLB3 161.00 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 161.00 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5THOMHLU3SU (301507) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_312 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2MOCITY (300304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_313 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_314 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_315 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_316 | 3 Phase fault on 2ELM 69.000 (300327) 69 kV Bus a. Apply fault at the 2ELM 69.000 (300327) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELM (300327) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_317 | 3 Phase fault on 5BTLFD 161.00 (300348) 161 kV Bus a. Apply fault at the 5BTLFD 161.00 (300348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_318 | 3 Phase fault on 2BEAMAN 69.000 (300527) 69 kV Bus a. Apply fault at the 2BEAMAN 69.000 (300527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEAMAN (300527) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_319 | 3 Phase fault on 2DRESDN 69.000 (300528) 69 kV Bus a. Apply fault at the 2DRESDN 69.000 (300528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DRESDN (300528) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_320 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_321 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_322 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_323 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_324 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_325 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_326 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_327 | 3 Phase fault on 2MALTAJ 69.000 (300536) 69 kV Bus a. Apply fault at the 2MALTAJ 69.000 (300536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAJ (300536) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_328 | 3 Phase fault on 2NAPTON 69.000 (300538) 69 kV Bus a. Apply fault at the 2NAPTON 69.000 (300538) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NAPTON (300538) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_329 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Instantaneous frequency relay trips GI91 (99915) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_330 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_331 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2FLORNC (300553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_332 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_333 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2MEDOC (300653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_334 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_335 | 3 Phase fault on 2ASHGRV 69.000 (300657) 69 kV Bus a. Apply fault at the 2ASHGRV 69.000 (300657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_336 | 3 Phase fault on 2BOWRML 69.000 (300659) 69 kV Bus a. Apply fault at the 2BOWRML 69.000 (300659) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOWRML (300659) 69.0 kV to 2REEDS (300751) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_337 | 3 Phase fault on 2CRANE 69.000 (300667) 69 kV Bus a. Apply fault at the 2CRANE 69.000 (300667) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CRANE (300667) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_338 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_339 | 3 Phase fault on 2ELWOOD 69.000 (300669) 69 kV Bus a. Apply fault at the 2ELWOOD 69.000 (300669) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_340 | 3 Phase fault on 5NIXA-1 161.00 (300678) 161 kV Bus a. Apply fault at the 5NIXA-1 161.00 (300678) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_341 | 3 Phase fault on 2PRDYTP 69.000 (300679) 69 kV Bus a. Apply fault at the 2PRDYTP 69.000 (300679) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PRDYTP (300679) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_342 | 3 Phase fault on 2VERONA 69.000 (300680) 69 kV Bus a. Apply fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_343 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_344 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_345 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_346 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_347 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_348 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_349 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_350 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_351 | 3 Phase fault on 2DMNDGR 69.000 (300744) 69 kV Bus a. Apply fault at the 2DMNDGR 69.000 (300744) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDGR (300744) 69.0 kV to 2DMNDTP (300745) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_352 | 3 Phase fault on 2DMNDTP 69.000 (300745) 69 kV Bus a. Apply fault at the 2DMNDTP 69.000 (300745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDTP (300745) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_353 | 3 Phase fault on 2DMNDTP 69.000 (300745) 69 kV Bus a. Apply fault at the 2DMNDTP 69.000 (300745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_354 | 3 Phase fault on 2NEOSAC 69.000 (300748) 69 kV Bus a. Apply fault at the 2NEOSAC 69.000 (300748) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to 2NEOSHO (300750) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_355 | 3 Phase fault on 2NEOSAC 69.000 (300748) 69 kV Bus a. Apply fault at the 2NEOSAC 69.000 (300748) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to 2SWTWT (300758) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_356 | 3 Phase fault on 2REEDS 69.000 (300751) 69 kV Bus a. Apply fault at the 2REEDS 69.000 (300751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_357 | 3 Phase fault on 2ELKTON 69.000 (300773) 69 kV Bus a. Apply fault at the 2ELKTON 69.000 (300773) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELKTON (300773) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_358 | 3 Phase fault on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2EUDORA (300774) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_359 | 3 Phase fault on 2FRSTOE 69.000 (300776) 69 kV Bus a. Apply fault at the 2FRSTOE 69.000 (300776) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FRSTOE (300776) 69.0 kV to 2WARSAW (300790) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_360 | 3 Phase fault on 2KNOBBY 69.000 (300780) 69 kV Bus a. Apply fault at the 2KNOBBY 69.000 (300780) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KNOBBY (300780) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_361 | 3 Phase fault on 2WARSAW 69.000 (300790) 69 kV Bus a. Apply fault at the 2WARSAW 69.000 (300790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WARSAW (300790) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_362 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_363 | 3 Phase fault on 2DAMSCUS 69.000 (300804) 69 kV Bus a. Apply fault at the 2DAMSCUS 69.000 (300804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DAMSCUS (300804) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_364 | 3 Phase fault on 2ICONTP 69.000 (300809) 69 kV Bus a. Apply fault at the 2ICONTP 69.000 (300809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ICONTP (300809) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_365 | 3 Phase fault on 2OSCEOL 69.000 (300811) 69 kV Bus a. Apply fault at the 2OSCEOL 69.000 (300811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_366 | 3 Phase fault on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_367 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_368 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_369 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_370 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_371 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_372 | 3 Phase fault on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOKC (301522) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_373 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_374 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_375 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_376 | 3 Phase fault on BEAVER 5 161.00 (505480) 161 kV Bus a. Apply fault at the BEAVER 5 161.00 (505480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_377 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_378 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_379 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_380 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_381 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_382 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_383 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_384 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_385 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_386 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_387 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_388 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_389 | 3 Phase fault on NIXA 2 69.000 (505501) 69 kV Bus a. Apply fault at the NIXA 2 69.000 (505501) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_390 | 3 Phase fault on NIXA DT2 69.000 (505541) 69 kV Bus a. Apply fault at the NIXA DT2 69.000 (505541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA DT2 (505541) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_391 | 3 Phase fault on NIXA NE2 69.000 (505544) 69 kV Bus a. Apply fault at the NIXA NE2 69.000 (505544) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA NE2 (505544) 69.0 kV to JRPS 69B-2 2 (549903) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_392 | 3 Phase fault on DELWARE4 138.00 (510379) 138 kV Bus a. Apply fault at the DELWARE4 138.00 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_393 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_394 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_395 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_396 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_397 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_398 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_399 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_400 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_401 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_402 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_403 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_404 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_405 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_406 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_407 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_408 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_409 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_410 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_411 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_412 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_413 | 3 Phase fault on MOSCOW 2 69.000 (531384) 69 kV Bus a. Apply fault at the MOSCOW 2 69.000 (531384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOW 2 (531384) 69.0 kV to MOSCOWT2 (531385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_414 | 3 Phase fault on MOSCOWT2 69.000 (531385) 69 kV Bus a. Apply fault at the MOSCOWT2 69.000 (531385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOWT2 (531385) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_415 | 3 Phase fault on NORTH6 2 69.000 (531388) 69 kV Bus a. Apply fault at the NORTH6 2 69.000 (531388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6 2 (531388) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_416 | 3 Phase fault on NORTH6T2 69.000 (531389) 69 kV Bus a. Apply fault at the NORTH6T2 69.000 (531389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6T2 (531389) 69.0 kV to WALKMYR2 (531404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_417 | 3 Phase fault on ROLLA 2 115.00 (531395) 115 kV Bus a. Apply fault at the ROLLA 2 115.00 (531395) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLA 2 (531395) 115.0 kV to ABBK 2 (531494) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_418 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WOODS 2 (531406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_419 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G08-124 (579483, 579486) units. The issue was also observed in the base case. | Reduce clearing time to 5 cycles. The same clearing time is required in the base case.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_420 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_421 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_422 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G17-227 (760664), G17-221 (760307), G17-086 (589243) and G16-153 (588363) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_423 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G17-227 (760664), G17-221 (760307), G17-086 (589243) and G16-153 (588363) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_424 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_425 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_426 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_427 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_428 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_429 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_430 | 3 Phase fault on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_431 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_432 | 3 Phase fault on EUDORA 3 115.00 (533240) 115 kV Bus a. Apply fault at the EUDORA 3 115.00 (533240) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_433 | 3 Phase fault on ARKCTYW2 69.000 (533540) 69 kV Bus a. Apply fault at the ARKCTYW2 69.000 (533540) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to ARKCTYE2 (533542) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_434 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_435 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_436 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_437 | 3 Phase fault on FLORAL 2 69.000 (533545) 69 kV Bus a. Apply fault at the FLORAL 2 69.000 (533545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORAL 2 (533545) 69.0 kV to FLORALJ2 (533546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_438 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_439 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to TIMBER 2 (533557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_440 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_441 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_442 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_443 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_444 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_445 | 3 Phase fault on PRAIRIE2 69.000 (533562) 69 kV Bus a. Apply fault at the PRAIRIE2 69.000 (533562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAIRIE2 (533562) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_446 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to BURLIND2 (533625) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_447 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to CC1BURL2 (533628) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_448 | 3 Phase fault on NEOSHON2 69.000 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 69.000 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_449 | 3 Phase fault on EAST SUB 2 69.000 (533990) 69 kV Bus a. Apply fault at the EAST SUB 2 69.000 (533990) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_450 | 3 Phase fault on WEST SUB 2 69.000 (533991) 69 kV Bus a. Apply fault at the WEST SUB 2 69.000 (533991) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_451 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and frequency relays trip G18-116 (763335) and instantaneous frequency relay trips G19-051 (763826). | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_452 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_453 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_454 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_455 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_456 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G08-124 (579483, 579486) units. | 1- Operational steady state fixes (existing caps/taps/gen set points) 2- Change acceleration rate to 0.7
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_457 | 3 Phase fault on CLNTPLT_CAP269.000 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP269.000 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_458 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_459 | 3 Phase fault on WSTELEC_CAP5161.00 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5161.00 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_460 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of OUTLAW (541546, 541549,541550) units. The issue was also observed in the base case. | Disabling the Drive Train at Outlaw (541546, 541549,541550) resolves the issue. This action is also required in the base case.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_461 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of OUTLAW (541546, 541549,541550) units. The issue was also observed in the base case. | Disabling the Drive Train at Outlaw (541546, 541549,541550) resolves the issue. This action is also required in the base case.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_462 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of OUTLAW (541546, 541549,541550) units. The issue was also observed in the base case. | Disabling the Drive Train at Outlaw (541546, 541549,541550) resolves the issue. This action is also required in the base case.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_463 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_464 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_465 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_466 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_467 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_468 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_469 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_470 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_471 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_472 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_473 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_474 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_475 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_476 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_477 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_478 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to GRDVWE 5 (541223) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_479 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_480 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_481 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_482 | 3 Phase fault on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_483 | 3 Phase fault on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_484 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_485 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_486 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_487 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_488 | 3 Phase fault on NRAYMORETP 5161.00 (541231) 161 kV Bus a. Apply fault at the NRAYMORETP 5161.00 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORETP 5 (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_489 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_490 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_491 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_492 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_493 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_494 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_495 | 3 Phase fault on LEX69 2 69.000 (541264) 69 kV Bus a. Apply fault at the LEX69 2 69.000 (541264) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX69 2 (541264) 69.0 kV to LEXNTON2 (541265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_496 | 3 Phase fault on 13&40 2 69.000 (541266) 69 kV Bus a. Apply fault at the 13&40 2 69.000 (541266) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to ODESSA 2 (541267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_497 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to KELHYS 2 (541273) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_498 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_499 | 3 Phase fault on SEDS 2 69.000 (541272) 69 kV Bus a. Apply fault at the SEDS 2 69.000 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_500 | 3 Phase fault on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_501 | 3 Phase fault on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_502 | 3 Phase fault on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_503 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_504 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_505 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_506 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to HSNVLN 2 (541297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_507 | 3 Phase fault on LNGVW 2 69.000 (541282) 69 kV Bus a. Apply fault at the LNGVW 2 69.000 (541282) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to BRMALL 2 (541283) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_508 | 3 Phase fault on HSNVL 2 69.000 (541295) 69 kV Bus a. Apply fault at the HSNVL 2 69.000 (541295) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVLSW2 (541296) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_509 | 3 Phase fault on HSNVLSW2 69.000 (541296) 69 kV Bus a. Apply fault at the HSNVLSW2 69.000 (541296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLSW2 (541296) 69.0 kV to HSNVLN 2 (541297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_510 | 3 Phase fault on HSNVLSW2 69.000 (541296) 69 kV Bus a. Apply fault at the HSNVLSW2 69.000 (541296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLSW2 (541296) 69.0 kV to GRDNCTY2 (541298) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_511 | 3 Phase fault on GRDNCTY2 69.000 (541298) 69 kV Bus a. Apply fault at the GRDNCTY2 69.000 (541298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY2 (541298) 69.0 kV to GUNNPS2 (541299) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_512 | 3 Phase fault on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_513 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBW5 (541336) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_514 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_515 | 3 Phase fault on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161.0 kV to WAFBE5 (541338) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_516 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_517 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_518 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_519 | 3 Phase fault on PECULR 5 161.00 (541342) 161 kV Bus a. Apply fault at the PECULR 5 161.00 (541342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECULR 5 (541342) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_520 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_521 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-058 (764382, 764376, 764379). After disabling instantaneous voltage relay, instantaneous frequency relay trips G20-058-GEN1 (764382) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_522 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Instantaneous frequency relay trips G20-058 (764376) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_523 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_524 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_525 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-196 (762303) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_526 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-196 (762303) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_527 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_528 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_529 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-073 (764394, 764391) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_530 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_531 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_532 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_533 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_534 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_535 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_536 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_537 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_538 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_539 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_540 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_541 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_542 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_543 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_544 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_545 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_546 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_547 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_548 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_549 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_550 | 3 Phase fault on PFLUMM 5 161.00 (542979) 161 kV Bus a. Apply fault at the PFLUMM 5 161.00 (542979) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_551 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_552 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_553 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-007 units (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283) and G20-079 (764311) units. After disabling voltage relay, instantaneous frequency relays trips G20-007 units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_554 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-007 units (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283) and G20-079 (764311) units. After disabling voltage relay, instantaneous frequency relays trips G20-007 units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_555 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | No | No | Voltage relay trips G20-007 units (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283) and G20-079 (764311) units. After disabling voltage relay, instantaneous frequency relays trips G20-007 units. Disabling the relay demonstrates that there are slow dampening oscillations in the angle of WCGS U1. | Protection disabled at G20-007 and G20-079 units and reduce clearing time to 4.75 cycles. TO submitted fault sheet states the clearing time to be 4.75 cycles.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_556 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_557 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_558 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_559 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_560 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_561 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_562 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_563 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_564 | 3 Phase fault on SWAVCAP5 161.00 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 161.00 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_565 | 3 Phase fault on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_566 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_567 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_568 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_569 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_570 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_571 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_572 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_573 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_574 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_575 | 3 Phase fault on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LENEXA 5 (543038) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_576 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_577 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-073 (764394, 764391) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_578 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to NEASTOTTW5 (543166) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_579 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-073 (764394, 764391) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_580 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_581 | 3 Phase fault on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_582 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_583 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_584 | 3 Phase fault on S.OTTWA5 161.00 (543066) 161 kV Bus a. Apply fault at the S.OTTWA5 161.00 (543066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.OTTWA5 (543066) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-073 (764394, 764391) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_585 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_586 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_587 | 3 Phase fault on S EAST 5 161.00 (543071) 161 kV Bus a. Apply fault at the S EAST 5 161.00 (543071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S EAST 5 (543071) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_588 | 3 Phase fault on MRSHLJT5 161.00 (543072) 161 kV Bus a. Apply fault at the MRSHLJT5 161.00 (543072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRSHLJT5 (543072) 161.0 kV to MIAMI_ 5 (543073) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_589 | 3 Phase fault on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSTVAL5 (543077) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-073 (764394, 764391) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_590 | 3 Phase fault on OSAWAT 5 161.00 (543112) 161 kV Bus a. Apply fault at the OSAWAT 5 161.00 (543112) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWAT 5 (543112) 161.0 kV to OSAWTM_CAP5 (543135) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_591 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON416J2 (547402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_592 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_593 | 3 Phase fault on MON376 2 69.000 (547401) 69 kV Bus a. Apply fault at the MON376 2 69.000 (547401) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376 2 (547401) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_594 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON352 2 (547406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_595 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_596 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_597 | 3 Phase fault on MON311J2 69.000 (547407) 69 kV Bus a. Apply fault at the MON311J2 69.000 (547407) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON311J2 (547407) 69.0 kV to MON311 2 (547408) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_598 | 3 Phase fault on SCAM66 2 69.000 (547409) 69 kV Bus a. Apply fault at the SCAM66 2 69.000 (547409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCAM66 2 (547409) 69.0 kV to SCM66T 2 (547455) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_599 | 3 Phase fault on COL282 2 69.000 (547411) 69 kV Bus a. Apply fault at the COL282 2 69.000 (547411) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL282 2 (547411) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_600 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_601 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_602 | 3 Phase fault on WEB105 2 69.000 (547431) 69 kV Bus a. Apply fault at the WEB105 2 69.000 (547431) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB105 2 (547431) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_603 | 3 Phase fault on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUPTAP 2 (547436) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_604 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to EXP4492 (547439) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_605 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_606 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_607 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_608 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_609 | 3 Phase fault on JAS344T2 69.000 (547450) 69 kV Bus a. Apply fault at the JAS344T2 69.000 (547450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAS344T2 (547450) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_610 | 3 Phase fault on SCM66T 2 69.000 (547455) 69 kV Bus a. Apply fault at the SCM66T 2 69.000 (547455) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCM66T 2 (547455) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_611 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_612 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_613 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_614 | 3 Phase fault on KOD471 2 69.000 (547463) 69 kV Bus a. Apply fault at the KOD471 2 69.000 (547463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOD471 2 (547463) 69.0 kV to DIA131 2 (547538) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_615 | 3 Phase fault on KOD471 2 69.000 (547463) 69 kV Bus a. Apply fault at the KOD471 2 69.000 (547463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOD471 2 (547463) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_616 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_617 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_618 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_619 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_620 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_621 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_622 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_623 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_624 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_625 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_626 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_627 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_628 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_629 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_630 | 3 Phase fault on ASB349 5 161.00 (547476) 161 kV Bus a. Apply fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. After disabling Voltage relay, instantaneous frequency relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_631 | 3 Phase fault on ASB349 5 161.00 (547476) 161 kV Bus a. Apply fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. After disabling Voltage relay, instantaneous frequency relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_632 | 3 Phase fault on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_633 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_634 | 3 Phase fault on LAR382 5 161.00 (547479) 161 kV Bus a. Apply fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-060 (588984, 589203) units. After disabling Voltage relay, instantaneous frequency relay trips G17-060 (588984, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_635 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_636 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_637 | 3 Phase fault on DEC392 5 161.00 (547484) 161 kV Bus a. Apply fault at the DEC392 5 161.00 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 (547484) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_638 | 3 Phase fault on CAR395 5 161.00 (547485) 161 kV Bus a. Apply fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_639 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_640 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_641 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_642 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_643 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_644 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_645 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_646 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_647 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to ORO110 2 (547534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_648 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_649 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_650 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_651 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_652 | 3 Phase fault on CAR108 2 69.000 (547532) 69 kV Bus a. Apply fault at the CAR108 2 69.000 (547532) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAR108 2 (547532) 69.0 kV to ATL109 2 (547533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_653 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_654 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to JOP360 2 (547581) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_655 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_656 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_657 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_658 | 3 Phase fault on NIX114 2 69.000 (547535) 69 kV Bus a. Apply fault at the NIX114 2 69.000 (547535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIX114 2 (547535) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_659 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_660 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MON152 2 (547540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_661 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_662 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_663 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_664 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_665 | 3 Phase fault on MON152 2 69.000 (547540) 69 kV Bus a. Apply fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_666 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_667 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_668 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to REP345 2 (547576) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_669 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_670 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_671 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to ROC296 2 (547560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_672 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to LIN314 2 (547563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_673 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to AND322 2 (547566) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_674 | 3 Phase fault on FRP217 2 69.000 (547545) 69 kV Bus a. Apply fault at the FRP217 2 69.000 (547545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRP217 2 (547545) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_675 | 3 Phase fault on GAT258 2 69.000 (547551) 69 kV Bus a. Apply fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_676 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_677 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_678 | 3 Phase fault on GAL278 2 69.000 (547555) 69 kV Bus a. Apply fault at the GAL278 2 69.000 (547555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAL278 2 (547555) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_679 | 3 Phase fault on TIP292 2 69.000 (547559) 69 kV Bus a. Apply fault at the TIP292 2 69.000 (547559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 2 (547559) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_680 | 3 Phase fault on COM381T2 69.000 (547579) 69 kV Bus a. Apply fault at the COM381T2 69.000 (547579) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COM381T2 (547579) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_681 | 3 Phase fault on JOP360 2 69.000 (547581) 69 kV Bus a. Apply fault at the JOP360 2 69.000 (547581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP360 2 (547581) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_682 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_683 | 3 Phase fault on JOP389 2 69.000 (547592) 69 kV Bus a. Apply fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_684 | 3 Phase fault on RNM393 2 69.000 (547595) 69 kV Bus a. Apply fault at the RNM393 2 69.000 (547595) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 2 (547595) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_685 | 3 Phase fault on GLF339 2 69.000 (547690) 69 kV Bus a. Apply fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_686 | 3 Phase fault on JRPS 69B-2 269.000 (549903) 69 kV Bus a. Apply fault at the JRPS 69B-2 269.000 (549903) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JRPS 69B-2 2 (549903) 69.0 kV to PLAINVIEW 2 (549905) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_687 | 3 Phase fault on JRPS 69B-2 269.000 (549903) 69 kV Bus a. Apply fault at the JRPS 69B-2 269.000 (549903) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JRPS 69B-2 2 (549903) 69.0 kV to TWIN OAKS 2 (549933) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_688 | 3 Phase fault on JRPS 69B-2 269.000 (549903) 69 kV Bus a. Apply fault at the JRPS 69B-2 269.000 (549903) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JRPS 69B-2 2 (549903) 69.0 kV to SEMINOLE 2 (549934) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_689 | 3 Phase fault on JAMES RIVER269.000 (549904) 69 kV Bus a. Apply fault at the JAMES RIVER269.000 (549904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER2 (549904) 69.0 kV to S HWY 65 2 (549908) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_690 | 3 Phase fault on JAMES RIVER269.000 (549904) 69 kV Bus a. Apply fault at the JAMES RIVER269.000 (549904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER2 (549904) 69.0 kV to HIGHWAY M 2 (549909) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_691 | 3 Phase fault on KICKAPOO 269.000 (549906) 69 kV Bus a. Apply fault at the KICKAPOO 269.000 (549906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KICKAPOO 2 (549906) 69.0 kV to SUNSET 2 (549907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_692 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to S HWY 65 2 (549908) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_693 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to FORT 2 (549914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_694 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to MONROE 2 (549923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_695 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to SEMINOLE 2 (549934) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_696 | 3 Phase fault on COX 269.000 (549910) 69 kV Bus a. Apply fault at the COX 269.000 (549910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_697 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to LAUREL 2 (549924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_698 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_699 | 3 Phase fault on DAYTON 269.000 (549913) 69 kV Bus a. Apply fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_700 | 3 Phase fault on MILL 269.000 (549918) 69 kV Bus a. Apply fault at the MILL 269.000 (549918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 2 (549918) 69.0 kV to CHAD 2 (549919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_701 | 3 Phase fault on CHAD 269.000 (549919) 69 kV Bus a. Apply fault at the CHAD 269.000 (549919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAD 2 (549919) 69.0 kV to HARGISS 2 (549920) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_702 | 3 Phase fault on HARGISS 269.000 (549920) 69 kV Bus a. Apply fault at the HARGISS 269.000 (549920) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARGISS 2 (549920) 69.0 kV to MAIN STREET2 (549921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_703 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to GRAND 2 (549922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_704 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_705 | 3 Phase fault on GRAND 269.000 (549922) 69 kV Bus a. Apply fault at the GRAND 269.000 (549922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 2 (549922) 69.0 kV to MONROE 2 (549923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_706 | 3 Phase fault on LAUREL 269.000 (549924) 69 kV Bus a. Apply fault at the LAUREL 269.000 (549924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAUREL 2 (549924) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_707 | 3 Phase fault on NICHOLS 269.000 (549925) 69 kV Bus a. Apply fault at the NICHOLS 269.000 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 2 (549925) 69.0 kV to FRISCO 2 (549926) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_708 | 3 Phase fault on FRISCO 269.000 (549926) 69 kV Bus a. Apply fault at the FRISCO 269.000 (549926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRISCO 2 (549926) 69.0 kV to N HWY13 2 (549927) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_709 | 3 Phase fault on N HWY13 269.000 (549927) 69 kV Bus a. Apply fault at the N HWY13 269.000 (549927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HWY13 2 (549927) 69.0 kV to NORTON 2 (549928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_710 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_711 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to NEERGARD 2 (549930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_712 | 3 Phase fault on NEERGARD 269.000 (549930) 69 kV Bus a. Apply fault at the NEERGARD 269.000 (549930) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEERGARD 2 (549930) 69.0 kV to LECOMPTE 2 (549931) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_713 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_714 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_715 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_716 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_717 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_718 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_719 | 3 Phase fault on MENTOR 5161.00 (549963) 161 kV Bus a. Apply fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_720 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_721 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_722 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_723 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 7HUBEN (300042) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_724 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_725 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF3 (301506) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_726 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF4 (301510) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_727 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_728 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_729 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_730 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_731 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_732 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHRP (300302) 69.0 kV to 5LATHRP (300091) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_733 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MORGAN (300782) 69.0 kV to 5MORGAN (300101) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_734 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NORTON (300540) 69.0 kV to 5NORTON (300105) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_735 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_736 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_737 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 5THMHILB1 (300120) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_738 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HOLDEN (300336) 69.0 kV to 5HOLDENB2 (300124) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_739 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_740 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_741 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_742 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_743 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_744 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to NEO184 5 (547471) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_745 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WASHBRN (300763) 69.0 kV to WASHBURN5 (505485) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_746 | 3 Phase fault on 5OSCEOL 161.00 (301040) 161 kV Bus a. Apply fault at the 5OSCEOL 161.00 (301040) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 5OSCEOL (301040) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_747 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_748 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TURKEYCRK (301401) 69.0 kV to 5TURKEYCRK (301370) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_749 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_750 | 3 Phase fault on 5LATHROP 161.00 (344923) 161 kV Bus a. Apply fault at the 5LATHROP 161.00 (344923) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHROP (346093) 69.0 kV to 5LATHROP (344923) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_751 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_752 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_753 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_754 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_755 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_756 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_757 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_758 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_759 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_760 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_761 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_762 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_763 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_764 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_765 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_766 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_767 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY2 (512741) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_768 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR41 (523098) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_769 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR11 (523092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_770 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_771 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_772 | 3 Phase fault on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_773 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to G06-44 (560577) 115.0 kV to NOVUS1_TR2 2 (560578) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_774 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_775 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_776 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_777 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_778 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 2 1 (525538) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_779 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to HUGOTON3 (531481) 115.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_780 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_781 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_782 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_783 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_784 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_785 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of HOLCGEN (531447), BUFF_DUNES (523061, 523062), TOLK_2 (525562) and G20-008 (764981) units. | 1- Operational steady state fixes (existing caps/taps/gen set points) 2- Change acceleration factor to 0.7
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_786 | 3 Phase fault on SEWARD-3 115.00 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 115.00 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMSSWRD2 (531466) 69.0 kV to SEWARD-3 (531467) 115.0 kV to SEWARD 1 (531260) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_787 | 3 Phase fault on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_788 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_789 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_790 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_791 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_792 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_793 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G16-153 (588363) and G17-086 (589243) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_794 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G16-153 (588363) and G17-086 (589243) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_795 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_796 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_797 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_798 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_799 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_800 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G17-227 (760664), G17-221 (760307), G17-086 (589243) and G16-153 (588363) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_801 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G17-227 (760664), G17-221 (760307), G17-086 (589243) and G16-153 (588363) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_802 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_803 | 3 Phase fault on EDWRDVL5 161.00 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 161.00 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to EDWARVL3 (533238) 115.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_804 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_805 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_806 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_807 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_808 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_809 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_810 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_811 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_812 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of HOLCGEN (531447), BUFF_DUNES (523061, 523062), TOLK_2 (525562) and G20-008 (764981) units. | 1- Operational steady state fixes (existing caps/taps/gen set points) 2- Change acceleration factor to 0.7
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_813 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of HOLCGEN (531447), BUFF_DUNES (523061, 523062), TOLK_2 (525562) and G20-008 (764981) units. | 1- Operational steady state fixes (existing caps/taps/gen set points) 2- Change acceleration factor to 0.7
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_814 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_815 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_816 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_817 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_818 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_819 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to LNGVW 5 (541224) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_820 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_821 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_822 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_823 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_824 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_825 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN S2 (541320) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_826 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to LBRTYST5 (541248) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_827 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_828 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_829 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS2 (541290) 69.0 kV to BELTONS5 (541340) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_830 | 3 Phase fault on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_831 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_832 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-196 (762303) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_833 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_834 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_835 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_836 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_837 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_838 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_839 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_840 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_841 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH 12 (400) 13.8 kV Three Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_842 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-007 (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283) units. After disabling voltage relay, instantaneous frequency relays trips G20-007 units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_843 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-007 (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283) units. After disabling voltage relay, instantaneous frequency relays trips G20-007 units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_844 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_845 | 3 Phase fault on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to SWAVRLY5 (543063) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_846 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_847 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) and ROCKCK (541514) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_848 | 3 Phase fault on ATL109 5 161.00 (547466) 161 kV Bus a. Apply fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_849 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-082 (589204, 589203) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_850 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_851 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_852 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_853 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 (547471) 161.0 kV to NEO184 2 (547543) 69.0 kV to NEO184B1 (547709) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_854 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_855 | 3 Phase fault on MON383 5 161.00 (547480) 161 kV Bus a. Apply fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_856 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_857 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_858 | 3 Phase fault on NOL435 5 161.00 (547496) 161 kV Bus a. Apply fault at the NOL435 5 161.00 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 5 (547496) 161.0 kV to NOL435 2 (547610) 69.0 kV to NOL435 1 (547720) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_859 | 3 Phase fault on CPK446 5 161.00 (547499) 161 kV Bus a. Apply fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_860 | 3 Phase fault on RNM393 5 161.00 (547500) 161 kV Bus a. Apply fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_861 | 3 Phase fault on SUB N-161 161.00 (548820) 161 kV Bus a. Apply fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_862 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_863 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_864 | 3 Phase fault on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_865 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to JAMES RIVER2 (549904) 69.0 kV to JRPS XF1 1 (549944) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_866 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to JRPS 69B-2 2 (549903) 69.0 kV to JRPS XF2 1 (549945) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_867 | 3 Phase fault on NORTON 5161.00 (549967) 161 kV Bus a. Apply fault at the NORTON 5161.00 (549967) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (549967) 161.0 kV to NORTON 2 (549928) 69.0 kV to NORTON XF1 1 (549942) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_868 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_869 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_870 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Instantaneous frequency relay trips GI91 (99915) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_871 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_872 | 3 Phase fault on 2WARSAW 69.000 (300790) 69 kV Bus a. Apply fault at the 2WARSAW 69.000 (300790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WARSAW (300790) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_873 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_874 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_875 | 3 Phase fault on MON383 2 69.000 (547591) 69 kV Bus a. Apply fault at the MON383 2 69.000 (547591) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 2 (547591) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_876 | 3 Phase fault on JOP430 2 69.000 (547608) 69 kV Bus a. Apply fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP430 2 (547608) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_877 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_878 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_879 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_880 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_001 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_002 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_003 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_004 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_005 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_006 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_007 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_008 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_009 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_010 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_011 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of HOLCGEN (531447),Tolk (525562), HARRNGTON3 (523973) and G20-008 (764981, 764984) units and observed voltage issues at BUFF_DUNES (523118), LAMAR7 (599950) and FINNEY 7 (523853). | 1- Operational steady state fixes (existing caps/taps/gen set points) 2- Change acceleration factor to 0.7
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G17-227 (760664), G17-221 (760307), G17-086 (589243) and G16-153 (588363) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_013 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G17-227 (760664), G17-221 (760307), G17-086 (589243) and G16-153 (588363) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_014 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G17-227 (760664), G17-221 (760307), G17-086 (589243) and G16-153 (588363) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_015 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_016 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_017 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_018 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_019 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS (532751), LEC U5 (532663) IAT G2 (542962) and COOPER (640009) units. | Reduce clearing time to 3.75 cycles. TO submitted fault sheet states the clearing time to be 3.75 cycles.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_020 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G17-227 (760664), G17-221 (760307), G17-086 (589243) and G16-153 (588363) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_021 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_022 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_023 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_024 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_025 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_026 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_027 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_028 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_029 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844), G16-153 (588363) and G17-086 (589243) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_030 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_031 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_032 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Instantaneous frequency relay trips G11-008 (539858), G19-058 (763895), G19-063 (763926) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_033 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage and frequency relays trip G11-008 (539858). | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_036 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_037 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_038 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_039 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_040 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_041 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_042 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_043 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_044 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_045 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_046 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_048 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G17-121 (761841, 761844) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_049 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_051 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips OUTLAW (541546, 541549,541550) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 b.3. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply Fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 b.2. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 b.3. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 b.4. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply Fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.3. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.4. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on KCSOUTH5 161.00 (541245) 161 kV Bus a. Apply Fault at the KCSOUTH5 161.00 (541245) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 b.2. NRAYMORETP 5 (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on STROTHR2 69.000 (533556) 69 kV Bus a. Apply Fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.2. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.3. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.4. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.5. EAST SUB 2 (533990) 69.0 kV to GEN-2020-003 (765085) 69.0 kV Transmission Circuit #1 b.6. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on OAK 2 69.000 (533547) 69 kV Bus a. Apply Fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.3. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.4. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.5. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.3. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on NORTON 5 161.00 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply Fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.4. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-007 (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G20-007 (766271, 766268, 766265, 766262, 766280, 766277, 766274, 766283) units. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to ATLNTIC7 (542940) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to ATLNTIC7 (542940) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on PIONEER3 115.00 (531391) 115 kV Bus a. Apply Fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. HICKOCK3 (531378) 115.0 kV to PIONEER3 (531391) 115.0 kV Transmission Circuit #1 b.3. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.4. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.5. PIONEER3 (531391) 115.0 kV to ULYSPLT3 (531490) 115.0 kV Transmission Circuit #1 b.6. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 b.7. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.8. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 b.9. PIONEER3 (531391) 115.0 kV to PIONEER2 (531390) 69.0 kV to PIONEER1 (531251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply Fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to Trip Bus # b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.5. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.6. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.7. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.8. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.9. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 b.10. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.11. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.12. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.13. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.14. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WALDO 3 115.00 (539698) 115 kV Bus a. Apply Fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.3. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.4. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.5. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.6. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.7. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.8. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.9. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.10. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 b.11. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 b.12. SMITH-C3 (539693) 115.0 kV to SMITH-C1 (539731) 34.5 kV to SMITHC-T (539934) 7.2 kV Three Winding #1 b.13. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply Fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWNDTAP3 (531476) 115.0 kV to Trip Bus # b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. GRDNCTY3 (531445) 115.0 kV to S2 GEN 1 (531459) 13.8 kV Two Winding #1 b.4. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.5. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.6. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.3. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 b.4. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on JONES3 115.00 (531379) 115 kV Bus a. Apply Fault at the JONES3 115.00 (531379) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.3. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CIM-PLT3 (539654) 115.0 kV to CIM-PLT (539780) 13.8 kV Two Winding #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply Fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. GRDNCTY3 (531445) 115.0 kV to S2 GEN 1 (531459) 13.8 kV Two Winding #1 b.4. GRDNCTY3 (531445) 115.0 kV to S4 GEN 1 (531461) 13.2 kV Two Winding #1 b.5. GRDNCTY3 (531445) 115.0 kV to S5 GEN 1 (531462) 13.2 kV Two Winding #1 b.6. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.7. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.8. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.9. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.10. GRDNCTY3 (531445) 115.0 kV to GC-C 1 (531421) 34.5 kV to GC-CITY (531254) 13.8 kV Three Winding #1 b.11. GRDNCTY3 (531445) 115.0 kV to GARDNCY2 (531423) 69.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.4. SPF X3 1 (505495) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 b.4. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on AVOCA 5 161.00 (504000) 161 kV Bus a. Apply Fault at the AVOCA 5 161.00 (504000) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVOCA 5 (504000) 161.0 kV to BEAVER 5 (505480) 161.0 kV Transmission Circuit #1 b.2. AVOCA 5 (504000) 161.0 kV to EROGERS5 (506931) 161.0 kV Transmission Circuit #1 b.3. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 b.4. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on BEAVER 5 161.00 (505480) 161 kV Bus a. Apply Fault at the BEAVER 5 161.00 (505480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 b.2. BEAVER 5 (505480) 161.0 kV to EUREKA 5 (506932) 161.0 kV Transmission Circuit #1 b.3. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on STOCKTN5 161.00 (505498) 161 kV Bus a. Apply Fault at the STOCKTN5 161.00 (505498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 b.2. STOCKTN5 (505498) 161.0 kV to STK #1 1 (505500) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on TABLE R5 161.00 (505472) 161 kV Bus a. Apply Fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5RENOHLWTP (300130) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 b.2. 5RENOHLWTP (300130) 161.0 kV to 5RIVERSIDE (300805) 161.0 kV Transmission Circuit #1 b.3. 5RENOHLWTP (300130) 161.0 kV to 5RENOHLW (301129) 161.0 kV Transmission Circuit #1 b.4. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.5. 5COMPTN (300719) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 b.6. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.7. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.8. TABLE R5 (505472) 161.0 kV to TBR1&2 1 (505476) 13.8 kV Two Winding #1 b.9. TABLE R5 (505472) 161.0 kV to TBR3&4 1 (505478) 13.8 kV Two Winding #1 b.10. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.11. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.12. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.13. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on TABLE R5 161.00 (505472) 161 kV Bus a. Apply Fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.3. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.4. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.5. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.6. TABLE R5 (505472) 161.0 kV to TBR1&2 1 (505476) 13.8 kV Two Winding #1 b.7. TABLE R5 (505472) 161.0 kV to TBR3&4 1 (505478) 13.8 kV Two Winding #1 b.8. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.9. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.10. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.11. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply Fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2WASHBRN (300763) 69.0 kV to WASHBURN5 (505485) 161.0 kV Two Winding #1 b.2. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 b.3. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 b.4. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.5. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 b.6. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.2. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.3. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.5. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.6. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.7. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.8. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 b.2. 2JASPER (300649) 69.0 kV to 2MEDOC (300653) 69.0 kV Transmission Circuit #1 b.3. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.4. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.6. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.7. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.2. 2BOWRML (300659) 69.0 kV to 2REEDS (300751) 69.0 kV Transmission Circuit #1 b.3. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.4. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.6. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.2. 2DMNDGR (300744) 69.0 kV to 2DMNDTP (300745) 69.0 kV Transmission Circuit #1 b.3. 2DMNDTP (300745) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 b.4. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. 2NEOSHO (300750) 69.0 kV to 2SPGCTP (300754) 69.0 kV Transmission Circuit #1 b.6. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.7. 2SPGCTP (300754) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 b.8. 2SPGCTP (300754) 69.0 kV to 2SPURGNTP (300764) 69.0 kV Transmission Circuit #1 b.9. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.10. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 b.2. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.5. SPF X1 1 (505491) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ASHGRV (300657) 69.0 kV to 2CAVESP (300664) 69.0 kV Transmission Circuit #1 b.2. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 b.3. 2ASHGRV (300657) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 b.4. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 b.5. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 b.6. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #2 b.7. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply Fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.4. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.5. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 b.7. TRUMAN 5 (505502) 161.0 kV to TRU123 1 (505504) 13.8 kV Two Winding #1 b.8. TRUMAN 5 (505502) 161.0 kV to TRU456 1 (505506) 13.8 kV Two Winding #1 b.9. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.5. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.6. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.7. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. NXA X1 1 (505497) 13.8 kV to NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. NXA X2 1 (505499) 13.8 kV to NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on SPRINGH3 115.00 (533267) 115 kV Bus a. Apply Fault at the SPRINGH3 115.00 (533267) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.4. SPRINGH3 (533267) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply Fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on JTEC 5161.00 (549954) 161 kV Bus a. Apply Fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 b.2. JTEC GEN#1 1 (549890) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.3. JTEC CTS 1 (549891) 12.5 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.4. JTEC GEN#2 1 (549893) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.5. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.6. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.7. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply Fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 b.4. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.4. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply Fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JRPS GT1 1 (549900) 13.8 kV to JAMES RIVER5 (549961) 161.0 kV Two Winding #1 b.2. JRPS GT2 1 (549901) 13.8 kV to JAMES RIVER5 (549961) 161.0 kV Two Winding #1 b.3. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.4. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 b.5. JAMES RIVER5 (549961) 161.0 kV to JRPS 69B-2 2 (549903) 69.0 kV to JRPS XF2 1 (549945) 13.2 kV Three Winding #1 b.6. JAMES RIVER5 (549961) 161.0 kV to JAMES RIVER2 (549904) 69.0 kV to JRPS XF1 1 (549944) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on MILL 5161.00 (549962) 161 kV Bus a. Apply Fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.3. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.4. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on MENTOR 5161.00 (549963) 161 kV Bus a. Apply Fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 b.2. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.3. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on NORTON 5161.00 (549967) 161 kV Bus a. Apply Fault at the NORTON 5161.00 (549967) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 b.2. NORTON 5 (549967) 161.0 kV to NORTON 2 (549928) 69.0 kV to NORTON XF1 1 (549942) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on MC CARTNEY 5161.00 (549968) 161 kV Bus a. Apply Fault at the MC CARTNEY 5161.00 (549968) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCCARTNEY (301568) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #z1 b.2. MAC GT1&2 1 (549892) 13.8 kV to MC CARTNEY 5 (549968) 161.0 kV Two Winding #1 b.3. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.4. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.5. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.6. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on CLAY 5161.00 (549970) 161 kV Bus a. Apply Fault at the CLAY 5161.00 (549970) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.3. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.4. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on PIC WEST 5161.00 (549971) 161 kV Bus a. Apply Fault at the PIC WEST 5161.00 (549971) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit # b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on AFTON 5 161.00 (512632) 161 kV Bus a. Apply Fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.4. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 b.2. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 b.4. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.5. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.6. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 b.7. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 b.8. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 b.2. G20-072-TAP (764355) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 b.4. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 b.5. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.7. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 b.8. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 b.9. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON (345409) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.3. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply Fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.5. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply Fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 b.2. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z b.3. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.4. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 b.5. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply Fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.2. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.3. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.4. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.5. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.3. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.4. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on RIV167 5 161.00 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on NEO184 5 161.00 (547471) 161 kV Bus a. Apply Fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2NEOSAC (300748) 69.0 kV to NEO184 5 (547471) 161.0 kV Two Winding #1 b.2. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 b.3. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.4. NEO184 5 (547471) 161.0 kV to NEO184 2 (547543) 69.0 kV to NEO184B1 (547709) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.4. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply Fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.4. DAD368 5 (547478) 161.0 kV to GEN-2019-016 (763560) 161.0 kV Transmission Circuit #1 b.5. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.4. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on FIR417 5 161.00 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 161.00 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on OAK432 5 161.00 (547494) 161 kV Bus a. Apply Fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on NOL435 5 161.00 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 161.00 (547496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROVE 5 (510411) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.2. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.3. DEC392 5 (547484) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.4. NOL435 5 (547496) 161.0 kV to NOL435 2 (547610) 69.0 kV to NOL435 1 (547720) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on CPK446 5 161.00 (547499) 161 kV Bus a. Apply Fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.3. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply Fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.4. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.5. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.6. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-079-TAP (764310) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit # b.2. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-079-TAP (764310) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit # b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to A2G349 1 (547650) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 b.2. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.4. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.5. DAD368 5 (547478) 161.0 kV to GEN-2019-016 (763560) 161.0 kV Transmission Circuit #1 b.6. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 b.4. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on JOP422 5 161.00 (547607) 161 kV Bus a. Apply Fault at the JOP422 5 161.00 (547607) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to L3G3821 (547653) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to L2G382 1 (547652) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to L1G382 1 (547651) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.6. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.7. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 b.8. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 b.9. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.6. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 b.7. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply Fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.2. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 b.3. 5MAURER 2 (344558) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.3. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.4. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.5. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.6. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.7. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.8. EAST SUB 2 (533990) 69.0 kV to GEN-2020-003 (765085) 69.0 kV Transmission Circuit #1 b.9. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply Fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on NESCTY 3 115.00 (530607) 115 kV Bus a. Apply Fault at the NESCTY 3 115.00 (530607) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NESCTY 3 (530607) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NESCTY 3 (530607) 115.0 kV to NESS-CT1 (539722) 34.5 kV to NES-CT-T (539924) 13.8 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.9. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.10. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 b.2. HITCHLD_TR11 (523092) 13.2 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV Three Winding #1 b.3. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply Fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.3. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.4. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.5. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.6. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.7. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.8. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.9. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.10. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.11. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.12. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.13. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.14. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPNSPUR_COL1 (524298) 34.5 kV to SPNSPUR_TR11 (524297) 13.2 kV to SPNSPUR_COL7 (524299) 345.0 kV Three Winding #1 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #1 b.4. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 b.5. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.7. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.8. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on WEST SUB 2 69.000 (533991) 69 kV Bus a. Apply Fault at the WEST SUB 2 69.000 (533991) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEST SUB 2 (533991) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 b.2. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply Fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LATHRP (300091) 161.0 kV to 2LATHRP (300302) 69.0 kV Two Winding #1 b.2. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply Fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.2. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply Fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on 2VERONA 69.000 (300680) 69 kV Bus a. Apply Fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2VERONA (300680) 69.0 kV to 2PRDYTP (300679) 69.0 kV Transmission Circuit #1 b.2. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply Fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 b.2. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply Fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply Fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SHARSNV (301515) 161.0 kV to 2SHARSNV (300709) 69.0 kV Two Winding #1 b.2. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on GEN-2011-022345.00 (523215) 345 kV Bus a. Apply Fault at the GEN-2011-022345.00 (523215) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2011-022 (523215) 345.0 kV to G11-022XFMR1 (523211) 34.5 kV Two Winding #1 b.2. GEN-2011-022 (523215) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply Fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply Fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.2. NEOSHOS4 (533020) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on ARKCTYE2 69.000 (533542) 69 kV Bus a. Apply Fault at the ARKCTYE2 69.000 (533542) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARKCTYE2 (533542) 69.0 kV to ARKCTYW2 (533540) 69.0 kV Transmission Circuit #z1 b.2. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on PARIS 2 69.000 (533548) 69 kV Bus a. Apply Fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARIS 2 (533548) 69.0 kV to ARKCTYW2 (533540) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply Fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.2. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply Fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SC5SILV2 (533554) 69.0 kV to ARKCTYE2 (533542) 69.0 kV Transmission Circuit #1 b.2. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on BURLJCT2 69.000 (533626) 69 kV Bus a. Apply Fault at the BURLJCT2 69.000 (533626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on CC2SHAR2 69.000 (533629) 69 kV Bus a. Apply Fault at the CC2SHAR2 69.000 (533629) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC2SHAR2 (533629) 69.0 kV to CC5SHAR1 (533888) 12.5 kV Two Winding #1 b.2. CC2SHAR2 (533629) 69.0 kV to CC6SHAR1 (533889) 12.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply Fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROLLHLS3 (539643) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on CIM-PLT3 115.00 (539654) 115 kV Bus a. Apply Fault at the CIM-PLT3 115.00 (539654) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIM-PLT3 (539654) 115.0 kV to WALKMYR3 (531405) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to HAYNE3 (539640) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply Fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDSR 5 (541217) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply Fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WSTELEC5 (541222) 161.0 kV to WSTELEC_CAP5 (541149) 161.0 kV Transmission Circuit #r b.2. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply Fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDVWE 5 (541223) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 b.2. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply Fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LKWINBG5 (541243) 161.0 kV to PHILL 5 (541225) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on LEXNTON2 69.000 (541265) 69 kV Bus a. Apply Fault at the LEXNTON2 69.000 (541265) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEXNTON2 (541265) 69.0 kV to LEX69 2 (541264) 69.0 kV Transmission Circuit #1 b.2. LEXNTON2 (541265) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on 13&40 2 69.000 (541266) 69 kV Bus a. Apply Fault at the 13&40 2 69.000 (541266) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 13&40 2 (541266) 69.0 kV to ODESSA 2 (541267) 69.0 kV Transmission Circuit #1 b.2. 13&40 2 (541266) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on PHILL 5 161.00 (541225) 161 kV Bus a. Apply Fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 b.2. PHILL 2 (541280) 69.0 kV to RGREEN 2 (541279) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply Fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on ANCONDA2 69.000 (541292) 69 kV Bus a. Apply Fault at the ANCONDA2 69.000 (541292) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANCONDA2 (541292) 69.0 kV to FREEMAN2 (541291) 69.0 kV Transmission Circuit #1 b.2. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on HSNVLW 2 69.000 (541293) 69 kV Bus a. Apply Fault at the HSNVLW 2 69.000 (541293) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVLW 2 (541293) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on HSNVLS 2 69.000 (541294) 69 kV Bus a. Apply Fault at the HSNVLS 2 69.000 (541294) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVLS 2 (541294) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.2. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply Fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 b.2. HSNVL 2 (541295) 69.0 kV to HSNVLSW2 (541296) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply Fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTOAK2 (541300) 69.0 kV to WBURGP 2 (541268) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply Fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on BELTONS5 161.00 (541340) 161 kV Bus a. Apply Fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELTONS5 (541340) 161.0 kV to TURNER_RD5 (541259) 161.0 kV Transmission Circuit #1 b.2. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to PECULR 7 (541198) 345.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 5 (541342) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on RAYMORE 69.000 (541347) 69 kV Bus a. Apply Fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAYMORE (541347) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 b.2. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on KNGSVIL 2 69.000 (541387) 69 kV Bus a. Apply Fault at the KNGSVIL 2 69.000 (541387) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNGSVIL 2 (541387) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.2. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply Fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply Fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 b.2. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply Fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply Fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCYRUS5 (543057) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on MALTABN5 161.00 (543059) 161 kV Bus a. Apply Fault at the MALTABN5 161.00 (543059) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 b.2. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALSBRY5 (543062) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on PAOLA 5 161.00 (543069) 161 kV Bus a. Apply Fault at the PAOLA 5 161.00 (543069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAOLA 5 (543069) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 b.2. PAOLA 5 (543069) 161.0 kV to CENTENL5 (543067) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply Fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWAVRLY2 (543094) 69.0 kV to SWAVRLY5 (543063) 161.0 kV Two Winding #1 b.2. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on MAYVWTP2 69.000 (543096) 69 kV Bus a. Apply Fault at the MAYVWTP2 69.000 (543096) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAYVWTP2 (543096) 69.0 kV to LEXNTON2 (541265) 69.0 kV Transmission Circuit #1 b.2. MAYVWTP2 (543096) 69.0 kV to 13&40 2 (541266) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on HIGNSVL2 69.000 (543099) 69 kV Bus a. Apply Fault at the HIGNSVL2 69.000 (543099) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGNSVL2 (543099) 69.0 kV to CTY HIG2 (543098) 69.0 kV Transmission Circuit #1 b.2. HIGNSVL2 (543099) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on AMOCOPL2 69.000 (543100) 69 kV Bus a. Apply Fault at the AMOCOPL2 69.000 (543100) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AMOCOPL2 (543100) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.2. AMOCOPL2 (543100) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on CORDERTP2 69.000 (543657) 69 kV Bus a. Apply Fault at the CORDERTP2 69.000 (543657) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORDERTP2 (543657) 69.0 kV to CTY HIG2 (543098) 69.0 kV Transmission Circuit #1 b.2. CORDERTP2 (543657) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on EXP449T2 69.000 (547438) 69 kV Bus a. Apply Fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXP449T2 (547438) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 b.2. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on PRC460 2 69.000 (547449) 69 kV Bus a. Apply Fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 b.2. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on WEB436 2 69.000 (547527) 69 kV Bus a. Apply Fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEB436 2 (547527) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 b.2. WEB436 2 (547527) 69.0 kV to ORO110 2 (547534) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on COL 94 2 69.000 (547530) 69 kV Bus a. Apply Fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on NIX114 2 69.000 (547535) 69 kV Bus a. Apply Fault at the NIX114 2 69.000 (547535) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NIX114 2 (547535) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 b.2. NIX114 2 (547535) 69.0 kV to BHJ415 2 (547604) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on AUR124 2 69.000 (547537) 69 kV Bus a. Apply Fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 b.2. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on MON152 2 69.000 (547540) 69 kV Bus a. Apply Fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON152 2 (547540) 69.0 kV to AUR124 2 (547537) 69.0 kV Transmission Circuit #1 b.2. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on GAT258 2 69.000 (547551) 69 kV Bus a. Apply Fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GAT258 2 (547551) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 b.2. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on BAX271 2 69.000 (547554) 69 kV Bus a. Apply Fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAX271 2 (547554) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 b.2. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on TIP292 2 69.000 (547559) 69 kV Bus a. Apply Fault at the TIP292 2 69.000 (547559) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 2 (547559) 69.0 kV to NEO332 2 (547571) 69.0 kV Transmission Circuit #1 b.2. TIP292 2 (547559) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on JOP360 2 69.000 (547581) 69 kV Bus a. Apply Fault at the JOP360 2 69.000 (547581) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP360 2 (547581) 69.0 kV to ATL109 2 (547533) 69.0 kV Transmission Circuit #1 b.2. JOP360 2 (547581) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on JOP389 2 69.000 (547592) 69 kV Bus a. Apply Fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 2 (547592) 69.0 kV to EXP449T2 (547438) 69.0 kV Transmission Circuit #1 b.2. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNM393 2 (547595) 69.0 kV to KOD471 2 (547463) 69.0 kV Transmission Circuit #1 b.2. RNM393 2 (547595) 69.0 kV to RNM393 5 (547500) 161.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on COX 269.000 (549910) 69 kV Bus a. Apply Fault at the COX 269.000 (549910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COX 2 (549910) 69.0 kV to PLAINVIEW 2 (549905) 69.0 kV Transmission Circuit #1 b.2. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on DAYTON 269.000 (549913) 69 kV Bus a. Apply Fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAYTON 2 (549913) 69.0 kV to FORT 2 (549914) 69.0 kV Transmission Circuit #1 b.2. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on LAUREL 269.000 (549924) 69 kV Bus a. Apply Fault at the LAUREL 269.000 (549924) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAUREL 2 (549924) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 b.2. LAUREL 2 (549924) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 2 (549925) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 b.2. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on FRISCO 269.000 (549926) 69 kV Bus a. Apply Fault at the FRISCO 269.000 (549926) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRISCO 2 (549926) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 b.2. FRISCO 2 (549926) 69.0 kV to N HWY13 2 (549927) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on GEN-2010-014345.00 (576395) 345 kV Bus a. Apply Fault at the GEN-2010-014345.00 (576395) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2010-014 (576395) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 b.2. GEN-2010-014 (576395) 345.0 kV to G10-014XFMR2 (576398) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on GEN-2017-108161.00 (761271) 161 kV Bus a. Apply Fault at the GEN-2017-108161.00 (761271) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-108 (761271) 161.0 kV to G17-108-XFM1 (761272) 34.5 kV Two Winding #1 b.2. GEN-2017-108 (761271) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on GEN-2017-195345.00 (762279) 345 kV Bus a. Apply Fault at the GEN-2017-195345.00 (762279) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-195 (762279) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-195 (762279) 345.0 kV to G17-195XFM1 (762280) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on GEN-2020-007345.00 (766260) 345 kV Bus a. Apply Fault at the GEN-2020-007345.00 (766260) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-007 (766260) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-007 (766260) 345.0 kV to G20-007-XFM1 (766264) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 7 (531465) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR7 (531512) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEOSHON4 (533022) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDLIAW_CAP5 (541146) 161.0 kV Transmission Circuit #r b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply Fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWAVRLY5 (543063) 161.0 kV to MALTABN5 (543059) 161.0 kV Transmission Circuit #1 b.2. SWAVRLY5 (543063) 161.0 kV to SWAVRLY2 (543094) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.2. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on NEO184 5 161.00 (547471) 161 kV Bus a. Apply Fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO184 5 (547471) 161.0 kV to 2NEOSAC (300748) 69.0 kV Two Winding #1 b.2. NEO184 5 (547471) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAD368 5 (547478) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON383 5 (547480) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 5 (547483) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.2. NICHOLS 5 (549956) 161.0 kV to JUNCTION 5 (549955) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on OAK 2 69.000 (533547) 69 kV Bus a. Apply Fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to CRESWLN2 (533543) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on UDALL 2 69.000 (533559) 69 kV Bus a. Apply Fault at the UDALL 2 69.000 (533559) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UDALL 2 (533559) 69.0 kV to RICHLAN2 (533550) 69.0 kV Transmission Circuit #1 b.2. UDALL 2 (533559) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON383 2 (547591) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 b.2. MON383 2 (547591) 69.0 kV to MON383 5 (547480) 161.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on JOP430 2 69.000 (547608) 69 kV Bus a. Apply Fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP430 2 (547608) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 b.2. JOP430 2 (547608) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on NORTON 5 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTON 5 (543064) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on 5NORTON (300105) 161 kV Bus a. Apply Fault at the 5NORTON (300105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on CORDERTP2 (543657) 69 kV Bus a. Apply Fault at the CORDERTP2 (543657) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORDERTP2 (543657) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on CTY HIG2 (543098) 69 kV Bus a. Apply Fault at the CTY HIG2 (543098) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTY HIG2 (543098) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on HIGNSVL2 (543099) 69 kV Bus a. Apply Fault at the HIGNSVL2 (543099) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGNSVL2 (543099) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on WHGNSVL2 (543102) 69 kV Bus a. Apply Fault at the WHGNSVL2 (543102) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHGNSVL2 (543102) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on MAYVWTP2 (543096) 69 kV Bus a. Apply Fault at the MAYVWTP2 (543096) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAYVWTP2 (543096) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on SALSBRY5 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALSBRY5 (543062) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on 5THMHILB1 (300120) 161 kV Bus a. Apply Fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on 5THMHLB2 (300132) 161 kV Bus a. Apply Fault at the 5THMHLB2 (300132) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB2 (300132) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on 5THMHLB4 (301443) 161 kV Bus a. Apply Fault at the 5THMHLB4 (301443) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on 5MAURER 2 (344558) 161 kV Bus a. Apply Fault at the 5MAURER 2 (344558) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MAURER 2 (344558) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on WINFLD 2 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINFLD 2 (533561) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on TIMBJCT2 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on OAK 2 (533547) 69 kV Bus a. Apply Fault at the OAK 2 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on FINNEY 7 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on HOLCOMB3 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on CIM-PLT3 (539654) 115 kV Bus a. Apply Fault at the CIM-PLT3 (539654) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIM-PLT3 (539654) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on NORTH6T2 (531389) 69 kV Bus a. Apply Fault at the NORTH6T2 (531389) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTH6T2 (531389) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on GRTBEND3 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on CRAIG 5 (542978) 161 kV Bus a. Apply Fault at the CRAIG 5 (542978) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on LENEXA 5 (543038) 161 kV Bus a. Apply Fault at the LENEXA 5 (543038) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LENEXA 5 (543038) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_381 | Single Phase Fault with Stuck Breaker on WGARDNR5 (542966) 161 kV Bus a. Apply Fault at the WGARDNR5 (542966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_382 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_383 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_384 | Single Phase Fault with Stuck Breaker on LNGVW 5 (541224) 161 kV Bus a. Apply Fault at the LNGVW 5 (541224) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 5 (541224) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_385 | Single Phase Fault with Stuck Breaker on KETCHEM7 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_386 | Single Phase Fault with Stuck Breaker on HAWTH 7 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_387 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips G18-031 (762672) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_388 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_389 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_390 | Single Phase Fault with Stuck Breaker on HSNVL 2 (541295) 69 kV Bus a. Apply Fault at the HSNVL 2 (541295) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVL 2 (541295) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_391 | Single Phase Fault with Stuck Breaker on ORO110 5 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_392 | Single Phase Fault with Stuck Breaker on JOP389 5 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 5 (547483) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_393 | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_394 | Single Phase Fault with Stuck Breaker on SEDALIA5 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_395 | Single Phase Fault with Stuck Breaker on S.OTTWA5 (543066) 161 kV Bus a. Apply Fault at the S.OTTWA5 (543066) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.OTTWA5 (543066) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_396 | Single Phase Fault with Stuck Breaker on PAOLA 5 (543069) 161 kV Bus a. Apply Fault at the PAOLA 5 (543069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAOLA 5 (543069) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_397 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_398 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_399 | Single Phase Fault with Stuck Breaker on RIV167 2 (547541) 69 kV Bus a. Apply Fault at the RIV167 2 (547541) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_400 | Single Phase Fault with Stuck Breaker on JOP 59 2 (547525) 69 kV Bus a. Apply Fault at the JOP 59 2 (547525) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 59 2 (547525) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_401 | Single Phase Fault with Stuck Breaker on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_402 | Single Phase Fault with Stuck Breaker on SPRGFLD2 (505494) 69 kV Bus a. Apply Fault at the SPRGFLD2 (505494) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD2 (505494) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_403 | Single Phase Fault with Stuck Breaker on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 5 (549969) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_404 | Single Phase Fault with Stuck Breaker on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_405 | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_406 | Single Phase Fault with Stuck Breaker on DAD368 5 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAD368 5 (547478) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_407 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_408 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_409 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_410 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_EDE1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_EDE2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_EDE3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_EDE4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_EDE5 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_EDE6 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy10 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy11 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy12 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy13 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy14 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy15 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy16 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy17 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy18 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy19 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy20 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy21 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy22 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy23 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy24 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy25 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy26 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy27 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy28 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy29 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy30 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy31 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy32 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy33 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy34 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy35 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy36 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy37 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy38 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy39 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy40 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy41 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy42 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy43 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy44 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy45 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy46 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy47 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy48 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy49 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy5 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy50 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy51 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy52 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy53 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy54 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy55 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy56 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy57 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy58 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy59 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy6 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy60 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy7 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy8 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy9 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_GRDA1 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_GRDA2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_INDN1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_INDN2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_INDN3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_OKGE1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_OKGE2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPRM1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPS1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPS2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPS3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPS4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPS5 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPS6 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SUNC1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SUNC2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SWPA1 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SWPA2 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage relay trips FRMR CTY W1 (635020) unit. | Protection disabled without any impact on stability.
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_015 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of OUTLAW (541546, 541549,541550) units. | Disabling the Drive Train at Outlaw (541546, 541549,541550) resolves the issue.
03 CENTRAL | DISIS-2020-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_016 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of OUTLAW (541546, 541549,541550) units. | Disabling the Drive Train at Outlaw (541546, 541549,541550) resolves the issue.
03 CENTRAL | DISIS-2020-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_419 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of G08-124 (579483, 579486) units. | Reduce clearing time to 5 cycles.
03 CENTRAL | DISIS-2020-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_460 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of OUTLAW (541546, 541549,541550) units. | Disabling the Drive Train at Outlaw (541546, 541549,541550) resolves the issue.
03 CENTRAL | DISIS-2020-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_461 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of OUTLAW (541546, 541549,541550) units. | Disabling the Drive Train at Outlaw (541546, 541549,541550) resolves the issue.
03 CENTRAL | DISIS-2020-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_462 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of OUTLAW (541546, 541549,541550) units. | Disabling the Drive Train at Outlaw (541546, 541549,541550) resolves the issue.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_001 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_002 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_003 | 3 Phase fault on 5ADAIR1 161.00 (344004) 161 kV Bus a. Apply fault at the 5ADAIR1 161.00 (344004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR1 (344004) 161.0 kV to 2ADAIR 1 (346005) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_004 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_005 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.2. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_006 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_007 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_008 | 3 Phase fault on 5COMPTN 161.00 (300719) 161 kV Bus a. Apply fault at the 5COMPTN 161.00 (300719) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_009 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.3. BUFORD 5 (504440) 161.0 kV to NORFORK5 (505448) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_010 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.2. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_011 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_012 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_013 | 3 Phase fault on 5GRANDVIEW% 161.00 (338099) 161 kV Bus a. Apply fault at the 5GRANDVIEW% 161.00 (338099) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_014 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_015 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_016 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_017 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_018 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_019 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_020 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_021 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_022 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_023 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_024 | 3 Phase fault on CONCRDTP2 69.000 (541523) 69 kV Bus a. Apply fault at the CONCRDTP2 69.000 (541523) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to CONCRDTP2 (541523) 69.0 kV Transmission Circuit #1 b.2. CONCORD2 (541319) 69.0 kV to CONCRDTP2 (541523) 69.0 kV Transmission Circuit #1 b.3. CONCORD2 (541319) 69.0 kV to ENBRIDGE PS2 (541542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_025 | 3 Phase fault on FAYETVLTP2 69.000 (541383) 69 kV Bus a. Apply fault at the FAYETVLTP2 69.000 (541383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to FAYETVLTP2 (541383) 69.0 kV Transmission Circuit #1 b.2. WBURGP 2 (541268) 69.0 kV to FAYETVLTP2 (541383) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on GRDVWTP2 69.000 (541284) 69 kV Bus a. Apply fault at the GRDVWTP2 69.000 (541284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 b.3. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.4. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.5. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.6. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_028 | 3 Phase fault on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 b.3. FREEMAN2 (541291) 69.0 kV to FREEMAN_SP2 (541540) 69.0 kV Transmission Circuit #1 b.4. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.5. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 b.6. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_029 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 b.2. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_030 | 3 Phase fault on HLDENTP2 69.000 (541386) 69 kV Bus a. Apply fault at the HLDENTP2 69.000 (541386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to CNTRVIEW2 (541385) 69.0 kV Transmission Circuit #1 b.2. HOLDEN 2 (541278) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.3. RGREEN 2 (541279) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 b.4. CNTRVIEW2 (541385) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.5. HLDENTP2 (541386) 69.0 kV to KNGSVIL 2 (541387) 69.0 kV Transmission Circuit #1 b.6. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_031 | 3 Phase fault on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.3. POSTOAK2 (541300) 69.0 kV to POSTOAK1 (541373) 34.5 kV to POSTOAK_TER1 (541374) 2.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_032 | 3 Phase fault on CLNTPLT_CAP269.000 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP269.000 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_033 | 3 Phase fault on LEXNTON2 69.000 (541265) 69 kV Bus a. Apply fault at the LEXNTON2 69.000 (541265) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNTON2 (541265) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_034 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_035 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_036 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_037 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_038 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_039 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_040 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_041 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_042 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_043 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_044 | 3 Phase fault on NAVY 5 161.00 (542989) 161 kV Bus a. Apply fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_045 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_046 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_047 | 3 Phase fault on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_048 | 3 Phase fault on NORTON 5 161.00 (543064) 161 kV Bus a. Apply fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 b.2. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. NORTON 5 (543064) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_049 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_050 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_051 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. MERRIAM_CAP5 (542947) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_052 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_053 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_054 | 3 Phase fault on SWAVCAP2 69.000 (543012) 69 kV Bus a. Apply fault at the SWAVCAP2 69.000 (543012) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.2. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.3. SWAVCAP2 (543012) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_055 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_056 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_057 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_058 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_059 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_060 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_061 | 3 Phase fault on CORDER 2 69.000 (543097) 69 kV Bus a. Apply fault at the CORDER 2 69.000 (543097) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.2. CORDER 2 (543097) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.3. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.4. DOVER2 (543101) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.5. CORDERTP2 (543657) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.6. CORDER 2 (543097) 69.0 kV to CORDER1 (543150) 12.5 kV to CORDER_TER1 (543151) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_062 | 3 Phase fault on WHGNSVL2 69.000 (543102) 69 kV Bus a. Apply fault at the WHGNSVL2 69.000 (543102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNTON2 (541265) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.2. 13&40 2 (541266) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.3. MAYVWTP2 (543096) 69.0 kV to AMOCOPL2 (543100) 69.0 kV Transmission Circuit #1 b.4. CTY HIG2 (543098) 69.0 kV to HIGNSVL2 (543099) 69.0 kV Transmission Circuit #1 b.5. HIGNSVL2 (543099) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 b.6. AMOCOPL2 (543100) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 b.7. HIGNSVL2 (543099) 69.0 kV to HGNSVL1 (543152) 12.5 kV to HGNSVL_TER1 (543153) 2.4 kV Three Winding #1 b.8. WHGNSVL2 (543102) 69.0 kV to WHGNSVL1 (543154) 12.5 kV to WHGNSVL_TER1 (543155) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_063 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_064 | 3 Phase fault on KCSOUTH5 161.00 (541245) 161 kV Bus a. Apply fault at the KCSOUTH5 161.00 (541245) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCSOUTH5 (541245) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_065 | 3 Phase fault on OSAWTM_CAP5 161.00 (543135) 161 kV Bus a. Apply fault at the OSAWTM_CAP5 161.00 (543135) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWTM_CAP5 (543135) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_066 | 3 Phase fault on SWAVCAP5 161.00 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 161.00 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_067 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_068 | 3 Phase fault on COLLEG 2 69.000 (530574) 69 kV Bus a. Apply fault at the COLLEG 2 69.000 (530574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 b.2. COLLEG 2 (530574) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_069 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_070 | 3 Phase fault on BKHLTAP2 69.000 (530589) 69 kV Bus a. Apply fault at the BKHLTAP2 69.000 (530589) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.2. SUSANK 2 (530571) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.3. BNK HL 2 (530572) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.4. HITHMN 2 (530573) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_071 | 3 Phase fault on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_072 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_073 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_074 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_075 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_076 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_077 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_078 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_079 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_080 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_081 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_082 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_083 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_084 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. The issue is also observed in the PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_085 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_086 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_087 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_088 | 3 Phase fault on SETAB 3 115.00 (531464) 115 kV Bus a. Apply fault at the SETAB 3 115.00 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_089 | 3 Phase fault on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_090 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_091 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_092 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_093 | 3 Phase fault on GRANTTP3 115.00 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 115.00 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_094 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_095 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_096 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_097 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_098 | 3 Phase fault on SAT-TAP3 115.00 (531442) 115 kV Bus a. Apply fault at the SAT-TAP3 115.00 (531442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASKELL3 (531374) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.2. HASKELL3 (531374) 115.0 kV to SEWARD-3 (531467) 115.0 kV Transmission Circuit #1 b.3. PIONTAP3 (531392) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.4. SAT-TAP3 (531442) 115.0 kV to SATMKEC3 (539691) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_099 | 3 Phase fault on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_100 | 3 Phase fault on WILLIAM3 115.00 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 115.00 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_101 | 3 Phase fault on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.3. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_102 | 3 Phase fault on GANO 3 115.00 (531493) 115 kV Bus a. Apply fault at the GANO 3 115.00 (531493) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.3. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_103 | 3 Phase fault on KSAVWTP3 115.00 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 115.00 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_104 | 3 Phase fault on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_105 | 3 Phase fault on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.2. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.3. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_106 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_107 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_108 | 3 Phase fault on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_109 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_110 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_111 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_112 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_113 | 3 Phase fault on WALDO 3 115.00 (539698) 115 kV Bus a. Apply fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_114 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_115 | 3 Phase fault on PHLBURG3 115.00 (539685) 115 kV Bus a. Apply fault at the PHLBURG3 115.00 (539685) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_116 | 3 Phase fault on GLENELD3 115.00 (539663) 115 kV Bus a. Apply fault at the GLENELD3 115.00 (539663) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.2. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_117 | 3 Phase fault on JEWELL 3 115.00 (539669) 115 kV Bus a. Apply fault at the JEWELL 3 115.00 (539669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.2. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.4. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_118 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_119 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_120 | 3 Phase fault on 5LOGAN 161.00 (301161) 161 kV Bus a. Apply fault at the 5LOGAN 161.00 (301161) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MANSFDMN (300095) 161.0 kV to 5LOGAN (301161) 161.0 kV Transmission Circuit #1 b.2. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_121 | 3 Phase fault on WAVERLY3 115.00 (533278) 115 kV Bus a. Apply fault at the WAVERLY3 115.00 (533278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.2. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_122 | 3 Phase fault on MNTCLLO3 115.00 (533281) 115 kV Bus a. Apply fault at the MNTCLLO3 115.00 (533281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_123 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_124 | 3 Phase fault on MUND 3 115.00 (533282) 115 kV Bus a. Apply fault at the MUND 3 115.00 (533282) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_125 | 3 Phase fault on 166TH 3 115.00 (533233) 115 kV Bus a. Apply fault at the 166TH 3 115.00 (533233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.3. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_126 | 3 Phase fault on MIDLADN3 115.00 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 115.00 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_127 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_128 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_129 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_130 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_131 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_132 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_133 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_134 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_135 | 3 Phase fault on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_136 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_137 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_138 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_139 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_140 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_141 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_142 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_143 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_144 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_145 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_146 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_147 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_148 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_149 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_150 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_151 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_152 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_153 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_154 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_155 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_156 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_157 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_158 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_159 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_160 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_161 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_162 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_163 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_164 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_165 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_166 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_167 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_168 | 3 Phase fault on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.3. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_169 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_170 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 b.2. SC3MILL2 (533552) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 b.3. SC3MILL2 (533552) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 b.4. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_171 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC7CRES2 (533555) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_172 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_173 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_174 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_175 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_176 | 3 Phase fault on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_177 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_178 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_179 | 3 Phase fault on STROTHR2 69.000 (533556) 69 kV Bus a. Apply fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_180 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_181 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_182 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_183 | 3 Phase fault on EDWARVL3 115.00 (533238) 115 kV Bus a. Apply fault at the EDWARVL3 115.00 (533238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_184 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_185 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_186 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_187 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_188 | 3 Phase fault on UDALL 2 69.000 (533559) 69 kV Bus a. Apply fault at the UDALL 2 69.000 (533559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UDALL 2 (533559) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_189 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_190 | 3 Phase fault on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_191 | 3 Phase fault on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_192 | 3 Phase fault on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.4. NICHOL XF1 1 (549940) 13.2 kV to NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_193 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.3. MILL XF1 1 (549946) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_194 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 b.3. MILL XF2 1 (549948) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_195 | 3 Phase fault on HAWTHRN4 138.00 (510413) 138 kV Bus a. Apply fault at the HAWTHRN4 138.00 (510413) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 (510396) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.2. CHELSA4 (510410) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.3. CHELSA4 (510410) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 b.4. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_196 | 3 Phase fault on GROVE 5 161.00 (510411) 161 kV Bus a. Apply fault at the GROVE 5 161.00 (510411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 5 (510411) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_197 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_198 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_199 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_200 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_201 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_202 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_203 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_204 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_205 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_206 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 (510418) 69.0 kV to VINTAJC4 (510417) 138.0 kV to VINJT1-1 (510367) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_207 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_208 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_209 | 3 Phase fault on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_210 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_211 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_212 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_213 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_214 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_215 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_216 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_217 | 3 Phase fault on LOCSTGVKM 5 161.00 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 161.00 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_218 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_219 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_220 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_221 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_222 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_223 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_224 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_225 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_226 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_227 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_228 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_229 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_230 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_231 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_232 | 3 Phase fault on TONECE7 345.00 (512750) 345 kV Bus a. Apply fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_233 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_234 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.3. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_235 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.3. OCHILTREE 3 (523154) 115.0 kV to OCHILTREE 6 (523155) 230.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_236 | 3 Phase fault on TEXAS_CNTY 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_237 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_238 | 3 Phase fault on TEXAS_CNTY 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_239 | 3 Phase fault on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_240 | 3 Phase fault on COLE 3115.00 (523120) 115 kV Bus a. Apply fault at the COLE 3115.00 (523120) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 3 (523120) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_241 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. TXFARMS 3 (523140) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 b.3. SPEARMAN 3 (523186) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_242 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_243 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_244 | 3 Phase fault on WADE_TP 3115.00 (523145) 115 kV Bus a. Apply fault at the WADE_TP 3115.00 (523145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIPSCOMB 3 (523135) 115.0 kV to WADE_TP 3 (523145) 115.0 kV Transmission Circuit #1 b.2. WADE_TP 3 (523145) 115.0 kV to WADE 3 (523147) 115.0 kV Transmission Circuit #1 b.3. WADE_TP 3 (523145) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_245 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.5. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.7. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.8. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.9. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.10. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.11. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_246 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_247 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_248 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_249 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_250 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_251 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_252 | 3 Phase fault on BOL431 5 161.00 (547493) 161 kV Bus a. Apply fault at the BOL431 5 161.00 (547493) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_253 | 3 Phase fault on JOP391 5 161.00 (547593) 161 kV Bus a. Apply fault at the JOP391 5 161.00 (547593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.2. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_254 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. HOC404A1 (547715) 12.5 kV to HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_255 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_256 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_257 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_258 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_259 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_260 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_261 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MPLTAP (300036) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 b.3. 5MPLTAP (300036) 161.0 kV to 5LATHROP (344923) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_262 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_263 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_264 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.3. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.4. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_265 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_266 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_267 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_268 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_269 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_270 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_271 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_272 | 3 Phase fault on 5HIGBEEB1 161.00 (300066) 161 kV Bus a. Apply fault at the 5HIGBEEB1 161.00 (300066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HIGBEEB1 (300066) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_273 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_274 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_275 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_276 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_277 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_278 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_279 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_280 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_281 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_282 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5BTLFD (300348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_283 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_284 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5RIVRDL (300726) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_285 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_286 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_287 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_288 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to 5MORGANXF2 (301622) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_289 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_290 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_291 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_292 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_293 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_294 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_295 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOL (301040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_296 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_297 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_298 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_299 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_300 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_301 | 3 Phase fault on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STKAEC (300118) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_302 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5THMHLB2 (300132) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_303 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5THMHILTFERB (301511) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_304 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HOLDENB2 (300124) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_305 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB3 (300133) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_306 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5BEVIER (300381) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_307 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_308 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THOMHLXF1 (301508) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_309 | 3 Phase fault on 5THMHLB3 161.00 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 161.00 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5MEADVLB1 (300207) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_310 | 3 Phase fault on 5THMHLB3 161.00 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 161.00 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5THOMHLXF3 (301506) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_311 | 3 Phase fault on 5THMHLB3 161.00 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 161.00 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5THOMHLU3SU (301507) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_312 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2MOCITY (300304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_313 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_314 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_315 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_316 | 3 Phase fault on 2ELM 69.000 (300327) 69 kV Bus a. Apply fault at the 2ELM 69.000 (300327) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELM (300327) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_317 | 3 Phase fault on 5BTLFD 161.00 (300348) 161 kV Bus a. Apply fault at the 5BTLFD 161.00 (300348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_318 | 3 Phase fault on 2BEAMAN 69.000 (300527) 69 kV Bus a. Apply fault at the 2BEAMAN 69.000 (300527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEAMAN (300527) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_319 | 3 Phase fault on 2DRESDN 69.000 (300528) 69 kV Bus a. Apply fault at the 2DRESDN 69.000 (300528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DRESDN (300528) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_320 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_321 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_322 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_323 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_324 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_325 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_326 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_327 | 3 Phase fault on 2MALTAJ 69.000 (300536) 69 kV Bus a. Apply fault at the 2MALTAJ 69.000 (300536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAJ (300536) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_328 | 3 Phase fault on 2NAPTON 69.000 (300538) 69 kV Bus a. Apply fault at the 2NAPTON 69.000 (300538) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NAPTON (300538) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_329 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_330 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_331 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2FLORNC (300553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_332 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_333 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2MEDOC (300653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_334 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_335 | 3 Phase fault on 2ASHGRV 69.000 (300657) 69 kV Bus a. Apply fault at the 2ASHGRV 69.000 (300657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_336 | 3 Phase fault on 2BOWRML 69.000 (300659) 69 kV Bus a. Apply fault at the 2BOWRML 69.000 (300659) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOWRML (300659) 69.0 kV to 2REEDS (300751) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_337 | 3 Phase fault on 2CRANE 69.000 (300667) 69 kV Bus a. Apply fault at the 2CRANE 69.000 (300667) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CRANE (300667) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_338 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_339 | 3 Phase fault on 2ELWOOD 69.000 (300669) 69 kV Bus a. Apply fault at the 2ELWOOD 69.000 (300669) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_340 | 3 Phase fault on 5NIXA-1 161.00 (300678) 161 kV Bus a. Apply fault at the 5NIXA-1 161.00 (300678) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_341 | 3 Phase fault on 2PRDYTP 69.000 (300679) 69 kV Bus a. Apply fault at the 2PRDYTP 69.000 (300679) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PRDYTP (300679) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_342 | 3 Phase fault on 2VERONA 69.000 (300680) 69 kV Bus a. Apply fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_343 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_344 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_345 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_346 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_347 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_348 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_349 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_350 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_351 | 3 Phase fault on 2DMNDGR 69.000 (300744) 69 kV Bus a. Apply fault at the 2DMNDGR 69.000 (300744) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDGR (300744) 69.0 kV to 2DMNDTP (300745) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_352 | 3 Phase fault on 2DMNDTP 69.000 (300745) 69 kV Bus a. Apply fault at the 2DMNDTP 69.000 (300745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDTP (300745) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_353 | 3 Phase fault on 2DMNDTP 69.000 (300745) 69 kV Bus a. Apply fault at the 2DMNDTP 69.000 (300745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_354 | 3 Phase fault on 2NEOSAC 69.000 (300748) 69 kV Bus a. Apply fault at the 2NEOSAC 69.000 (300748) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to 2NEOSHO (300750) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_355 | 3 Phase fault on 2NEOSAC 69.000 (300748) 69 kV Bus a. Apply fault at the 2NEOSAC 69.000 (300748) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to 2SWTWT (300758) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_356 | 3 Phase fault on 2REEDS 69.000 (300751) 69 kV Bus a. Apply fault at the 2REEDS 69.000 (300751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_357 | 3 Phase fault on 2ELKTON 69.000 (300773) 69 kV Bus a. Apply fault at the 2ELKTON 69.000 (300773) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELKTON (300773) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_358 | 3 Phase fault on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2EUDORA (300774) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_359 | 3 Phase fault on 2FRSTOE 69.000 (300776) 69 kV Bus a. Apply fault at the 2FRSTOE 69.000 (300776) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FRSTOE (300776) 69.0 kV to 2WARSAW (300790) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_360 | 3 Phase fault on 2KNOBBY 69.000 (300780) 69 kV Bus a. Apply fault at the 2KNOBBY 69.000 (300780) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KNOBBY (300780) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_361 | 3 Phase fault on 2WARSAW 69.000 (300790) 69 kV Bus a. Apply fault at the 2WARSAW 69.000 (300790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WARSAW (300790) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_362 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_363 | 3 Phase fault on 2DAMSCUS 69.000 (300804) 69 kV Bus a. Apply fault at the 2DAMSCUS 69.000 (300804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DAMSCUS (300804) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_364 | 3 Phase fault on 2ICONTP 69.000 (300809) 69 kV Bus a. Apply fault at the 2ICONTP 69.000 (300809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ICONTP (300809) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_365 | 3 Phase fault on 2OSCEOL 69.000 (300811) 69 kV Bus a. Apply fault at the 2OSCEOL 69.000 (300811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_366 | 3 Phase fault on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_367 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_368 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_369 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_370 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_371 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_372 | 3 Phase fault on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOKC (301522) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_373 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_374 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_375 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_376 | 3 Phase fault on BEAVER 5 161.00 (505480) 161 kV Bus a. Apply fault at the BEAVER 5 161.00 (505480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_377 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_378 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_379 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_380 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_381 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_382 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_383 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_384 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_385 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_386 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_387 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_388 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_389 | 3 Phase fault on NIXA 2 69.000 (505501) 69 kV Bus a. Apply fault at the NIXA 2 69.000 (505501) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_390 | 3 Phase fault on NIXA DT2 69.000 (505541) 69 kV Bus a. Apply fault at the NIXA DT2 69.000 (505541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA DT2 (505541) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_391 | 3 Phase fault on NIXA NE2 69.000 (505544) 69 kV Bus a. Apply fault at the NIXA NE2 69.000 (505544) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA NE2 (505544) 69.0 kV to JRPS 69B-2 2 (549903) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_392 | 3 Phase fault on DELWARE4 138.00 (510379) 138 kV Bus a. Apply fault at the DELWARE4 138.00 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_393 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_394 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_395 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_396 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_397 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_398 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_399 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_400 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_401 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_402 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_403 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_404 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_405 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_406 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_407 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_408 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_409 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_410 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_411 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_412 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_413 | 3 Phase fault on MOSCOW 2 69.000 (531384) 69 kV Bus a. Apply fault at the MOSCOW 2 69.000 (531384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOW 2 (531384) 69.0 kV to MOSCOWT2 (531385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_414 | 3 Phase fault on MOSCOWT2 69.000 (531385) 69 kV Bus a. Apply fault at the MOSCOWT2 69.000 (531385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOWT2 (531385) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_415 | 3 Phase fault on NORTH6 2 69.000 (531388) 69 kV Bus a. Apply fault at the NORTH6 2 69.000 (531388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6 2 (531388) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_416 | 3 Phase fault on NORTH6T2 69.000 (531389) 69 kV Bus a. Apply fault at the NORTH6T2 69.000 (531389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6T2 (531389) 69.0 kV to WALKMYR2 (531404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_417 | 3 Phase fault on ROLLA 2 115.00 (531395) 115 kV Bus a. Apply fault at the ROLLA 2 115.00 (531395) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLA 2 (531395) 115.0 kV to ABBK 2 (531494) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_418 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WOODS 2 (531406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_419 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_420 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_421 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_422 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_423 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_424 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_425 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_426 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_427 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_428 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_429 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_430 | 3 Phase fault on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_431 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_432 | 3 Phase fault on EUDORA 3 115.00 (533240) 115 kV Bus a. Apply fault at the EUDORA 3 115.00 (533240) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_433 | 3 Phase fault on ARKCTYW2 69.000 (533540) 69 kV Bus a. Apply fault at the ARKCTYW2 69.000 (533540) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to ARKCTYE2 (533542) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_434 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_435 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_436 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_437 | 3 Phase fault on FLORAL 2 69.000 (533545) 69 kV Bus a. Apply fault at the FLORAL 2 69.000 (533545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORAL 2 (533545) 69.0 kV to FLORALJ2 (533546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_438 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_439 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to TIMBER 2 (533557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_440 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_441 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_442 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_443 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_444 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_445 | 3 Phase fault on PRAIRIE2 69.000 (533562) 69 kV Bus a. Apply fault at the PRAIRIE2 69.000 (533562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAIRIE2 (533562) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_446 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to BURLIND2 (533625) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_447 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to CC1BURL2 (533628) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_448 | 3 Phase fault on NEOSHON2 69.000 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 69.000 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_449 | 3 Phase fault on EAST SUB 2 69.000 (533990) 69 kV Bus a. Apply fault at the EAST SUB 2 69.000 (533990) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_450 | 3 Phase fault on WEST SUB 2 69.000 (533991) 69 kV Bus a. Apply fault at the WEST SUB 2 69.000 (533991) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_451 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_452 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_453 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_454 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_455 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_456 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_457 | 3 Phase fault on CLNTPLT_CAP269.000 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP269.000 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_458 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_459 | 3 Phase fault on WSTELEC_CAP5161.00 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5161.00 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_460 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_461 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_462 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_463 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_464 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_465 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_466 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_467 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_468 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_469 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_470 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_471 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_472 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_473 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_474 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_475 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_476 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_477 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_478 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to GRDVWE 5 (541223) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_479 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_480 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_481 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_482 | 3 Phase fault on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_483 | 3 Phase fault on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_484 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_485 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_486 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_487 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_488 | 3 Phase fault on NRAYMORETP 5161.00 (541231) 161 kV Bus a. Apply fault at the NRAYMORETP 5161.00 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORETP 5 (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_489 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_490 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_491 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_492 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_493 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_494 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_495 | 3 Phase fault on LEX69 2 69.000 (541264) 69 kV Bus a. Apply fault at the LEX69 2 69.000 (541264) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX69 2 (541264) 69.0 kV to LEXNTON2 (541265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_496 | 3 Phase fault on 13&40 2 69.000 (541266) 69 kV Bus a. Apply fault at the 13&40 2 69.000 (541266) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to ODESSA 2 (541267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_497 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to KELHYS 2 (541273) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_498 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_499 | 3 Phase fault on SEDS 2 69.000 (541272) 69 kV Bus a. Apply fault at the SEDS 2 69.000 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_500 | 3 Phase fault on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_501 | 3 Phase fault on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_502 | 3 Phase fault on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_503 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_504 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_505 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_506 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to HSNVLN 2 (541297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_507 | 3 Phase fault on LNGVW 2 69.000 (541282) 69 kV Bus a. Apply fault at the LNGVW 2 69.000 (541282) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to BRMALL 2 (541283) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_508 | 3 Phase fault on HSNVL 2 69.000 (541295) 69 kV Bus a. Apply fault at the HSNVL 2 69.000 (541295) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVLSW2 (541296) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_509 | 3 Phase fault on HSNVLSW2 69.000 (541296) 69 kV Bus a. Apply fault at the HSNVLSW2 69.000 (541296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLSW2 (541296) 69.0 kV to HSNVLN 2 (541297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_510 | 3 Phase fault on HSNVLSW2 69.000 (541296) 69 kV Bus a. Apply fault at the HSNVLSW2 69.000 (541296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLSW2 (541296) 69.0 kV to GRDNCTY2 (541298) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_511 | 3 Phase fault on GRDNCTY2 69.000 (541298) 69 kV Bus a. Apply fault at the GRDNCTY2 69.000 (541298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY2 (541298) 69.0 kV to GUNNPS2 (541299) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_512 | 3 Phase fault on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_513 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBW5 (541336) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_514 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_515 | 3 Phase fault on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161.0 kV to WAFBE5 (541338) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_516 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_517 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_518 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_519 | 3 Phase fault on PECULR 5 161.00 (541342) 161 kV Bus a. Apply fault at the PECULR 5 161.00 (541342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECULR 5 (541342) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_520 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_521 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_522 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_523 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_524 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_525 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_526 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_527 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_528 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_529 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_530 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_531 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_532 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_533 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_534 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_535 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_536 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_537 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_538 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_539 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_540 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_541 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_542 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_543 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_544 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_545 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_546 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_547 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_548 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_549 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_550 | 3 Phase fault on PFLUMM 5 161.00 (542979) 161 kV Bus a. Apply fault at the PFLUMM 5 161.00 (542979) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_551 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_552 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_553 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_554 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_555 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_556 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_557 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_558 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_559 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_560 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_561 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_562 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_563 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_564 | 3 Phase fault on SWAVCAP5 161.00 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 161.00 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_565 | 3 Phase fault on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_566 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_567 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_568 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_569 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_570 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_571 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_572 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_573 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_574 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_575 | 3 Phase fault on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LENEXA 5 (543038) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_576 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_577 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_578 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to NEASTOTTW5 (543166) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_579 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_580 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_581 | 3 Phase fault on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_582 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_583 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_584 | 3 Phase fault on S.OTTWA5 161.00 (543066) 161 kV Bus a. Apply fault at the S.OTTWA5 161.00 (543066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.OTTWA5 (543066) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_585 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_586 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_587 | 3 Phase fault on S EAST 5 161.00 (543071) 161 kV Bus a. Apply fault at the S EAST 5 161.00 (543071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S EAST 5 (543071) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_588 | 3 Phase fault on MRSHLJT5 161.00 (543072) 161 kV Bus a. Apply fault at the MRSHLJT5 161.00 (543072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRSHLJT5 (543072) 161.0 kV to MIAMI_ 5 (543073) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_589 | 3 Phase fault on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSTVAL5 (543077) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_590 | 3 Phase fault on OSAWAT 5 161.00 (543112) 161 kV Bus a. Apply fault at the OSAWAT 5 161.00 (543112) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWAT 5 (543112) 161.0 kV to OSAWTM_CAP5 (543135) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_591 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON416J2 (547402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_592 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_593 | 3 Phase fault on MON376 2 69.000 (547401) 69 kV Bus a. Apply fault at the MON376 2 69.000 (547401) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376 2 (547401) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_594 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON352 2 (547406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_595 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_596 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_597 | 3 Phase fault on MON311J2 69.000 (547407) 69 kV Bus a. Apply fault at the MON311J2 69.000 (547407) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON311J2 (547407) 69.0 kV to MON311 2 (547408) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_598 | 3 Phase fault on SCAM66 2 69.000 (547409) 69 kV Bus a. Apply fault at the SCAM66 2 69.000 (547409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCAM66 2 (547409) 69.0 kV to SCM66T 2 (547455) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_599 | 3 Phase fault on COL282 2 69.000 (547411) 69 kV Bus a. Apply fault at the COL282 2 69.000 (547411) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL282 2 (547411) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_600 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_601 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_602 | 3 Phase fault on WEB105 2 69.000 (547431) 69 kV Bus a. Apply fault at the WEB105 2 69.000 (547431) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB105 2 (547431) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_603 | 3 Phase fault on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUPTAP 2 (547436) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_604 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to EXP4492 (547439) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_605 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_606 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_607 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_608 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_609 | 3 Phase fault on JAS344T2 69.000 (547450) 69 kV Bus a. Apply fault at the JAS344T2 69.000 (547450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAS344T2 (547450) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_610 | 3 Phase fault on SCM66T 2 69.000 (547455) 69 kV Bus a. Apply fault at the SCM66T 2 69.000 (547455) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCM66T 2 (547455) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_611 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_612 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_613 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_614 | 3 Phase fault on KOD471 2 69.000 (547463) 69 kV Bus a. Apply fault at the KOD471 2 69.000 (547463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOD471 2 (547463) 69.0 kV to DIA131 2 (547538) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_615 | 3 Phase fault on KOD471 2 69.000 (547463) 69 kV Bus a. Apply fault at the KOD471 2 69.000 (547463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOD471 2 (547463) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_616 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_617 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_618 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_619 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_620 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_621 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_622 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_623 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_624 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_625 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_626 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_627 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_628 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_629 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_630 | 3 Phase fault on ASB349 5 161.00 (547476) 161 kV Bus a. Apply fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_631 | 3 Phase fault on ASB349 5 161.00 (547476) 161 kV Bus a. Apply fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_632 | 3 Phase fault on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_633 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_634 | 3 Phase fault on LAR382 5 161.00 (547479) 161 kV Bus a. Apply fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_635 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_636 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_637 | 3 Phase fault on DEC392 5 161.00 (547484) 161 kV Bus a. Apply fault at the DEC392 5 161.00 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 (547484) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_638 | 3 Phase fault on CAR395 5 161.00 (547485) 161 kV Bus a. Apply fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_639 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_640 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_641 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_642 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_643 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_644 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_645 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_646 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_647 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to ORO110 2 (547534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_648 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_649 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_650 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_651 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_652 | 3 Phase fault on CAR108 2 69.000 (547532) 69 kV Bus a. Apply fault at the CAR108 2 69.000 (547532) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAR108 2 (547532) 69.0 kV to ATL109 2 (547533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_653 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_654 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to JOP360 2 (547581) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_655 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_656 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_657 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_658 | 3 Phase fault on NIX114 2 69.000 (547535) 69 kV Bus a. Apply fault at the NIX114 2 69.000 (547535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIX114 2 (547535) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_659 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_660 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MON152 2 (547540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_661 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_662 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_663 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_664 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_665 | 3 Phase fault on MON152 2 69.000 (547540) 69 kV Bus a. Apply fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_666 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_667 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_668 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to REP345 2 (547576) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_669 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_670 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_671 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to ROC296 2 (547560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_672 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to LIN314 2 (547563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_673 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to AND322 2 (547566) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_674 | 3 Phase fault on FRP217 2 69.000 (547545) 69 kV Bus a. Apply fault at the FRP217 2 69.000 (547545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRP217 2 (547545) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_675 | 3 Phase fault on GAT258 2 69.000 (547551) 69 kV Bus a. Apply fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_676 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_677 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_678 | 3 Phase fault on GAL278 2 69.000 (547555) 69 kV Bus a. Apply fault at the GAL278 2 69.000 (547555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAL278 2 (547555) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_679 | 3 Phase fault on TIP292 2 69.000 (547559) 69 kV Bus a. Apply fault at the TIP292 2 69.000 (547559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 2 (547559) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_680 | 3 Phase fault on COM381T2 69.000 (547579) 69 kV Bus a. Apply fault at the COM381T2 69.000 (547579) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COM381T2 (547579) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_681 | 3 Phase fault on JOP360 2 69.000 (547581) 69 kV Bus a. Apply fault at the JOP360 2 69.000 (547581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP360 2 (547581) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_682 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_683 | 3 Phase fault on JOP389 2 69.000 (547592) 69 kV Bus a. Apply fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_684 | 3 Phase fault on RNM393 2 69.000 (547595) 69 kV Bus a. Apply fault at the RNM393 2 69.000 (547595) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 2 (547595) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_685 | 3 Phase fault on GLF339 2 69.000 (547690) 69 kV Bus a. Apply fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_686 | 3 Phase fault on JRPS 69B-2 269.000 (549903) 69 kV Bus a. Apply fault at the JRPS 69B-2 269.000 (549903) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JRPS 69B-2 2 (549903) 69.0 kV to PLAINVIEW 2 (549905) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_687 | 3 Phase fault on JRPS 69B-2 269.000 (549903) 69 kV Bus a. Apply fault at the JRPS 69B-2 269.000 (549903) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JRPS 69B-2 2 (549903) 69.0 kV to TWIN OAKS 2 (549933) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_688 | 3 Phase fault on JRPS 69B-2 269.000 (549903) 69 kV Bus a. Apply fault at the JRPS 69B-2 269.000 (549903) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JRPS 69B-2 2 (549903) 69.0 kV to SEMINOLE 2 (549934) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_689 | 3 Phase fault on JAMES RIVER269.000 (549904) 69 kV Bus a. Apply fault at the JAMES RIVER269.000 (549904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER2 (549904) 69.0 kV to S HWY 65 2 (549908) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_690 | 3 Phase fault on JAMES RIVER269.000 (549904) 69 kV Bus a. Apply fault at the JAMES RIVER269.000 (549904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER2 (549904) 69.0 kV to HIGHWAY M 2 (549909) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_691 | 3 Phase fault on KICKAPOO 269.000 (549906) 69 kV Bus a. Apply fault at the KICKAPOO 269.000 (549906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KICKAPOO 2 (549906) 69.0 kV to SUNSET 2 (549907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_692 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to S HWY 65 2 (549908) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_693 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to FORT 2 (549914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_694 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to MONROE 2 (549923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_695 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to SEMINOLE 2 (549934) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_696 | 3 Phase fault on COX 269.000 (549910) 69 kV Bus a. Apply fault at the COX 269.000 (549910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_697 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to LAUREL 2 (549924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_698 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_699 | 3 Phase fault on DAYTON 269.000 (549913) 69 kV Bus a. Apply fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_700 | 3 Phase fault on MILL 269.000 (549918) 69 kV Bus a. Apply fault at the MILL 269.000 (549918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 2 (549918) 69.0 kV to CHAD 2 (549919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_701 | 3 Phase fault on CHAD 269.000 (549919) 69 kV Bus a. Apply fault at the CHAD 269.000 (549919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAD 2 (549919) 69.0 kV to HARGISS 2 (549920) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_702 | 3 Phase fault on HARGISS 269.000 (549920) 69 kV Bus a. Apply fault at the HARGISS 269.000 (549920) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARGISS 2 (549920) 69.0 kV to MAIN STREET2 (549921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_703 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to GRAND 2 (549922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_704 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_705 | 3 Phase fault on GRAND 269.000 (549922) 69 kV Bus a. Apply fault at the GRAND 269.000 (549922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 2 (549922) 69.0 kV to MONROE 2 (549923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_706 | 3 Phase fault on LAUREL 269.000 (549924) 69 kV Bus a. Apply fault at the LAUREL 269.000 (549924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAUREL 2 (549924) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_707 | 3 Phase fault on NICHOLS 269.000 (549925) 69 kV Bus a. Apply fault at the NICHOLS 269.000 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 2 (549925) 69.0 kV to FRISCO 2 (549926) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_708 | 3 Phase fault on FRISCO 269.000 (549926) 69 kV Bus a. Apply fault at the FRISCO 269.000 (549926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRISCO 2 (549926) 69.0 kV to N HWY13 2 (549927) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_709 | 3 Phase fault on N HWY13 269.000 (549927) 69 kV Bus a. Apply fault at the N HWY13 269.000 (549927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HWY13 2 (549927) 69.0 kV to NORTON 2 (549928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_710 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_711 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to NEERGARD 2 (549930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_712 | 3 Phase fault on NEERGARD 269.000 (549930) 69 kV Bus a. Apply fault at the NEERGARD 269.000 (549930) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEERGARD 2 (549930) 69.0 kV to LECOMPTE 2 (549931) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_713 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_714 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_715 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_716 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_717 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_718 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_719 | 3 Phase fault on MENTOR 5161.00 (549963) 161 kV Bus a. Apply fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_720 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_721 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_722 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_723 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 7HUBEN (300042) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_724 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_725 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF3 (301506) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_726 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF4 (301510) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_727 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_728 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_729 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_730 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_731 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_732 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHRP (300302) 69.0 kV to 5LATHRP (300091) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_733 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MORGAN (300782) 69.0 kV to 5MORGAN (300101) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_734 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NORTON (300540) 69.0 kV to 5NORTON (300105) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_735 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_736 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_737 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 5THMHILB1 (300120) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_738 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HOLDEN (300336) 69.0 kV to 5HOLDENB2 (300124) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_739 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_740 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_741 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_742 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_743 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_744 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to NEO184 5 (547471) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_745 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WASHBRN (300763) 69.0 kV to WASHBURN5 (505485) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_746 | 3 Phase fault on 5OSCEOL 161.00 (301040) 161 kV Bus a. Apply fault at the 5OSCEOL 161.00 (301040) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 5OSCEOL (301040) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_747 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_748 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TURKEYCRK (301401) 69.0 kV to 5TURKEYCRK (301370) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_749 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_750 | 3 Phase fault on 5LATHROP 161.00 (344923) 161 kV Bus a. Apply fault at the 5LATHROP 161.00 (344923) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHROP (346093) 69.0 kV to 5LATHROP (344923) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_751 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_752 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_753 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_754 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_755 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_756 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_757 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_758 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_759 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_760 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_761 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_762 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_763 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_764 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_765 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_766 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_767 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY2 (512741) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_768 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR41 (523098) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_769 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR11 (523092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_770 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_771 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_772 | 3 Phase fault on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_773 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to G06-44 (560577) 115.0 kV to NOVUS1_TR2 2 (560578) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_774 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_775 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_776 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_777 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_778 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 2 1 (525538) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_779 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to HUGOTON3 (531481) 115.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_780 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_781 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_782 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_783 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_784 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_785 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_786 | 3 Phase fault on SEWARD-3 115.00 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 115.00 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMSSWRD2 (531466) 69.0 kV to SEWARD-3 (531467) 115.0 kV to SEWARD 1 (531260) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_787 | 3 Phase fault on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_788 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_789 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_790 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_791 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_792 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_793 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_794 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_795 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_796 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_797 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_798 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_799 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_800 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_801 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_802 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_803 | 3 Phase fault on EDWRDVL5 161.00 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 161.00 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to EDWARVL3 (533238) 115.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_804 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_805 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_806 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_807 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_808 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_809 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_810 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_811 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_812 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_813 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_814 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_815 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_816 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_817 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_818 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_819 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to LNGVW 5 (541224) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_820 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_821 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_822 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_823 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_824 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_825 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN S2 (541320) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_826 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to LBRTYST5 (541248) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_827 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_828 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_829 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS2 (541290) 69.0 kV to BELTONS5 (541340) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_830 | 3 Phase fault on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_831 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_832 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_833 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_834 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_835 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_836 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_837 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_838 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_839 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_840 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_841 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH 12 (400) 13.8 kV Three Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_842 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_843 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_844 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_845 | 3 Phase fault on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to SWAVRLY5 (543063) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_846 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_847 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_848 | 3 Phase fault on ATL109 5 161.00 (547466) 161 kV Bus a. Apply fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_849 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_850 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_851 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_852 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_853 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 (547471) 161.0 kV to NEO184 2 (547543) 69.0 kV to NEO184B1 (547709) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_854 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_855 | 3 Phase fault on MON383 5 161.00 (547480) 161 kV Bus a. Apply fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_856 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_857 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_858 | 3 Phase fault on NOL435 5 161.00 (547496) 161 kV Bus a. Apply fault at the NOL435 5 161.00 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 5 (547496) 161.0 kV to NOL435 2 (547610) 69.0 kV to NOL435 1 (547720) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_859 | 3 Phase fault on CPK446 5 161.00 (547499) 161 kV Bus a. Apply fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_860 | 3 Phase fault on RNM393 5 161.00 (547500) 161 kV Bus a. Apply fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_861 | 3 Phase fault on SUB N-161 161.00 (548820) 161 kV Bus a. Apply fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_862 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_863 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_864 | 3 Phase fault on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_865 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to JAMES RIVER2 (549904) 69.0 kV to JRPS XF1 1 (549944) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_866 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to JRPS 69B-2 2 (549903) 69.0 kV to JRPS XF2 1 (549945) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_867 | 3 Phase fault on NORTON 5161.00 (549967) 161 kV Bus a. Apply fault at the NORTON 5161.00 (549967) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (549967) 161.0 kV to NORTON 2 (549928) 69.0 kV to NORTON XF1 1 (549942) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_868 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_869 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_870 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_871 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_872 | 3 Phase fault on 2WARSAW 69.000 (300790) 69 kV Bus a. Apply fault at the 2WARSAW 69.000 (300790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WARSAW (300790) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_873 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_874 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_875 | 3 Phase fault on MON383 2 69.000 (547591) 69 kV Bus a. Apply fault at the MON383 2 69.000 (547591) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 2 (547591) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_876 | 3 Phase fault on JOP430 2 69.000 (547608) 69 kV Bus a. Apply fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP430 2 (547608) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_877 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_878 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_879 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_880 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_001 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_002 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_003 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_004 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_005 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_006 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_007 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_008 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_009 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_010 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_011 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. The issue is also observed in the PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_013 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_014 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_015 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_016 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_017 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_018 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_019 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_020 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_021 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_022 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_023 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_024 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_025 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_026 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_027 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_028 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_029 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_030 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_031 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_032 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_033 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_036 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_037 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_038 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_039 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_040 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_041 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_042 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_043 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_044 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_045 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_046 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_048 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_049 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_051 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 b.3. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply Fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 b.2. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 b.3. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 b.4. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply Fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.3. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.4. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on KCSOUTH5 161.00 (541245) 161 kV Bus a. Apply Fault at the KCSOUTH5 161.00 (541245) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 b.2. NRAYMORETP 5 (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on STROTHR2 69.000 (533556) 69 kV Bus a. Apply Fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.2. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.3. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.4. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.5. EAST SUB 2 (533990) 69.0 kV to GEN-2020-003 (765085) 69.0 kV Transmission Circuit #1 b.6. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on OAK 2 69.000 (533547) 69 kV Bus a. Apply Fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.3. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.4. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.5. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.3. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on NORTON 5 161.00 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply Fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.4. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to ATLNTIC7 (542940) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to ATLNTIC7 (542940) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on PIONEER3 115.00 (531391) 115 kV Bus a. Apply Fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. HICKOCK3 (531378) 115.0 kV to PIONEER3 (531391) 115.0 kV Transmission Circuit #1 b.3. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.4. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.5. PIONEER3 (531391) 115.0 kV to ULYSPLT3 (531490) 115.0 kV Transmission Circuit #1 b.6. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 b.7. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.8. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 b.9. PIONEER3 (531391) 115.0 kV to PIONEER2 (531390) 69.0 kV to PIONEER1 (531251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply Fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to Trip Bus # b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.5. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.6. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.7. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.8. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.9. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 b.10. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.11. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.12. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.13. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.14. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WALDO 3 115.00 (539698) 115 kV Bus a. Apply Fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.3. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.4. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.5. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.6. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.7. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.8. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.9. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.10. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 b.11. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 b.12. SMITH-C3 (539693) 115.0 kV to SMITH-C1 (539731) 34.5 kV to SMITHC-T (539934) 7.2 kV Three Winding #1 b.13. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply Fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWNDTAP3 (531476) 115.0 kV to Trip Bus # b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. GRDNCTY3 (531445) 115.0 kV to S2 GEN 1 (531459) 13.8 kV Two Winding #1 b.4. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.5. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.6. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.3. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 b.4. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on JONES3 115.00 (531379) 115 kV Bus a. Apply Fault at the JONES3 115.00 (531379) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.3. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CIM-PLT3 (539654) 115.0 kV to CIM-PLT (539780) 13.8 kV Two Winding #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply Fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. GRDNCTY3 (531445) 115.0 kV to S2 GEN 1 (531459) 13.8 kV Two Winding #1 b.4. GRDNCTY3 (531445) 115.0 kV to S4 GEN 1 (531461) 13.2 kV Two Winding #1 b.5. GRDNCTY3 (531445) 115.0 kV to S5 GEN 1 (531462) 13.2 kV Two Winding #1 b.6. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.7. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.8. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.9. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.10. GRDNCTY3 (531445) 115.0 kV to GC-C 1 (531421) 34.5 kV to GC-CITY (531254) 13.8 kV Three Winding #1 b.11. GRDNCTY3 (531445) 115.0 kV to GARDNCY2 (531423) 69.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.4. SPF X3 1 (505495) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 b.4. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on AVOCA 5 161.00 (504000) 161 kV Bus a. Apply Fault at the AVOCA 5 161.00 (504000) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVOCA 5 (504000) 161.0 kV to BEAVER 5 (505480) 161.0 kV Transmission Circuit #1 b.2. AVOCA 5 (504000) 161.0 kV to EROGERS5 (506931) 161.0 kV Transmission Circuit #1 b.3. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 b.4. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on BEAVER 5 161.00 (505480) 161 kV Bus a. Apply Fault at the BEAVER 5 161.00 (505480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 b.2. BEAVER 5 (505480) 161.0 kV to EUREKA 5 (506932) 161.0 kV Transmission Circuit #1 b.3. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on STOCKTN5 161.00 (505498) 161 kV Bus a. Apply Fault at the STOCKTN5 161.00 (505498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 b.2. STOCKTN5 (505498) 161.0 kV to STK #1 1 (505500) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on TABLE R5 161.00 (505472) 161 kV Bus a. Apply Fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5RENOHLWTP (300130) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 b.2. 5RENOHLWTP (300130) 161.0 kV to 5RIVERSIDE (300805) 161.0 kV Transmission Circuit #1 b.3. 5RENOHLWTP (300130) 161.0 kV to 5RENOHLW (301129) 161.0 kV Transmission Circuit #1 b.4. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.5. 5COMPTN (300719) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 b.6. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.7. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.8. TABLE R5 (505472) 161.0 kV to TBR1&2 1 (505476) 13.8 kV Two Winding #1 b.9. TABLE R5 (505472) 161.0 kV to TBR3&4 1 (505478) 13.8 kV Two Winding #1 b.10. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.11. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.12. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.13. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on TABLE R5 161.00 (505472) 161 kV Bus a. Apply Fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.3. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.4. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.5. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.6. TABLE R5 (505472) 161.0 kV to TBR1&2 1 (505476) 13.8 kV Two Winding #1 b.7. TABLE R5 (505472) 161.0 kV to TBR3&4 1 (505478) 13.8 kV Two Winding #1 b.8. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.9. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.10. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.11. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply Fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2WASHBRN (300763) 69.0 kV to WASHBURN5 (505485) 161.0 kV Two Winding #1 b.2. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 b.3. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 b.4. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.5. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 b.6. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.2. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.3. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.5. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.6. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.7. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.8. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 b.2. 2JASPER (300649) 69.0 kV to 2MEDOC (300653) 69.0 kV Transmission Circuit #1 b.3. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.4. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.6. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.7. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.2. 2BOWRML (300659) 69.0 kV to 2REEDS (300751) 69.0 kV Transmission Circuit #1 b.3. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.4. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.6. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.2. 2DMNDGR (300744) 69.0 kV to 2DMNDTP (300745) 69.0 kV Transmission Circuit #1 b.3. 2DMNDTP (300745) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 b.4. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. 2NEOSHO (300750) 69.0 kV to 2SPGCTP (300754) 69.0 kV Transmission Circuit #1 b.6. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.7. 2SPGCTP (300754) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 b.8. 2SPGCTP (300754) 69.0 kV to 2SPURGNTP (300764) 69.0 kV Transmission Circuit #1 b.9. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.10. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 b.2. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.5. SPF X1 1 (505491) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ASHGRV (300657) 69.0 kV to 2CAVESP (300664) 69.0 kV Transmission Circuit #1 b.2. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 b.3. 2ASHGRV (300657) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 b.4. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 b.5. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 b.6. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #2 b.7. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply Fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.4. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.5. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 b.7. TRUMAN 5 (505502) 161.0 kV to TRU123 1 (505504) 13.8 kV Two Winding #1 b.8. TRUMAN 5 (505502) 161.0 kV to TRU456 1 (505506) 13.8 kV Two Winding #1 b.9. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.5. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.6. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.7. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. NXA X1 1 (505497) 13.8 kV to NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. NXA X2 1 (505499) 13.8 kV to NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on SPRINGH3 115.00 (533267) 115 kV Bus a. Apply Fault at the SPRINGH3 115.00 (533267) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.4. SPRINGH3 (533267) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply Fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on JTEC 5161.00 (549954) 161 kV Bus a. Apply Fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 b.2. JTEC GEN#1 1 (549890) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.3. JTEC CTS 1 (549891) 12.5 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.4. JTEC GEN#2 1 (549893) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.5. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.6. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.7. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply Fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 b.4. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.4. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply Fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JRPS GT1 1 (549900) 13.8 kV to JAMES RIVER5 (549961) 161.0 kV Two Winding #1 b.2. JRPS GT2 1 (549901) 13.8 kV to JAMES RIVER5 (549961) 161.0 kV Two Winding #1 b.3. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.4. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 b.5. JAMES RIVER5 (549961) 161.0 kV to JRPS 69B-2 2 (549903) 69.0 kV to JRPS XF2 1 (549945) 13.2 kV Three Winding #1 b.6. JAMES RIVER5 (549961) 161.0 kV to JAMES RIVER2 (549904) 69.0 kV to JRPS XF1 1 (549944) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on MILL 5161.00 (549962) 161 kV Bus a. Apply Fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.3. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.4. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on MENTOR 5161.00 (549963) 161 kV Bus a. Apply Fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 b.2. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.3. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on NORTON 5161.00 (549967) 161 kV Bus a. Apply Fault at the NORTON 5161.00 (549967) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 b.2. NORTON 5 (549967) 161.0 kV to NORTON 2 (549928) 69.0 kV to NORTON XF1 1 (549942) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on MC CARTNEY 5161.00 (549968) 161 kV Bus a. Apply Fault at the MC CARTNEY 5161.00 (549968) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCCARTNEY (301568) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #z1 b.2. MAC GT1&2 1 (549892) 13.8 kV to MC CARTNEY 5 (549968) 161.0 kV Two Winding #1 b.3. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.4. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.5. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.6. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on CLAY 5161.00 (549970) 161 kV Bus a. Apply Fault at the CLAY 5161.00 (549970) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.3. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.4. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on PIC WEST 5161.00 (549971) 161 kV Bus a. Apply Fault at the PIC WEST 5161.00 (549971) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit # b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on AFTON 5 161.00 (512632) 161 kV Bus a. Apply Fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.4. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 b.2. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 b.4. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.5. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.6. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 b.7. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 b.8. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 b.2. G20-072-TAP (764355) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 b.4. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 b.5. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.7. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 b.8. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 b.9. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON (345409) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.3. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply Fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.5. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply Fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 b.2. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z b.3. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.4. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 b.5. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply Fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.2. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.3. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.4. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.5. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.3. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.4. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on RIV167 5 161.00 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on NEO184 5 161.00 (547471) 161 kV Bus a. Apply Fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2NEOSAC (300748) 69.0 kV to NEO184 5 (547471) 161.0 kV Two Winding #1 b.2. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 b.3. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.4. NEO184 5 (547471) 161.0 kV to NEO184 2 (547543) 69.0 kV to NEO184B1 (547709) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.4. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply Fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.4. DAD368 5 (547478) 161.0 kV to GEN-2019-016 (763560) 161.0 kV Transmission Circuit #1 b.5. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.4. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on FIR417 5 161.00 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 161.00 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on OAK432 5 161.00 (547494) 161 kV Bus a. Apply Fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on NOL435 5 161.00 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 161.00 (547496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROVE 5 (510411) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.2. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.3. DEC392 5 (547484) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.4. NOL435 5 (547496) 161.0 kV to NOL435 2 (547610) 69.0 kV to NOL435 1 (547720) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on CPK446 5 161.00 (547499) 161 kV Bus a. Apply Fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.3. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply Fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.4. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.5. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.6. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-079-TAP (764310) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit # b.2. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-079-TAP (764310) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit # b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to A2G349 1 (547650) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 b.2. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.4. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.5. DAD368 5 (547478) 161.0 kV to GEN-2019-016 (763560) 161.0 kV Transmission Circuit #1 b.6. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 b.4. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on JOP422 5 161.00 (547607) 161 kV Bus a. Apply Fault at the JOP422 5 161.00 (547607) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to L3G3821 (547653) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to L2G382 1 (547652) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to L1G382 1 (547651) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.6. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.7. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 b.8. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 b.9. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.6. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 b.7. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply Fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.2. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 b.3. 5MAURER 2 (344558) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.3. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.4. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.5. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.6. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.7. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.8. EAST SUB 2 (533990) 69.0 kV to GEN-2020-003 (765085) 69.0 kV Transmission Circuit #1 b.9. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply Fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on NESCTY 3 115.00 (530607) 115 kV Bus a. Apply Fault at the NESCTY 3 115.00 (530607) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NESCTY 3 (530607) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NESCTY 3 (530607) 115.0 kV to NESS-CT1 (539722) 34.5 kV to NES-CT-T (539924) 13.8 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.9. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.10. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 b.2. HITCHLD_TR11 (523092) 13.2 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV Three Winding #1 b.3. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply Fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.3. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.4. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.5. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.6. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.7. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.8. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.9. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.10. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.11. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.12. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.13. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.14. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPNSPUR_COL1 (524298) 34.5 kV to SPNSPUR_TR11 (524297) 13.2 kV to SPNSPUR_COL7 (524299) 345.0 kV Three Winding #1 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #1 b.4. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 b.5. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.7. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.8. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on WEST SUB 2 69.000 (533991) 69 kV Bus a. Apply Fault at the WEST SUB 2 69.000 (533991) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEST SUB 2 (533991) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 b.2. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply Fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LATHRP (300091) 161.0 kV to 2LATHRP (300302) 69.0 kV Two Winding #1 b.2. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply Fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.2. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply Fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on 2VERONA 69.000 (300680) 69 kV Bus a. Apply Fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2VERONA (300680) 69.0 kV to 2PRDYTP (300679) 69.0 kV Transmission Circuit #1 b.2. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply Fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 b.2. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply Fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply Fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SHARSNV (301515) 161.0 kV to 2SHARSNV (300709) 69.0 kV Two Winding #1 b.2. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on GEN-2011-022345.00 (523215) 345 kV Bus a. Apply Fault at the GEN-2011-022345.00 (523215) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2011-022 (523215) 345.0 kV to G11-022XFMR1 (523211) 34.5 kV Two Winding #1 b.2. GEN-2011-022 (523215) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply Fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply Fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.2. NEOSHOS4 (533020) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on ARKCTYE2 69.000 (533542) 69 kV Bus a. Apply Fault at the ARKCTYE2 69.000 (533542) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARKCTYE2 (533542) 69.0 kV to ARKCTYW2 (533540) 69.0 kV Transmission Circuit #z1 b.2. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on PARIS 2 69.000 (533548) 69 kV Bus a. Apply Fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARIS 2 (533548) 69.0 kV to ARKCTYW2 (533540) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply Fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.2. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply Fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SC5SILV2 (533554) 69.0 kV to ARKCTYE2 (533542) 69.0 kV Transmission Circuit #1 b.2. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on BURLJCT2 69.000 (533626) 69 kV Bus a. Apply Fault at the BURLJCT2 69.000 (533626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on CC2SHAR2 69.000 (533629) 69 kV Bus a. Apply Fault at the CC2SHAR2 69.000 (533629) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC2SHAR2 (533629) 69.0 kV to CC5SHAR1 (533888) 12.5 kV Two Winding #1 b.2. CC2SHAR2 (533629) 69.0 kV to CC6SHAR1 (533889) 12.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply Fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROLLHLS3 (539643) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on CIM-PLT3 115.00 (539654) 115 kV Bus a. Apply Fault at the CIM-PLT3 115.00 (539654) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIM-PLT3 (539654) 115.0 kV to WALKMYR3 (531405) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to HAYNE3 (539640) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply Fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDSR 5 (541217) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply Fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WSTELEC5 (541222) 161.0 kV to WSTELEC_CAP5 (541149) 161.0 kV Transmission Circuit #r b.2. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply Fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDVWE 5 (541223) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 b.2. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply Fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LKWINBG5 (541243) 161.0 kV to PHILL 5 (541225) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on LEXNTON2 69.000 (541265) 69 kV Bus a. Apply Fault at the LEXNTON2 69.000 (541265) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEXNTON2 (541265) 69.0 kV to LEX69 2 (541264) 69.0 kV Transmission Circuit #1 b.2. LEXNTON2 (541265) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on 13&40 2 69.000 (541266) 69 kV Bus a. Apply Fault at the 13&40 2 69.000 (541266) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 13&40 2 (541266) 69.0 kV to ODESSA 2 (541267) 69.0 kV Transmission Circuit #1 b.2. 13&40 2 (541266) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on PHILL 5 161.00 (541225) 161 kV Bus a. Apply Fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 b.2. PHILL 2 (541280) 69.0 kV to RGREEN 2 (541279) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply Fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on ANCONDA2 69.000 (541292) 69 kV Bus a. Apply Fault at the ANCONDA2 69.000 (541292) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANCONDA2 (541292) 69.0 kV to FREEMAN2 (541291) 69.0 kV Transmission Circuit #1 b.2. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on HSNVLW 2 69.000 (541293) 69 kV Bus a. Apply Fault at the HSNVLW 2 69.000 (541293) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVLW 2 (541293) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on HSNVLS 2 69.000 (541294) 69 kV Bus a. Apply Fault at the HSNVLS 2 69.000 (541294) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVLS 2 (541294) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.2. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply Fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 b.2. HSNVL 2 (541295) 69.0 kV to HSNVLSW2 (541296) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply Fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTOAK2 (541300) 69.0 kV to WBURGP 2 (541268) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply Fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on BELTONS5 161.00 (541340) 161 kV Bus a. Apply Fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELTONS5 (541340) 161.0 kV to TURNER_RD5 (541259) 161.0 kV Transmission Circuit #1 b.2. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to PECULR 7 (541198) 345.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 5 (541342) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on RAYMORE 69.000 (541347) 69 kV Bus a. Apply Fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAYMORE (541347) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 b.2. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on KNGSVIL 2 69.000 (541387) 69 kV Bus a. Apply Fault at the KNGSVIL 2 69.000 (541387) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNGSVIL 2 (541387) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.2. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply Fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply Fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 b.2. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply Fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply Fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCYRUS5 (543057) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on MALTABN5 161.00 (543059) 161 kV Bus a. Apply Fault at the MALTABN5 161.00 (543059) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 b.2. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALSBRY5 (543062) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on PAOLA 5 161.00 (543069) 161 kV Bus a. Apply Fault at the PAOLA 5 161.00 (543069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAOLA 5 (543069) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 b.2. PAOLA 5 (543069) 161.0 kV to CENTENL5 (543067) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply Fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWAVRLY2 (543094) 69.0 kV to SWAVRLY5 (543063) 161.0 kV Two Winding #1 b.2. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on MAYVWTP2 69.000 (543096) 69 kV Bus a. Apply Fault at the MAYVWTP2 69.000 (543096) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAYVWTP2 (543096) 69.0 kV to LEXNTON2 (541265) 69.0 kV Transmission Circuit #1 b.2. MAYVWTP2 (543096) 69.0 kV to 13&40 2 (541266) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on HIGNSVL2 69.000 (543099) 69 kV Bus a. Apply Fault at the HIGNSVL2 69.000 (543099) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGNSVL2 (543099) 69.0 kV to CTY HIG2 (543098) 69.0 kV Transmission Circuit #1 b.2. HIGNSVL2 (543099) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on AMOCOPL2 69.000 (543100) 69 kV Bus a. Apply Fault at the AMOCOPL2 69.000 (543100) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AMOCOPL2 (543100) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.2. AMOCOPL2 (543100) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on CORDERTP2 69.000 (543657) 69 kV Bus a. Apply Fault at the CORDERTP2 69.000 (543657) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORDERTP2 (543657) 69.0 kV to CTY HIG2 (543098) 69.0 kV Transmission Circuit #1 b.2. CORDERTP2 (543657) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on EXP449T2 69.000 (547438) 69 kV Bus a. Apply Fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXP449T2 (547438) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 b.2. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on PRC460 2 69.000 (547449) 69 kV Bus a. Apply Fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 b.2. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on WEB436 2 69.000 (547527) 69 kV Bus a. Apply Fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEB436 2 (547527) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 b.2. WEB436 2 (547527) 69.0 kV to ORO110 2 (547534) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on COL 94 2 69.000 (547530) 69 kV Bus a. Apply Fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on NIX114 2 69.000 (547535) 69 kV Bus a. Apply Fault at the NIX114 2 69.000 (547535) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NIX114 2 (547535) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 b.2. NIX114 2 (547535) 69.0 kV to BHJ415 2 (547604) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on AUR124 2 69.000 (547537) 69 kV Bus a. Apply Fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 b.2. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on MON152 2 69.000 (547540) 69 kV Bus a. Apply Fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON152 2 (547540) 69.0 kV to AUR124 2 (547537) 69.0 kV Transmission Circuit #1 b.2. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on GAT258 2 69.000 (547551) 69 kV Bus a. Apply Fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GAT258 2 (547551) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 b.2. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on BAX271 2 69.000 (547554) 69 kV Bus a. Apply Fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAX271 2 (547554) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 b.2. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on TIP292 2 69.000 (547559) 69 kV Bus a. Apply Fault at the TIP292 2 69.000 (547559) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 2 (547559) 69.0 kV to NEO332 2 (547571) 69.0 kV Transmission Circuit #1 b.2. TIP292 2 (547559) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on JOP360 2 69.000 (547581) 69 kV Bus a. Apply Fault at the JOP360 2 69.000 (547581) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP360 2 (547581) 69.0 kV to ATL109 2 (547533) 69.0 kV Transmission Circuit #1 b.2. JOP360 2 (547581) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on JOP389 2 69.000 (547592) 69 kV Bus a. Apply Fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 2 (547592) 69.0 kV to EXP449T2 (547438) 69.0 kV Transmission Circuit #1 b.2. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNM393 2 (547595) 69.0 kV to KOD471 2 (547463) 69.0 kV Transmission Circuit #1 b.2. RNM393 2 (547595) 69.0 kV to RNM393 5 (547500) 161.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on COX 269.000 (549910) 69 kV Bus a. Apply Fault at the COX 269.000 (549910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COX 2 (549910) 69.0 kV to PLAINVIEW 2 (549905) 69.0 kV Transmission Circuit #1 b.2. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on DAYTON 269.000 (549913) 69 kV Bus a. Apply Fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAYTON 2 (549913) 69.0 kV to FORT 2 (549914) 69.0 kV Transmission Circuit #1 b.2. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on LAUREL 269.000 (549924) 69 kV Bus a. Apply Fault at the LAUREL 269.000 (549924) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAUREL 2 (549924) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 b.2. LAUREL 2 (549924) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 2 (549925) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 b.2. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on FRISCO 269.000 (549926) 69 kV Bus a. Apply Fault at the FRISCO 269.000 (549926) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRISCO 2 (549926) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 b.2. FRISCO 2 (549926) 69.0 kV to N HWY13 2 (549927) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on GEN-2010-014345.00 (576395) 345 kV Bus a. Apply Fault at the GEN-2010-014345.00 (576395) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2010-014 (576395) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 b.2. GEN-2010-014 (576395) 345.0 kV to G10-014XFMR2 (576398) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on GEN-2017-108161.00 (761271) 161 kV Bus a. Apply Fault at the GEN-2017-108161.00 (761271) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-108 (761271) 161.0 kV to G17-108-XFM1 (761272) 34.5 kV Two Winding #1 b.2. GEN-2017-108 (761271) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on GEN-2017-195345.00 (762279) 345 kV Bus a. Apply Fault at the GEN-2017-195345.00 (762279) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-195 (762279) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-195 (762279) 345.0 kV to G17-195XFM1 (762280) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on GEN-2020-007345.00 (766260) 345 kV Bus a. Apply Fault at the GEN-2020-007345.00 (766260) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-007 (766260) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-007 (766260) 345.0 kV to G20-007-XFM1 (766264) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 7 (531465) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR7 (531512) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEOSHON4 (533022) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDLIAW_CAP5 (541146) 161.0 kV Transmission Circuit #r b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply Fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWAVRLY5 (543063) 161.0 kV to MALTABN5 (543059) 161.0 kV Transmission Circuit #1 b.2. SWAVRLY5 (543063) 161.0 kV to SWAVRLY2 (543094) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.2. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on NEO184 5 161.00 (547471) 161 kV Bus a. Apply Fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO184 5 (547471) 161.0 kV to 2NEOSAC (300748) 69.0 kV Two Winding #1 b.2. NEO184 5 (547471) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAD368 5 (547478) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON383 5 (547480) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 5 (547483) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.2. NICHOLS 5 (549956) 161.0 kV to JUNCTION 5 (549955) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on OAK 2 69.000 (533547) 69 kV Bus a. Apply Fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to CRESWLN2 (533543) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on UDALL 2 69.000 (533559) 69 kV Bus a. Apply Fault at the UDALL 2 69.000 (533559) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UDALL 2 (533559) 69.0 kV to RICHLAN2 (533550) 69.0 kV Transmission Circuit #1 b.2. UDALL 2 (533559) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON383 2 (547591) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 b.2. MON383 2 (547591) 69.0 kV to MON383 5 (547480) 161.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on JOP430 2 69.000 (547608) 69 kV Bus a. Apply Fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP430 2 (547608) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 b.2. JOP430 2 (547608) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on NORTON 5 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTON 5 (543064) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on 5NORTON (300105) 161 kV Bus a. Apply Fault at the 5NORTON (300105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on CORDERTP2 (543657) 69 kV Bus a. Apply Fault at the CORDERTP2 (543657) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORDERTP2 (543657) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on CTY HIG2 (543098) 69 kV Bus a. Apply Fault at the CTY HIG2 (543098) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTY HIG2 (543098) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on HIGNSVL2 (543099) 69 kV Bus a. Apply Fault at the HIGNSVL2 (543099) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGNSVL2 (543099) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on WHGNSVL2 (543102) 69 kV Bus a. Apply Fault at the WHGNSVL2 (543102) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHGNSVL2 (543102) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on MAYVWTP2 (543096) 69 kV Bus a. Apply Fault at the MAYVWTP2 (543096) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAYVWTP2 (543096) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on SALSBRY5 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALSBRY5 (543062) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on 5THMHILB1 (300120) 161 kV Bus a. Apply Fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on 5THMHLB2 (300132) 161 kV Bus a. Apply Fault at the 5THMHLB2 (300132) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB2 (300132) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on 5THMHLB4 (301443) 161 kV Bus a. Apply Fault at the 5THMHLB4 (301443) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on 5MAURER 2 (344558) 161 kV Bus a. Apply Fault at the 5MAURER 2 (344558) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MAURER 2 (344558) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on WINFLD 2 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINFLD 2 (533561) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on TIMBJCT2 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on OAK 2 (533547) 69 kV Bus a. Apply Fault at the OAK 2 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on FINNEY 7 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on HOLCOMB3 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on CIM-PLT3 (539654) 115 kV Bus a. Apply Fault at the CIM-PLT3 (539654) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIM-PLT3 (539654) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on NORTH6T2 (531389) 69 kV Bus a. Apply Fault at the NORTH6T2 (531389) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTH6T2 (531389) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on GRTBEND3 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on CRAIG 5 (542978) 161 kV Bus a. Apply Fault at the CRAIG 5 (542978) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on LENEXA 5 (543038) 161 kV Bus a. Apply Fault at the LENEXA 5 (543038) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LENEXA 5 (543038) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_381 | Single Phase Fault with Stuck Breaker on WGARDNR5 (542966) 161 kV Bus a. Apply Fault at the WGARDNR5 (542966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_382 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_383 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_384 | Single Phase Fault with Stuck Breaker on LNGVW 5 (541224) 161 kV Bus a. Apply Fault at the LNGVW 5 (541224) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 5 (541224) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_385 | Single Phase Fault with Stuck Breaker on KETCHEM7 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_386 | Single Phase Fault with Stuck Breaker on HAWTH 7 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_387 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_388 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_389 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_390 | Single Phase Fault with Stuck Breaker on HSNVL 2 (541295) 69 kV Bus a. Apply Fault at the HSNVL 2 (541295) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVL 2 (541295) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_391 | Single Phase Fault with Stuck Breaker on ORO110 5 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_392 | Single Phase Fault with Stuck Breaker on JOP389 5 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 5 (547483) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_393 | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_394 | Single Phase Fault with Stuck Breaker on SEDALIA5 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_395 | Single Phase Fault with Stuck Breaker on S.OTTWA5 (543066) 161 kV Bus a. Apply Fault at the S.OTTWA5 (543066) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.OTTWA5 (543066) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_396 | Single Phase Fault with Stuck Breaker on PAOLA 5 (543069) 161 kV Bus a. Apply Fault at the PAOLA 5 (543069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAOLA 5 (543069) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_397 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_398 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_399 | Single Phase Fault with Stuck Breaker on RIV167 2 (547541) 69 kV Bus a. Apply Fault at the RIV167 2 (547541) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_400 | Single Phase Fault with Stuck Breaker on JOP 59 2 (547525) 69 kV Bus a. Apply Fault at the JOP 59 2 (547525) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 59 2 (547525) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_401 | Single Phase Fault with Stuck Breaker on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_402 | Single Phase Fault with Stuck Breaker on SPRGFLD2 (505494) 69 kV Bus a. Apply Fault at the SPRGFLD2 (505494) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD2 (505494) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_403 | Single Phase Fault with Stuck Breaker on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 5 (549969) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_404 | Single Phase Fault with Stuck Breaker on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_405 | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_406 | Single Phase Fault with Stuck Breaker on DAD368 5 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAD368 5 (547478) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_407 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_408 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_409 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_410 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_EDE1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_EDE2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_EDE3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_EDE4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_EDE5 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_EDE6 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy10 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy11 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy12 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy13 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy14 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy15 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy16 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy17 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy18 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy19 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy20 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy21 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy22 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy23 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy24 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy25 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy26 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy27 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy28 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy29 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy30 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy31 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy32 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy33 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy34 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy35 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy36 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy37 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy38 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy39 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy40 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy41 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy42 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy43 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy44 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy45 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy46 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy47 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy48 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy49 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy5 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy50 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy51 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy52 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy53 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy54 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy55 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy56 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy57 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy58 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy59 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy6 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy60 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy7 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy8 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy9 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_GRDA1 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_GRDA2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_INDN1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_INDN2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_INDN3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_OKGE1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_OKGE2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPRM1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPS1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPS2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPS3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPS4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPS5 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SPS6 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SUNC1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SUNC2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SWPA1 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_SWPA2 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_084 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_127 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_129 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_131 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_134 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_137 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_144 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_146 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_147 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_157 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_163 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_165 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_184 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_186 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_454 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_555 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_REGIONAL_FAULT_011 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_REGIONAL_FAULT_019 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_REGIONAL_FAULT_021 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P1_REGIONAL_FAULT_030 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25S | Base | GROUP3_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on GEN-2020-007345.00 (766260) 345 kV Bus a. Apply Fault at the GEN-2020-007345.00 (766260) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-007 (766260) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-007 (766260) 345.0 kV to G20-007-XFM1 (766264) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of WCGS U1 (532751) and JEC (532651, 532652, 532653) units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_001 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_002 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_003 | 3 Phase fault on 5ADAIR1 161.00 (344004) 161 kV Bus a. Apply fault at the 5ADAIR1 161.00 (344004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #1 b.2. 5ADAIR2 (344001) 161.0 kV to 5ADAIR1 (344004) 161.0 kV Transmission Circuit #z b.3. 5ADAIR1 (344004) 161.0 kV to 2ADAIR 1 (346005) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_004 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_005 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.2. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_006 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_007 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_008 | 3 Phase fault on 5COMPTN 161.00 (300719) 161 kV Bus a. Apply fault at the 5COMPTN 161.00 (300719) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_009 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.3. BUFORD 5 (504440) 161.0 kV to NORFORK5 (505448) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_010 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.2. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_011 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_012 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_013 | 3 Phase fault on 5GRANDVIEW% 161.00 (338099) 161 kV Bus a. Apply fault at the 5GRANDVIEW% 161.00 (338099) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_014 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_015 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_016 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_017 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_018 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_019 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_020 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_021 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_022 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_023 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_024 | 3 Phase fault on CONCRDTP2 69.000 (541523) 69 kV Bus a. Apply fault at the CONCRDTP2 69.000 (541523) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to CONCRDTP2 (541523) 69.0 kV Transmission Circuit #1 b.2. CONCORD2 (541319) 69.0 kV to CONCRDTP2 (541523) 69.0 kV Transmission Circuit #1 b.3. CONCORD2 (541319) 69.0 kV to ENBRIDGE PS2 (541542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_025 | 3 Phase fault on FAYETVLTP2 69.000 (541383) 69 kV Bus a. Apply fault at the FAYETVLTP2 69.000 (541383) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to FAYETVLTP2 (541383) 69.0 kV Transmission Circuit #1 b.2. WBURGP 2 (541268) 69.0 kV to FAYETVLTP2 (541383) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_026 | 3 Phase fault on GRDVWTP2 69.000 (541284) 69 kV Bus a. Apply fault at the GRDVWTP2 69.000 (541284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 b.3. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.4. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.5. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.6. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_027 | 3 Phase fault on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_028 | 3 Phase fault on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 b.3. FREEMAN2 (541291) 69.0 kV to FREEMAN_SP2 (541540) 69.0 kV Transmission Circuit #1 b.4. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.5. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 b.6. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_029 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 b.2. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_030 | 3 Phase fault on HLDENTP2 69.000 (541386) 69 kV Bus a. Apply fault at the HLDENTP2 69.000 (541386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to CNTRVIEW2 (541385) 69.0 kV Transmission Circuit #1 b.2. HOLDEN 2 (541278) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.3. RGREEN 2 (541279) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 b.4. CNTRVIEW2 (541385) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.5. HLDENTP2 (541386) 69.0 kV to KNGSVIL 2 (541387) 69.0 kV Transmission Circuit #1 b.6. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_031 | 3 Phase fault on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.3. POSTOAK2 (541300) 69.0 kV to POSTOAK1 (541373) 34.5 kV to POSTOAK_TER1 (541374) 2.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_032 | 3 Phase fault on CLNTPLT_CAP269.000 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP269.000 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_033 | 3 Phase fault on LEXNTON2 69.000 (541265) 69 kV Bus a. Apply fault at the LEXNTON2 69.000 (541265) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNTON2 (541265) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_034 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_035 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_036 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_037 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_038 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_039 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_040 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_041 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_042 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_043 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_044 | 3 Phase fault on NAVY 5 161.00 (542989) 161 kV Bus a. Apply fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_045 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_046 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_047 | 3 Phase fault on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_048 | 3 Phase fault on NORTON 5 161.00 (543064) 161 kV Bus a. Apply fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 b.2. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. NORTON 5 (543064) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_049 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_050 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_051 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. MERRIAM_CAP5 (542947) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_052 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_053 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_054 | 3 Phase fault on SWAVCAP2 69.000 (543012) 69 kV Bus a. Apply fault at the SWAVCAP2 69.000 (543012) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.2. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.3. SWAVCAP2 (543012) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_055 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_056 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_057 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_058 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_059 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_060 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_061 | 3 Phase fault on CORDER 2 69.000 (543097) 69 kV Bus a. Apply fault at the CORDER 2 69.000 (543097) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.2. CORDER 2 (543097) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.3. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.4. DOVER2 (543101) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.5. CORDERTP2 (543657) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.6. CORDER 2 (543097) 69.0 kV to CORDER1 (543150) 12.5 kV to CORDER_TER1 (543151) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_062 | 3 Phase fault on WHGNSVL2 69.000 (543102) 69 kV Bus a. Apply fault at the WHGNSVL2 69.000 (543102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNTON2 (541265) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.2. 13&40 2 (541266) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.3. MAYVWTP2 (543096) 69.0 kV to AMOCOPL2 (543100) 69.0 kV Transmission Circuit #1 b.4. CTY HIG2 (543098) 69.0 kV to HIGNSVL2 (543099) 69.0 kV Transmission Circuit #1 b.5. HIGNSVL2 (543099) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 b.6. AMOCOPL2 (543100) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 b.7. HIGNSVL2 (543099) 69.0 kV to HGNSVL1 (543152) 12.5 kV to HGNSVL_TER1 (543153) 2.4 kV Three Winding #1 b.8. WHGNSVL2 (543102) 69.0 kV to WHGNSVL1 (543154) 12.5 kV to WHGNSVL_TER1 (543155) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_063 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_064 | 3 Phase fault on KCSOUTH5 161.00 (541245) 161 kV Bus a. Apply fault at the KCSOUTH5 161.00 (541245) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCSOUTH5 (541245) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_065 | 3 Phase fault on OSAWTM_CAP5 161.00 (543135) 161 kV Bus a. Apply fault at the OSAWTM_CAP5 161.00 (543135) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWTM_CAP5 (543135) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_066 | 3 Phase fault on SWAVCAP5 161.00 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 161.00 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_067 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_068 | 3 Phase fault on COLLEG 2 69.000 (530574) 69 kV Bus a. Apply fault at the COLLEG 2 69.000 (530574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 b.2. COLLEG 2 (530574) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_069 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_070 | 3 Phase fault on BKHLTAP2 69.000 (530589) 69 kV Bus a. Apply fault at the BKHLTAP2 69.000 (530589) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.2. SUSANK 2 (530571) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.3. BNK HL 2 (530572) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.4. HITHMN 2 (530573) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_071 | 3 Phase fault on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_072 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_073 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_074 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_075 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_076 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_077 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_078 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_079 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_080 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_081 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_082 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_083 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_084 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. The issue is also observed in the PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_085 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_086 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_087 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_088 | 3 Phase fault on SETAB 3 115.00 (531464) 115 kV Bus a. Apply fault at the SETAB 3 115.00 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_089 | 3 Phase fault on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_090 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_091 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_092 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_093 | 3 Phase fault on GRANTTP3 115.00 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 115.00 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_094 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_095 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_096 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_097 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_098 | 3 Phase fault on SAT-TAP3 115.00 (531442) 115 kV Bus a. Apply fault at the SAT-TAP3 115.00 (531442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASKELL3 (531374) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.2. HASKELL3 (531374) 115.0 kV to SEWARD-3 (531467) 115.0 kV Transmission Circuit #1 b.3. PIONTAP3 (531392) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.4. SAT-TAP3 (531442) 115.0 kV to SATMKEC3 (539691) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_099 | 3 Phase fault on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_100 | 3 Phase fault on WILLIAM3 115.00 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 115.00 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_101 | 3 Phase fault on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.3. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_102 | 3 Phase fault on GANO 3 115.00 (531493) 115 kV Bus a. Apply fault at the GANO 3 115.00 (531493) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.3. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_103 | 3 Phase fault on KSAVWTP3 115.00 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 115.00 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_104 | 3 Phase fault on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_105 | 3 Phase fault on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.2. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.3. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_106 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_107 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_108 | 3 Phase fault on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_109 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_110 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_111 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_112 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_113 | 3 Phase fault on WALDO 3 115.00 (539698) 115 kV Bus a. Apply fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_114 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_115 | 3 Phase fault on PHLBURG3 115.00 (539685) 115 kV Bus a. Apply fault at the PHLBURG3 115.00 (539685) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_116 | 3 Phase fault on GLENELD3 115.00 (539663) 115 kV Bus a. Apply fault at the GLENELD3 115.00 (539663) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.2. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_117 | 3 Phase fault on JEWELL 3 115.00 (539669) 115 kV Bus a. Apply fault at the JEWELL 3 115.00 (539669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.2. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.4. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_118 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_119 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_120 | 3 Phase fault on 5LOGAN 161.00 (301161) 161 kV Bus a. Apply fault at the 5LOGAN 161.00 (301161) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MANSFDMN (300095) 161.0 kV to 5LOGAN (301161) 161.0 kV Transmission Circuit #1 b.2. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_121 | 3 Phase fault on WAVERLY3 115.00 (533278) 115 kV Bus a. Apply fault at the WAVERLY3 115.00 (533278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.2. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_122 | 3 Phase fault on MNTCLLO3 115.00 (533281) 115 kV Bus a. Apply fault at the MNTCLLO3 115.00 (533281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_123 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_124 | 3 Phase fault on MUND 3 115.00 (533282) 115 kV Bus a. Apply fault at the MUND 3 115.00 (533282) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_125 | 3 Phase fault on 166TH 3 115.00 (533233) 115 kV Bus a. Apply fault at the 166TH 3 115.00 (533233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.3. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_126 | 3 Phase fault on MIDLADN3 115.00 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 115.00 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_127 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_128 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_129 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_130 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_131 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_132 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_133 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_134 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_135 | 3 Phase fault on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_136 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_137 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_138 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_139 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes